## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1403-4_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1403-4_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1403-4_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1403-4_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1403-4_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1403-4_0_2_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1403-4_0_2_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1403-4_0_2_node_47 | 0.4 | n |  | TRUE
8 | bus_LV_1403-4_0_2_node_57 | 0.4 | n |  | TRUE
9 | bus_LV_1403-4_0_2_node_49 | 0.4 | n |  | TRUE
10 | bus_LV_1403-4_0_2_node_26 | 0.4 | n |  | TRUE
11 | bus_LV_1403-4_0_2_node_58 | 0.4 | n |  | TRUE
12 | bus_LV_1403-4_0_2_node_59 | 0.4 | n |  | TRUE
13 | bus_LV_1403-4_0_2_node_51 | 0.4 | n |  | TRUE
14 | bus_LV_1403-4_0_2_node_52 | 0.4 | n |  | TRUE
15 | bus_LV_1403-4_0_2_node_48 | 0.4 | n |  | TRUE
16 | bus_LV_1403-4_0_2_node_7 | 0.4 | n |  | TRUE
17 | bus_LV_1403-4_0_2_node_8 | 0.4 | n |  | TRUE
18 | bus_LV_1403-4_0_2_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_1403-4_0_2_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_1403-4_0_2_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_1403-4_0_2_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_1403-4_0_2_node_44 | 0.4 | n |  | TRUE
23 | bus_LV_1403-4_0_2_node_129 | 0.4 | n |  | TRUE
24 | bus_LV_1403-4_0_2_node_114 | 0.4 | n |  | TRUE
25 | bus_LV_1403-4_0_2_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_1403-4_0_2_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_1403-4_0_2_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_1403-4_0_2_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_1403-4_0_2_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_1403-4_0_2_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_1403-4_0_2_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_1403-4_0_2_node_25 | 0.4 | n |  | TRUE
33 | bus_LV_1403-4_0_2_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_1403-4_0_2_node_20 | 0.4 | n |  | TRUE
35 | bus_LV_1403-4_0_2_node_18 | 0.4 | n |  | TRUE
36 | bus_LV_1403-4_0_2_node_19 | 0.4 | n |  | TRUE
37 | bus_LV_1403-4_0_2_node_21 | 0.4 | n |  | TRUE
38 | bus_LV_1403-4_0_2_node_55 | 0.4 | n |  | TRUE
39 | bus_LV_1403-4_0_2_node_53 | 0.4 | n |  | TRUE
40 | bus_LV_1403-4_0_2_node_125 | 0.4 | n |  | TRUE
41 | bus_LV_1403-4_0_2_node_54 | 0.4 | n |  | TRUE
42 | bus_LV_1403-4_0_2_node_27 | 0.4 | n |  | TRUE
43 | bus_LV_1403-4_0_2_node_29 | 0.4 | n |  | TRUE
44 | bus_LV_1403-4_0_2_node_45 | 0.4 | n |  | TRUE
45 | bus_LV_1403-4_0_2_node_34 | 0.4 | n |  | TRUE
46 | bus_LV_1403-4_0_2_node_37 | 0.4 | n |  | TRUE
47 | bus_LV_1403-4_0_2_node_42 | 0.4 | n |  | TRUE
48 | bus_LV_1403-4_0_2_node_67 | 0.4 | n |  | TRUE
49 | bus_LV_1403-4_0_2_node_35 | 0.4 | n |  | TRUE
50 | bus_LV_1403-4_0_2_node_46 | 0.4 | n |  | TRUE
51 | bus_LV_1403-4_0_2_node_36 | 0.4 | n |  | TRUE
52 | bus_LV_1403-4_0_2_node_147 | 0.4 | n |  | TRUE
53 | bus_LV_1403-4_0_2_node_38 | 0.4 | n |  | TRUE
54 | bus_LV_1403-4_0_2_node_146 | 0.4 | n |  | TRUE
55 | bus_LV_1403-4_0_2_node_136 | 0.4 | n |  | TRUE
56 | bus_LV_1403-4_0_2_node_145 | 0.4 | n |  | TRUE
57 | bus_LV_1403-4_0_2_node_39 | 0.4 | n |  | TRUE
58 | bus_LV_1403-4_0_2_node_142 | 0.4 | n |  | TRUE
59 | bus_LV_1403-4_0_2_node_40 | 0.4 | n |  | TRUE
60 | bus_LV_1403-4_0_2_node_78 | 0.4 | n |  | TRUE
61 | bus_LV_1403-4_0_2_node_71 | 0.4 | n |  | TRUE
62 | bus_LV_1403-4_0_2_node_122 | 0.4 | n |  | TRUE
63 | bus_LV_1403-4_0_2_node_128 | 0.4 | n |  | TRUE
64 | bus_LV_1403-4_0_2_node_127 | 0.4 | n |  | TRUE
65 | bus_LV_1403-4_0_2_node_120 | 0.4 | n |  | TRUE
66 | bus_LV_1403-4_0_2_node_119 | 0.4 | n |  | TRUE
67 | bus_LV_1403-4_0_2_node_66 | 0.4 | n |  | TRUE
68 | bus_LV_1403-4_0_2_node_151 | 0.4 | n |  | TRUE
69 | bus_LV_1403-4_0_2_node_135 | 0.4 | n |  | TRUE
70 | bus_LV_1403-4_0_2_node_77 | 0.4 | n |  | TRUE
71 | bus_LV_1403-4_0_2_node_121 | 0.4 | n |  | TRUE
72 | bus_LV_1403-4_0_2_node_83 | 0.4 | n |  | TRUE
73 | bus_LV_1403-4_0_2_node_72 | 0.4 | n |  | TRUE
74 | bus_LV_1403-4_0_2_node_123 | 0.4 | n |  | TRUE
75 | bus_LV_1403-4_0_2_node_115 | 0.4 | n |  | TRUE
76 | bus_LV_1403-4_0_2_node_126 | 0.4 | n |  | TRUE
77 | bus_LV_1403-4_0_2_node_50 | 0.4 | n |  | TRUE
78 | bus_LV_1403-4_0_2_node_56 | 0.4 | n |  | TRUE
79 | bus_LV_1403-4_0_2_node_124 | 0.4 | n |  | TRUE
80 | bus_LV_1403-4_0_2_node_132 | 0.4 | n |  | TRUE
81 | bus_LV_1403-4_0_2_node_130 | 0.4 | n |  | TRUE
82 | bus_LV_1403-4_0_2_node_140 | 0.4 | n |  | TRUE
83 | bus_LV_1403-4_0_2_node_131 | 0.4 | n |  | TRUE
84 | bus_LV_1403-4_0_2_node_141 | 0.4 | n |  | TRUE
85 | bus_LV_1403-4_0_2_node_60 | 0.4 | n |  | TRUE
86 | bus_LV_1403-4_0_2_node_61 | 0.4 | n |  | TRUE
87 | bus_LV_1403-4_0_2_node_62 | 0.4 | n |  | TRUE
88 | bus_LV_1403-4_0_2_node_63 | 0.4 | n |  | TRUE
89 | bus_LV_1403-4_0_2_node_69 | 0.4 | n |  | TRUE
90 | bus_LV_1403-4_0_2_node_70 | 0.4 | n |  | TRUE
91 | bus_LV_1403-4_0_2_node_138 | 0.4 | n |  | TRUE
92 | bus_LV_1403-4_0_2_node_153 | 0.4 | n |  | TRUE
93 | bus_LV_1403-4_0_2_node_81 | 0.4 | n |  | TRUE
94 | bus_LV_1403-4_0_2_node_68 | 0.4 | n |  | TRUE
95 | bus_LV_1403-4_0_2_node_74 | 0.4 | n |  | TRUE
96 | bus_LV_1403-4_0_2_node_82 | 0.4 | n |  | TRUE
97 | bus_LV_1403-4_0_2_node_79 | 0.4 | n |  | TRUE
98 | bus_LV_1403-4_0_2_node_73 | 0.4 | n |  | TRUE
99 | bus_LV_1403-4_0_2_node_76 | 0.4 | n |  | TRUE
100 | bus_LV_1403-4_0_2_node_139 | 0.4 | n |  | TRUE
101 | bus_LV_1403-4_0_2_node_75 | 0.4 | n |  | TRUE
102 | bus_LV_1403-4_0_2_node_134 | 0.4 | n |  | TRUE
103 | bus_LV_1403-4_0_2_node_144 | 0.4 | n |  | TRUE
104 | bus_LV_1403-4_0_2_node_143 | 0.4 | n |  | TRUE
105 | bus_LV_1403-4_0_2_node_154 | 0.4 | n |  | TRUE
106 | bus_LV_1403-4_0_2_node_155 | 0.4 | n |  | TRUE
107 | bus_LV_1403-4_0_2_node_133 | 0.4 | n |  | TRUE
108 | bus_LV_1403-4_0_2_node_80 | 0.4 | n |  | TRUE
109 | bus_LV_1403-4_0_2_node_152 | 0.4 | n |  | TRUE
110 | bus_LV_1403-4_0_2_node_116 | 0.4 | n |  | TRUE
111 | bus_LV_1403-4_0_2_node_117 | 0.4 | n |  | TRUE
112 | bus_LV_1403-4_0_2_node_118 | 0.4 | n |  | TRUE
113 | bus_LV_1403-4_0_2_node_137 | 0.4 | n |  | TRUE
114 | bus_MV_138_0_node_38 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1403-4_0_2_load_0 | 0 | 0.0029922 | 0.00074991 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1403-4_0_2_load_1 | 1 | 0.0029261 | 0.00073335 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1403-4_0_2_load_3 | 3 | 0.007985 | 0.0020012 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1403-4_0_2_load_4 | 4 | 0.004458 | 0.0011173 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1403-4_0_2_load_5 | 5 | 0.0073341 | 0.0018381 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1403-4_0_2_load_6 | 6 | 0.0054619 | 0.0013689 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1403-4_0_2_load_47 | 7 | 0.0014189 | 0.00035562 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1403-4_0_2_load_26 | 10 | 0.0019738 | 0.00049469 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1403-4_0_2_load_59 | 12 | 0.0034227 | 0.0008578 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1403-4_0_2_load_51 | 13 | 0.0033523 | 0.00084017 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1403-4_0_2_load_52 | 14 | 0.0014829 | 0.00037165 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1403-4_0_2_load_48 | 15 | 0.0074106 | 0.0018573 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1403-4_0_2_load_7 | 16 | 0.0024481 | 0.00061355 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1403-4_0_2_load_8 | 17 | 0.0012392 | 0.00031056 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1403-4_0_2_load_10 | 19 | 0.0050467 | 0.0012648 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1403-4_0_2_load_11 | 20 | 0.00058137 | 0.00014571 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1403-4_0_2_load_12 | 21 | 0.00072522 | 0.00018176 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1403-4_0_2_load_129 | 23 | 0.0039586 | 0.00099211 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1403-4_0_2_load_114 | 24 | 0.00035548 | 8.9091e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1403-4_0_2_load_13 | 25 | 0.0009166 | 0.00022972 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1403-4_0_2_load_14 | 26 | 0.0019859 | 0.00049771 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1403-4_0_2_load_15 | 27 | 0.0003141 | 7.8722e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1403-4_0_2_load_16 | 28 | 0.001381 | 0.00034612 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1403-4_0_2_load_17 | 29 | 0.00085344 | 0.00021389 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1403-4_0_2_load_24 | 30 | 0.0025895 | 0.000649 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1403-4_0_2_load_25 | 32 | 0.0023719 | 0.00059445 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1403-4_0_2_load_20 | 34 | 0.0015192 | 0.00038076 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1403-4_0_2_load_18 | 35 | 0.001478 | 0.00037041 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1403-4_0_2_load_19 | 36 | 0.00026208 | 6.5683e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1403-4_0_2_load_21 | 37 | 0.00060853 | 0.00015251 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1403-4_0_2_load_55 | 38 | 0.00053333 | 0.00013367 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1403-4_0_2_load_53 | 39 | 0.00051678 | 0.00012952 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1403-4_0_2_load_27 | 42 | 0.0020649 | 0.0005175 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1403-4_0_2_load_45 | 44 | 0.0021653 | 0.00054267 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1403-4_0_2_load_67 | 48 | 4.3628e-05 | 1.0934e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1403-4_0_2_load_146 | 54 | 4.0235e-05 | 1.0084e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1403-4_0_2_load_136 | 55 | 6.6592e-05 | 1.6689e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1403-4_0_2_load_145 | 56 | 4.7461e-05 | 1.1895e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1403-4_0_2_load_142 | 58 | 0.001007 | 0.00025239 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1403-4_0_2_load_78 | 60 | 0.00027882 | 6.9878e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1403-4_0_2_load_71 | 61 | 0.00010814 | 2.7103e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1403-4_0_2_load_122 | 62 | 0.00057614 | 0.00014439 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1403-4_0_2_load_128 | 63 | 0.00073589 | 0.00018443 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1403-4_0_2_load_127 | 64 | 0.00040936 | 0.0001026 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1403-4_0_2_load_120 | 65 | 0.00013483 | 3.3791e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1403-4_0_2_load_119 | 66 | 0.0004759 | 0.00011927 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1403-4_0_2_load_66 | 67 | 0.00010662 | 2.6722e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1403-4_0_2_load_151 | 68 | 9.2713e-05 | 2.3236e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1403-4_0_2_load_135 | 69 | 0.00014122 | 3.5392e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1403-4_0_2_load_121 | 71 | 0.00046946 | 0.00011766 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1403-4_0_2_load_83 | 72 | 0.0015328 | 0.00038416 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1403-4_0_2_load_123 | 74 | 0.0004353 | 0.0001091 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1403-4_0_2_load_115 | 75 | 0.00039845 | 9.986e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1403-4_0_2_load_126 | 76 | 0.00056725 | 0.00014217 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1403-4_0_2_load_50 | 77 | 0.0071605 | 0.0017946 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1403-4_0_2_load_56 | 78 | 0.00083313 | 0.0002088 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1403-4_0_2_load_124 | 79 | 0.00059328 | 0.00014869 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1403-4_0_2_load_132 | 80 | 0.010139 | 0.0025411 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1403-4_0_2_load_130 | 81 | 0.0042649 | 0.0010689 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1403-4_0_2_load_140 | 82 | 0.0041316 | 0.0010355 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1403-4_0_2_load_131 | 83 | 0.0052821 | 0.0013238 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1403-4_0_2_load_141 | 84 | 0.0037748 | 0.00094606 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1403-4_0_2_load_60 | 85 | 8.2753e-05 | 2.074e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1403-4_0_2_load_61 | 86 | 9.9597e-05 | 2.4961e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1403-4_0_2_load_62 | 87 | 4.9379e-05 | 1.2376e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1403-4_0_2_load_69 | 89 | 0.00011122 | 2.7875e-05 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1403-4_0_2_load_138 | 91 | 8.6824e-05 | 2.176e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1403-4_0_2_load_153 | 92 | 0.00015796 | 3.9588e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1403-4_0_2_load_68 | 94 | 0.00019226 | 4.8184e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1403-4_0_2_load_79 | 97 | 4.3633e-05 | 1.0936e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1403-4_0_2_load_73 | 98 | 0.00012433 | 3.1161e-05 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1403-4_0_2_load_134 | 102 | 0.00012651 | 3.1707e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1403-4_0_2_load_144 | 103 | 0.00015639 | 3.9196e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1403-4_0_2_load_143 | 104 | 4.606e-05 | 1.1544e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1403-4_0_2_load_154 | 105 | 0.00015651 | 3.9225e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1403-4_0_2_load_155 | 106 | 0.00015394 | 3.8581e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1403-4_0_2_load_133 | 107 | 0.00045667 | 0.00011445 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1403-4_0_2_load_80 | 108 | 0.00056669 | 0.00014203 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1403-4_0_2_load_152 | 109 | 0.00012048 | 3.0196e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1403-4_0_2_load_116 | 110 | 0.0002314 | 5.7995e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1403-4_0_2_load_117 | 111 | 0.00032794 | 8.2189e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1403-4_0_2_load_118 | 112 | 0.00013085 | 3.2793e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1403-4_0_2_load_137 | 113 | 0.00013452 | 3.3713e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 7 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1403-4_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0018457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1403-4_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.014068 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1403-4_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.012653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1403-4_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.018091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1403-4_0_2_line_4 | NAYY 4x150 SE | 2 | 5 | 0.01965 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1403-4_0_2_line_5 | NAYY 4x150 SE | 2 | 6 | 0.031634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1403-4_0_2_line_6 | NAYY 4x150 SE | 4 | 7 | 0.010476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1403-4_0_2_line_7 | NAYY 4x150 SE | 5 | 8 | 0.04551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1403-4_0_2_line_8 | NAYY 4x150 SE | 6 | 9 | 0.033492 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1403-4_0_2_line_9 | NAYY 4x150 SE | 7 | 10 | 0.011621 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1403-4_0_2_line_10 | NAYY 4x150 SE | 8 | 11 | 0.002734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1403-4_0_2_line_11 | NAYY 4x150 SE | 8 | 12 | 0.02341 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1403-4_0_2_line_12 | NAYY 4x150 SE | 9 | 13 | 0.013259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1403-4_0_2_line_13 | NAYY 4x150 SE | 9 | 14 | 0.023417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1403-4_0_2_line_14 | NAYY 4x150 SE | 9 | 15 | 0.023038 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1403-4_0_2_line_15 | NAYY 4x150 SE | 10 | 32 | 0.0056376 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1403-4_0_2_line_16 | NAYY 4x150 SE | 11 | 80 | 0.0531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1403-4_0_2_line_17 | NAYY 4x150 SE | 11 | 81 | 0.068505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1403-4_0_2_line_18 | NAYY 4x150 SE | 12 | 82 | 0.0084635 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1403-4_0_2_line_19 | NAYY 4x150 SE | 14 | 19 | 0.014095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1403-4_0_2_line_20 | NAYY 4x150 SE | 15 | 77 | 0.016697 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1403-4_0_2_line_21 | NAYY 4x150 SE | 16 | 17 | 0.0019705 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1403-4_0_2_line_22 | NAYY 4x150 SE | 16 | 18 | 0.02065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1403-4_0_2_line_23 | NAYY 4x150 SE | 17 | 19 | 0.035626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1403-4_0_2_line_24 | NAYY 4x150 SE | 18 | 20 | 0.078929 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1403-4_0_2_line_25 | NAYY 4x150 SE | 18 | 21 | 0.049193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1403-4_0_2_line_26 | NAYY 4x150 SE | 20 | 22 | 0.088971 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1403-4_0_2_line_27 | NAYY 4x150 SE | 21 | 23 | 0.0042026 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1403-4_0_2_line_28 | NAYY 4x150 SE | 22 | 24 | 0.037267 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1403-4_0_2_line_29 | NAYY 4x150 SE | 24 | 75 | 0.048487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1403-4_0_2_line_30 | NAYY 4x150 SE | 25 | 26 | 0.012816 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1403-4_0_2_line_31 | NAYY 4x150 SE | 25 | 27 | 0.0080631 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1403-4_0_2_line_32 | NAYY 4x150 SE | 26 | 28 | 0.010254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1403-4_0_2_line_33 | NAYY 4x150 SE | 27 | 29 | 0.018732 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1403-4_0_2_line_34 | NAYY 4x150 SE | 28 | 30 | 0.015524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1403-4_0_2_line_35 | NAYY 4x150 SE | 29 | 31 | 0.018302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1403-4_0_2_line_36 | NAYY 4x150 SE | 30 | 32 | 0.01897 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1403-4_0_2_line_37 | NAYY 4x150 SE | 31 | 33 | 0.046952 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1403-4_0_2_line_38 | NAYY 4x150 SE | 31 | 34 | 0.037824 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1403-4_0_2_line_39 | NAYY 4x150 SE | 33 | 38 | 0.052653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1403-4_0_2_line_40 | NAYY 4x150 SE | 33 | 39 | 0.019869 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1403-4_0_2_line_41 | NAYY 4x150 SE | 34 | 35 | 0.040342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1403-4_0_2_line_42 | NAYY 4x150 SE | 35 | 36 | 0.010044 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1403-4_0_2_line_43 | NAYY 4x150 SE | 36 | 37 | 0.017312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1403-4_0_2_line_44 | NAYY 4x150 SE | 38 | 40 | 0.0059834 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1403-4_0_2_line_45 | NAYY 4x150 SE | 39 | 41 | 0.0035558 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1403-4_0_2_line_46 | NAYY 4x150 SE | 40 | 76 | 0.024559 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1403-4_0_2_line_47 | NAYY 4x150 SE | 40 | 79 | 0.0085134 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1403-4_0_2_line_48 | NAYY 4x150 SE | 41 | 78 | 0.023547 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1403-4_0_2_line_49 | NAYY 4x150 SE | 42 | 43 | 0.017397 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1403-4_0_2_line_50 | NAYY 4x150 SE | 43 | 44 | 0.0017877 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1403-4_0_2_line_51 | NAYY 4x150 SE | 44 | 49 | 0.11633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1403-4_0_2_line_52 | NAYY 4x150 SE | 45 | 46 | 0.19531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1403-4_0_2_line_53 | NAYY 4x150 SE | 45 | 47 | 0.49645 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1403-4_0_2_line_54 | NAYY 4x150 SE | 45 | 48 | 0.11731 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1403-4_0_2_line_55 | NAYY 4x150 SE | 46 | 53 | 0.161 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1403-4_0_2_line_56 | NAYY 4x150 SE | 46 | 55 | 0.0077461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1403-4_0_2_line_57 | NAYY 4x150 SE | 47 | 62 | 0.076108 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1403-4_0_2_line_58 | NAYY 4x150 SE | 47 | 57 | 0.42351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1403-4_0_2_line_59 | NAYY 4x150 SE | 47 | 59 | 0.22826 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1403-4_0_2_line_60 | NAYY 4x150 SE | 48 | 67 | 0.093434 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1403-4_0_2_line_61 | NAYY 4x150 SE | 49 | 50 | 0.12125 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1403-4_0_2_line_62 | NAYY 4x150 SE | 50 | 63 | 0.13426 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1403-4_0_2_line_63 | NAYY 4x150 SE | 50 | 64 | 0.062475 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1403-4_0_2_line_64 | NAYY 4x150 SE | 51 | 52 | 0.17842 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1403-4_0_2_line_65 | NAYY 4x150 SE | 51 | 53 | 0.066309 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1403-4_0_2_line_66 | NAYY 4x150 SE | 51 | 54 | 0.103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1403-4_0_2_line_67 | NAYY 4x150 SE | 52 | 68 | 0.35332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1403-4_0_2_line_68 | NAYY 4x150 SE | 53 | 56 | 0.0052267 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1403-4_0_2_line_69 | NAYY 4x150 SE | 55 | 69 | 0.028558 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1403-4_0_2_line_70 | NAYY 4x150 SE | 57 | 58 | 0.0084134 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1403-4_0_2_line_71 | NAYY 4x150 SE | 59 | 60 | 0.027558 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1403-4_0_2_line_72 | NAYY 4x150 SE | 59 | 61 | 0.13539 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1403-4_0_2_line_73 | NAYY 4x150 SE | 60 | 72 | 0.022761 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1403-4_0_2_line_74 | NAYY 4x150 SE | 61 | 73 | 0.05267 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1403-4_0_2_line_75 | NAYY 4x150 SE | 62 | 74 | 0.032637 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1403-4_0_2_line_76 | NAYY 4x150 SE | 64 | 76 | 0.027769 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1403-4_0_2_line_77 | NAYY 4x150 SE | 65 | 66 | 0.016215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1403-4_0_2_line_78 | NAYY 4x150 SE | 66 | 112 | 0.0038162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1403-4_0_2_line_79 | NAYY 4x150 SE | 67 | 94 | 0.011769 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1403-4_0_2_line_80 | NAYY 4x150 SE | 69 | 113 | 0.023815 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1403-4_0_2_line_81 | NAYY 4x150 SE | 70 | 71 | 0.025843 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1403-4_0_2_line_82 | NAYY 4x150 SE | 70 | 72 | 0.047533 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1403-4_0_2_line_83 | NAYY 4x150 SE | 73 | 98 | 0.049798 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1403-4_0_2_line_84 | NAYY 4x150 SE | 73 | 99 | 0.15799 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1403-4_0_2_line_85 | NAYY 4x150 SE | 74 | 79 | 0.004995 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1403-4_0_2_line_86 | NAYY 4x150 SE | 75 | 110 | 0.0081294 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1403-4_0_2_line_87 | NAYY 4x150 SE | 81 | 83 | 0.028847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1403-4_0_2_line_88 | NAYY 4x150 SE | 82 | 84 | 0.0046092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1403-4_0_2_line_89 | NAYY 4x150 SE | 85 | 86 | 0.00074532 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1403-4_0_2_line_90 | NAYY 4x150 SE | 85 | 87 | 0.0086363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1403-4_0_2_line_91 | NAYY 4x150 SE | 86 | 88 | 0.04746 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1403-4_0_2_line_92 | NAYY 4x150 SE | 88 | 89 | 0.024726 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1403-4_0_2_line_93 | NAYY 4x150 SE | 88 | 90 | 0.22133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1403-4_0_2_line_94 | NAYY 4x150 SE | 89 | 91 | 0.0050094 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1403-4_0_2_line_95 | NAYY 4x150 SE | 90 | 92 | 0.060122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1403-4_0_2_line_96 | NAYY 4x150 SE | 90 | 93 | 0.055465 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1403-4_0_2_line_97 | NAYY 4x150 SE | 91 | 95 | 0.20069 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1403-4_0_2_line_98 | NAYY 4x150 SE | 93 | 96 | 0.037781 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1403-4_0_2_line_99 | NAYY 4x150 SE | 93 | 97 | 0.080791 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1403-4_0_2_line_100 | NAYY 4x150 SE | 95 | 100 | 0.078378 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1403-4_0_2_line_101 | NAYY 4x150 SE | 95 | 99 | 0.57073 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1403-4_0_2_line_102 | NAYY 4x150 SE | 95 | 101 | 0.072232 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1403-4_0_2_line_103 | NAYY 4x150 SE | 96 | 109 | 0.053312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1403-4_0_2_line_104 | NAYY 4x150 SE | 97 | 108 | 0.029978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1403-4_0_2_line_105 | NAYY 4x150 SE | 99 | 103 | 0.020339 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1403-4_0_2_line_106 | NAYY 4x150 SE | 99 | 104 | 0.031089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1403-4_0_2_line_107 | NAYY 4x150 SE | 100 | 105 | 0.025424 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1403-4_0_2_line_108 | NAYY 4x150 SE | 100 | 106 | 0.005921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1403-4_0_2_line_109 | NAYY 4x150 SE | 101 | 102 | 0.0057952 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1403-4_0_2_line_110 | NAYY 4x150 SE | 102 | 107 | 0.026475 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_1403-4_0_2_line_111 | NAYY 4x150 SE | 110 | 111 | 0.0041216 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_1403-4_0_2_line_112 | NAYY 4x150 SE | 111 | 112 | 0.031261 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1403-4_0_2_trafo_47 | 0.25 MVA 20/0.4 kV | 114 | 7 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37 | x38 | y38 | x39 | y39
0 | 2655075.7198 | 1188789.4215 | 2655077.2448 | 1188788.3818
1 | 2655064.0965 | 1188797.3462 | 2655075.7198 | 1188789.4215
2 | 2655087.6992 | 1188781.2541 | 2655077.2448 | 1188788.3818
3 | 2655064.0965 | 1188797.3462 | 2655053.9966 | 1188782.3367
4 | 2655064.0965 | 1188797.3462 | 2655047.9603 | 1188808.5597
5 | 2655064.0965 | 1188797.3462 | 2655082.6222 | 1188822.988
6 | 2655053.9966 | 1188782.3367 | 2655048.1481 | 1188773.6452
7 | 2655005.3963 | 1188801.3536 | 2655008.5355 | 1188800.8933 | 2655012.6807 | 1188801.3427 | 2655017.5116 | 1188802.7101 | 2655026.0724 | 1188807.4025 | 2655033.5526 | 1188810.9732 | 2655038.6869 | 1188811.6985 | 2655043.1249 | 1188811.0056 | 2655047.9603 | 1188808.5597
8 | 2655098.3724 | 1188852.2922 | 2655096.8312 | 1188847.3641 | 2655094.2477 | 1188841.3259 | 2655089.591 | 1188832.6337 | 2655082.6222 | 1188822.988
9 | 2655041.8881 | 1188763.8658 | 2655043.2454 | 1188766.3594 | 2655048.1481 | 1188773.6452
10 | 2655002.6848 | 1188801.7623 | 2655005.3963 | 1188801.3536
11 | 2655005.3963 | 1188801.3536 | 2655008.2856 | 1188809.8294 | 2655011.4283 | 1188823.9394
12 | 2655098.3724 | 1188852.2922 | 2655101.7673 | 1188865.1096
13 | 2655098.3724 | 1188852.2922 | 2655104.8729 | 1188848.7722 | 2655115.7595 | 1188840.2454 | 2655117.2903 | 1188838.6706
14 | 2655098.3724 | 1188852.2922 | 2655076.015 | 1188857.849
15 | 2655041.8881 | 1188763.8658 | 2655039.1928 | 1188758.9143
16 | 2654953.3737 | 1188794.1944 | 2654957.8478 | 1188789.5662 | 2654962.2531 | 1188789.1063 | 2655002.6848 | 1188801.7623
17 | 2655002.6848 | 1188801.7623 | 2654998.454 | 1188803.1576 | 2654994.106 | 1188805.6857 | 2654990.7731 | 1188808.9681 | 2654987.9558 | 1188813.4225 | 2654985.8031 | 1188819.4284 | 2654985.3261 | 1188825.6831 | 2654986.6218 | 1188831.5983 | 2654989.6938 | 1188839.2864 | 2654997.047 | 1188856.6859 | 2654997.4783 | 1188859.8513
18 | 2655013.2683 | 1188832.2005 | 2655011.4283 | 1188823.9394
19 | 2655117.2903 | 1188838.6706 | 2655118.6086 | 1188837.3144 | 2655125.5401 | 1188827.2709
20 | 2655059.8114 | 1188861.8764 | 2655076.015 | 1188857.849
21 | 2655146.8954 | 1188796.328 | 2655145.7761 | 1188797.9497
22 | 2655158.0918 | 1188778.9894 | 2655152.9328 | 1188787.5801 | 2655146.8954 | 1188796.328
23 | 2655145.7761 | 1188797.9497 | 2655125.5401 | 1188827.2709
24 | 2655158.0918 | 1188778.9894 | 2655160.1799 | 1188767.6022 | 2655162.4685 | 1188758.4626 | 2655167.1494 | 1188744.6535 | 2655174.6484 | 1188723.8442 | 2655180.593 | 1188705.3441 | 2655182.337 | 1188705.7838
25 | 2655158.0918 | 1188778.9894 | 2655166.0732 | 1188773.7044 | 2655202.504 | 1188758.129
26 | 2655269.9025 | 1188717.1962 | 2655237.9902 | 1188717.8356 | 2655224.9894 | 1188716.5372 | 2655182.337 | 1188705.7838
27 | 2655206.3683 | 1188756.477 | 2655202.504 | 1188758.129
28 | 2655269.9025 | 1188717.1962 | 2655270.3793 | 1188707.6842 | 2655268.4144 | 1188686.6987 | 2655268.0257 | 1188680.0445
29 | 2655268.0257 | 1188680.0445 | 2655266.8402 | 1188659.7468 | 2655266.0063 | 1188641.829 | 2655264.2731 | 1188631.7593
30 | 2655021.051 | 1188718.0172 | 2655015.8486 | 1188708.0972 | 2655014.9535 | 1188706.7529
31 | 2655010.4847 | 1188700.0414 | 2655014.9535 | 1188706.7529
32 | 2655021.051 | 1188718.0172 | 2655021.051 | 1188718.0172 | 2655025.1995 | 1188727.3946
33 | 2655010.4847 | 1188700.0414 | 2655000.103 | 1188684.4497
34 | 2655031.4424 | 1188741.6076 | 2655028.1573 | 1188734.0804 | 2655025.1995 | 1188727.3946
35 | 2654990.427 | 1188668.9196 | 2654996.6327 | 1188679.2379 | 2655000.103 | 1188684.4497
36 | 2655031.4424 | 1188741.6076 | 2655038.1973 | 1188757.0856 | 2655039.1928 | 1188758.9143
37 | 2654990.427 | 1188668.9196 | 2654985.6624 | 1188662.8057 | 2654981.6834 | 1188659.2005 | 2654978.0531 | 1188656.6547 | 2654966.1382 | 1188650.8754 | 2654951.1307 | 1188644.6454
38 | 2654990.427 | 1188668.9196 | 2655011.9155 | 1188657.9885 | 2655020.6675 | 1188653.4997 | 2655024.4616 | 1188652.6948
39 | 2654951.1307 | 1188644.6454 | 2654939.4935 | 1188640.1917 | 2654900.9983 | 1188628.6329
40 | 2654951.1307 | 1188644.6454 | 2654936.8456 | 1188656.9324 | 2654935.9708 | 1188657.4699
41 | 2655024.4616 | 1188652.6948 | 2655031.8181 | 1188651.1341 | 2655036.661 | 1188653.7022 | 2655040.8263 | 1188661.934 | 2655044.5922 | 1188664.6701 | 2655053.4364 | 1188665.9188 | 2655057.6697 | 1188664.3132
42 | 2655057.6697 | 1188664.3132 | 2655065.4845 | 1188661.3492 | 2655067.0793 | 1188661.8959
43 | 2655075.2775 | 1188676.3809 | 2655070.8706 | 1188664.556 | 2655068.1838 | 1188662.2745 | 2655067.0793 | 1188661.8959
44 | 2654895.2676 | 1188626.9122 | 2654900.9983 | 1188628.6329
45 | 2654932.9411 | 1188659.3313 | 2654935.9708 | 1188657.4699
46 | 2654895.2676 | 1188626.9122 | 2654901.0727 | 1188608.5773 | 2654903.0086 | 1188603.6143
47 | 2654895.2676 | 1188626.9122 | 2654887.7007 | 1188623.0111
48 | 2654942.6832 | 1188680.7771 | 2654932.9411 | 1188659.3313
49 | 2655029.129 | 1188422.5032 | 2655046.07 | 1188418.5443
50 | 2655029.129 | 1188422.5032 | 2655027.3684 | 1188422.8127
51 | 2654914.4198 | 1188449.866 | 2654974.0269 | 1188432.1916 | 2655027.3684 | 1188422.8127
52 | 2654223.6359 | 1188711.3655 | 2654374.0752 | 1188640 | 2654401.5724 | 1188629.9996
53 | 2654401.5724 | 1188629.9996 | 2654406.4719 | 1188623.0068 | 2654469.2944 | 1188576.0068 | 2654530.7097 | 1188562.1689 | 2654573.9031 | 1188534.8802 | 2654610.9748 | 1188513.0946 | 2654667.7113 | 1188493.8457 | 2654722.728 | 1188483.3643 | 2654718.839 | 1188486.5639 | 2654716.5985 | 1188490.5123 | 2654715.752 | 1188496.3301 | 2654716.5606 | 1188541.4072 | 2654786.169 | 1188571.7826
54 | 2654401.5724 | 1188629.9996 | 2654439.9325 | 1188627.4577 | 2654453.7258 | 1188627.194 | 2654461.3656 | 1188627.5414 | 2654467.86 | 1188628.8679 | 2654488.4003 | 1188633.1904 | 2654496.3925 | 1188635.8869 | 2654501.8228 | 1188638.471 | 2654506.1299 | 1188641.2673 | 2654514.4152 | 1188647.242
55 | 2654077.4321 | 1188711.9444 | 2654076.4209 | 1188721.7185 | 2654142.3727 | 1188729.7631 | 2654156.7271 | 1188730.6823 | 2654171.0961 | 1188730.0007 | 2654189.4464 | 1188725.9643 | 2654223.6359 | 1188711.3655
56 | 2654223.6359 | 1188711.3655 | 2654226.5225 | 1188716.0498 | 2654227.9063 | 1188717.8161
57 | 2654786.169 | 1188571.7826 | 2654808.3933 | 1188582.125 | 2654854.2524 | 1188605.7672
58 | 2654556.0482 | 1188256.6949 | 2654596.8561 | 1188269.5738 | 2654636.6035 | 1188290.8258 | 2654661.887 | 1188307.9549 | 2654675.6469 | 1188317.2857 | 2654701.8289 | 1188336.2464 | 2654771.3377 | 1188469.5229 | 2654772.2817 | 1188513.0893 | 2654773.8913 | 1188552.2705 | 2654786.169 | 1188571.7826
59 | 2654771.494 | 1188680.087 | 2654769.757 | 1188671.5219 | 2654767.166 | 1188662.0818 | 2654763.1568 | 1188651.7504 | 2654758.802 | 1188641.6716 | 2654755.0633 | 1188635.1227 | 2654746.1935 | 1188621.634 | 2654732.785 | 1188601.4891 | 2654718.9301 | 1188576.7709 | 2654717.5364 | 1188569.0094 | 2654716.5606 | 1188541.4072 | 2654786.169 | 1188571.7826
60 | 2654514.4152 | 1188647.242 | 2654530.925 | 1188659.1474 | 2654536.3519 | 1188662.0985 | 2654542.0852 | 1188664.074 | 2654546.9814 | 1188664.9969 | 2654557.1788 | 1188665.0787 | 2654563.6418 | 1188663.9925 | 2654570.5802 | 1188661.7878 | 2654579.4615 | 1188658.9782 | 2654583.341 | 1188658.4688 | 2654586.0153 | 1188658.8045 | 2654588.4403 | 1188659.7049 | 2654591.0071 | 1188661.7961 | 2654592.5362 | 1188663.9112 | 2654593.4735 | 1188666.5212 | 2654593.4967 | 1188669.8344 | 2654593.2332 | 1188671.1141
61 | 2654914.4198 | 1188449.866 | 2654934.1922 | 1188472.2488 | 2654950.4182 | 1188479.5795 | 2654965.1352 | 1188489.2532 | 2654976.9334 | 1188510.2622 | 2654971.5367 | 1188525.6324 | 2654964.316 | 1188539.4406
62 | 2654964.316 | 1188539.4406 | 2655038.7565 | 1188546.0499 | 2655089.3748 | 1188550.2063 | 2655098.4926 | 1188549.9345
63 | 2654964.316 | 1188539.4406 | 2654951.6175 | 1188550.0411 | 2654930.8299 | 1188568.5164 | 2654918.8781 | 1188577.5564 | 2654916.7038 | 1188579.8168
64 | 2654019.5276 | 1188900.8501 | 2654019.1417 | 1188888.662 | 2654017.6588 | 1188879.7214 | 2654005.5478 | 1188839.8232 | 2654002.3922 | 1188822.674 | 2654002.835 | 1188777.8084 | 2654005.2978 | 1188760.9879 | 2654009.0319 | 1188747.8364 | 2654021.14 | 1188728.8905
65 | 2654021.14 | 1188728.8905 | 2654026.075 | 1188727.2007 | 2654040.8613 | 1188722.5314 | 2654052.542 | 1188720.5246 | 2654076.4209 | 1188721.7185 | 2654077.4321 | 1188711.9444
66 | 2654021.14 | 1188728.8905 | 2653977.1156 | 1188741.3451 | 2653955.387 | 1188746.1632 | 2653944.843 | 1188748.1583 | 2653938.8866 | 1188748.9273 | 2653932.326 | 1188749.0238 | 2653925.4537 | 1188748.1615 | 2653920.8503 | 1188746.9082
67 | 2654019.5276 | 1188900.8501 | 2654019.3481 | 1188910.5984 | 2654023.936 | 1188925.3814 | 2654026.3627 | 1188932.0181 | 2654023.5129 | 1188938.4627 | 2654018.7536 | 1188938.442 | 2654012.2334 | 1188934.9368 | 2654008.96 | 1188935.074 | 2654007.8138 | 1188942.9237 | 2654016.8811 | 1188953.2445 | 2654022.0393 | 1188958.9276 | 2654024.9843 | 1188962.2115 | 2654022.4201 | 1188965.7459 | 2654017.0555 | 1188966.8871 | 2654003.2403 | 1188965.4284 | 2653995.4869 | 1188967.5819 | 2653995.8691 | 1188974.2558 | 2654005.5749 | 1188986.5057 | 2654010.4089 | 1188995.143 | 2654010.1 | 1189012.4833 | 2654009.9154 | 1189032.9487 | 2654008.2672 | 1189034.7126 | 2654000.8273 | 1189035.0902 | 2653989.3321 | 1189039.4334 | 2653980.1746 | 1189049.2787 | 2653968.4797 | 1189059.7014 | 2653959.6998 | 1189060.6561 | 2653953.4898 | 1189056.5979 | 2653949.3951 | 1189048.8567 | 2653943.6266 | 1189028.7935 | 2653939.9529 | 1189023.4241 | 2653920.1434 | 1189010.0494 | 2653916.7574 | 1189006.6059 | 2653913.7721 | 1188990.8591 | 2653908.5436 | 1188976.882
68 | 2654077.4321 | 1188711.9444 | 2654076.6108 | 1188706.7826
69 | 2654227.9063 | 1188717.8161 | 2654228.2945 | 1188718.3116 | 2654230.708 | 1188719.6453 | 2654238.4313 | 1188720.8714 | 2654255.6537 | 1188722.9768
70 | 2654556.0482 | 1188256.6949 | 2654547.9174 | 1188254.5328
71 | 2654771.494 | 1188680.087 | 2654760.1723 | 1188697.849 | 2654756.8743 | 1188703.4435
72 | 2654771.494 | 1188680.087 | 2654774.5503 | 1188702.8722 | 2654775.2417 | 1188712.3394 | 2654774.9859 | 1188720.2859 | 2654774.7392 | 1188727.2431 | 2654773.4043 | 1188740.594 | 2654769.226 | 1188767.9378 | 2654766.8196 | 1188790.0171 | 2654765.7318 | 1188805.5492 | 2654765.5719 | 1188814.6862
73 | 2654756.8743 | 1188703.4435 | 2654752.4477 | 1188710.9525 | 2654749.7004 | 1188713.6066 | 2654747.3074 | 1188715.0522 | 2654744.2399 | 1188716.0136 | 2654740.026 | 1188716.0047
74 | 2654776.5205 | 1188866.0374 | 2654772.1241 | 1188852.1894 | 2654767.6464 | 1188833.0488 | 2654766.362 | 1188823.3761 | 2654765.5719 | 1188814.6862
75 | 2654883.2609 | 1188620.7222 | 2654854.2524 | 1188605.7672
76 | 2654903.0086 | 1188603.6143 | 2654907.1655 | 1188592.9577 | 2654912.4861 | 1188584.2015 | 2654916.7038 | 1188579.8168
77 | 2655301.7427 | 1188583.3785 | 2655292.7636 | 1188593.1819 | 2655290.5479 | 1188595.0858
78 | 2655287.6535 | 1188597.5729 | 2655290.5479 | 1188595.0858
79 | 2654588.2331 | 1188681.6042 | 2654591.278 | 1188677.2517 | 2654592.8342 | 1188673.0524 | 2654593.2332 | 1188671.1141
80 | 2654279.2929 | 1188725.8665 | 2654255.6537 | 1188722.9768
81 | 2654710.3447 | 1188709.1224 | 2654710.9616 | 1188695.865 | 2654710.1227 | 1188683.3281
82 | 2654710.1227 | 1188683.3281 | 2654715.0662 | 1188686.5862 | 2654718.4473 | 1188690.5304 | 2654721.8197 | 1188697.0982 | 2654723.234 | 1188705.1045 | 2654724.6856 | 1188708.1861 | 2654727.5544 | 1188710.5915 | 2654734.5117 | 1188714.6684 | 2654739.4956 | 1188716.0036 | 2654740.026 | 1188716.0047
83 | 2654776.5205 | 1188866.0374 | 2654781.6093 | 1188869.2302 | 2654788.854 | 1188876.8785 | 2654805.043 | 1188886.4875 | 2654814.1545 | 1188897.6772
84 | 2654776.5205 | 1188866.0374 | 2654779.6539 | 1188874.5375 | 2654783.0244 | 1188881.2943 | 2654786.6182 | 1188886.9859 | 2654792.2253 | 1188894.3858 | 2654795.5908 | 1188899.186 | 2654797.487 | 1188903.6836 | 2654798.9534 | 1188907.6437 | 2654799.9791 | 1188912.2446 | 2654801.2014 | 1188922.039 | 2654802.2709 | 1188932.6881 | 2654802.3203 | 1188937.2912 | 2654801.8535 | 1188942.4565 | 2654800.8672 | 1188947.7171 | 2654799.2422 | 1188952.7606 | 2654791.754 | 1188969.2236 | 2654786.2284 | 1188983.7701 | 2654781.9194 | 1188997.9053 | 2654784.5634 | 1189002.3542 | 2654789.0701 | 1189012.4678
85 | 2654883.2609 | 1188620.7222 | 2654887.7007 | 1188623.0111
86 | 2655264.2731 | 1188631.7593 | 2655264.0878 | 1188630.6828 | 2655264.1985 | 1188623.6466
87 | 2654997.4783 | 1188859.8513 | 2654998.0117 | 1188863.7654 | 2654996.3427 | 1188888.6057
88 | 2655014.2704 | 1188836.6994 | 2655013.2683 | 1188832.2005
89 | 2654396.3727 | 1188958.4587 | 2654395.9965 | 1188957.8153
90 | 2654400.7325 | 1188965.9138 | 2654396.3727 | 1188958.4587
91 | 2654371.8528 | 1188917.4911 | 2654378.3578 | 1188927.7003 | 2654391.256 | 1188944.449 | 2654392.5454 | 1188947.7626 | 2654394.4228 | 1188954.3611 | 2654395.7454 | 1188957.386 | 2654395.9965 | 1188957.8153
92 | 2654371.8528 | 1188917.4911 | 2654380.0777 | 1188918.0439 | 2654396.545 | 1188917.3238
93 | 2654298.7359 | 1188963.0202 | 2654293.5687 | 1188916.3138 | 2654291.3259 | 1188901.2072 | 2654289.8007 | 1188894.4452 | 2654287.4723 | 1188887.9427 | 2654284.0319 | 1188880.4184 | 2654278.5369 | 1188870.6853 | 2654277.6862 | 1188867.7649 | 2654277.6924 | 1188864.552 | 2654278.3939 | 1188862.057 | 2654279.6048 | 1188859.7333 | 2654281.6351 | 1188857.8951 | 2654284.4477 | 1188857.2758 | 2654287.8988 | 1188857.7296 | 2654291.2719 | 1188859.2165 | 2654294.4056 | 1188861.8686 | 2654298.2261 | 1188867.0061 | 2654303.8099 | 1188874.5165 | 2654308.2436 | 1188879.3261 | 2654314.153 | 1188884.5715 | 2654325.7529 | 1188893.1259 | 2654355.442 | 1188912.9285 | 2654362.1522 | 1188915.6576 | 2654371.8528 | 1188917.4911
94 | 2654396.545 | 1188917.3238 | 2654401.5497 | 1188917.1049 | 2654401.5497 | 1188917.1049
95 | 2654298.7359 | 1188963.0202 | 2654295.6201 | 1188970.1849 | 2654295.7107 | 1188977.0117 | 2654297.4346 | 1188985.4099 | 2654297.8924 | 1188989.5941 | 2654297.2587 | 1188993.0348 | 2654295.9553 | 1188994.6127 | 2654294.2784 | 1188995.3313 | 2654291.8407 | 1188994.9979 | 2654287.3141 | 1188992.8779 | 2654281.9762 | 1188989.3831 | 2654274.1666 | 1188980.8854
96 | 2654321.4696 | 1189012.9877 | 2654308.1065 | 1188991.9881 | 2654305.2759 | 1188986.1925 | 2654302.7181 | 1188979.7657 | 2654300.7431 | 1188972.9884 | 2654298.7359 | 1188963.0202
97 | 2654578.5256 | 1189007.6655 | 2654554.4893 | 1188987.0572 | 2654546.2216 | 1188981.1675 | 2654530.1987 | 1188972.5612 | 2654433.4103 | 1188926.2106 | 2654422.6813 | 1188921.7106 | 2654414.6287 | 1188918.9914 | 2654408.4778 | 1188917.6682 | 2654401.5497 | 1188917.1049
98 | 2654320.6483 | 1189050.5569 | 2654322.8559 | 1189030.8436 | 2654322.5793 | 1189020.98 | 2654321.4696 | 1189012.9877
99 | 2654321.4696 | 1189012.9877 | 2654329.571 | 1189022.9334 | 2654337.5324 | 1189035.7016 | 2654344.6625 | 1189048.4512 | 2654348.062 | 1189052.0619 | 2654352.3382 | 1189055.7138 | 2654356.9194 | 1189057.6899 | 2654364.6798 | 1189058.9832 | 2654379.5204 | 1189059.9038
100 | 2654578.5256 | 1189007.6655 | 2654572.3641 | 1188988.2762 | 2654568.1636 | 1188964.6136 | 2654568.4022 | 1188952.6535 | 2654586.6457 | 1188940.2238
101 | 2654578.5256 | 1189007.6655 | 2654595.345 | 1189022.5827 | 2654602.4743 | 1189027.0057 | 2654626.4558 | 1189041.8882 | 2654635.3643 | 1189049.4181 | 2654647.3774 | 1189061.9236 | 2654652.0558 | 1189067.4472 | 2654655.1153 | 1189072.3556 | 2654657.2389 | 1189077.0109 | 2654658.3187 | 1189081.5456 | 2654659.6229 | 1189090.7404 | 2654660.7886 | 1189103.4137 | 2654662.9126 | 1189113.8723 | 2654665.7988 | 1189124.3823 | 2654686.1664 | 1189182.4786 | 2654690.5332 | 1189206.243 | 2654690.4441 | 1189216.0032 | 2654689.3075 | 1189232.7133 | 2654690.4696 | 1189239.928 | 2654693.1305 | 1189243.3653 | 2654697.2755 | 1189245.4822 | 2654701.3098 | 1189245.519 | 2654704.5199 | 1189243.1025 | 2654706.6331 | 1189239.7088 | 2654708.1688 | 1189231.9073 | 2654708.9261 | 1189215.8052 | 2654710.364 | 1189206.1796 | 2654719.0972 | 1189175.2642 | 2654723.939 | 1189154.5523 | 2654727.7073 | 1189130.3065 | 2654730.2223 | 1189123.0031 | 2654733.5846 | 1189117.2973 | 2654760.2812 | 1189089.5923 | 2654764.2526 | 1189084.0144 | 2654767.9028 | 1189072.697 | 2654773.9656 | 1189039.4337 | 2654780.154 | 1189004.9487 | 2654781.9194 | 1188997.9053 | 2654784.5634 | 1189002.3542 | 2654789.0701 | 1189012.4678
102 | 2654578.5256 | 1189007.6655 | 2654595.345 | 1189022.5827 | 2654589.2509 | 1189027.5966 | 2654588.088 | 1189029.6538 | 2654587.5501 | 1189033.4399 | 2654588.3441 | 1189038.3833 | 2654590.1639 | 1189043.7362 | 2654593.8684 | 1189052.3526 | 2654595.1818 | 1189056.3779 | 2654595.7782 | 1189060.3967 | 2654594.5148 | 1189067.6226
103 | 2654320.6483 | 1189050.5569 | 2654317.456 | 1189046.8036 | 2654312.6384 | 1189039.7671 | 2654308.3153 | 1189034.5583 | 2654303.0151 | 1189030.2745 | 2654292.6615 | 1189024.7665 | 2654288.5721 | 1189022.3725 | 2654284.4882 | 1189019.3783 | 2654281.2716 | 1189015.7804
104 | 2654379.5204 | 1189059.9038 | 2654390.0869 | 1189060.5592 | 2654409.1372 | 1189064.1786
105 | 2654790.5549 | 1189032.7483 | 2654789.0701 | 1189012.4678
106 | 2654789.0701 | 1189012.4678 | 2654806.3523 | 1189038.3105
107 | 2654586.6457 | 1188940.2238 | 2654605.3043 | 1188957.548
108 | 2654586.6457 | 1188940.2238 | 2654583.9019 | 1188934.9736
109 | 2654594.5148 | 1189067.6226 | 2654596.2755 | 1189073.1439
110 | 2654612.5892 | 1189093.0293 | 2654610.9327 | 1189088.9064 | 2654609.8767 | 1189086.7734 | 2654608.5931 | 1189085.3498 | 2654603.2108 | 1189081.732 | 2654599.0489 | 1189078.1032 | 2654596.769 | 1189074.6916 | 2654596.2755 | 1189073.1439
111 | 2655264.1985 | 1188623.6466 | 2655264.1985 | 1188623.6466 | 2655266.3545 | 1188620.1337
112 | 2655287.6535 | 1188597.5729 | 2655278.9776 | 1188605.028 | 2655270.4404 | 1188613.4762 | 2655266.3545 | 1188620.1337

## bus_geodata
| x | y | coords
0 | 2655075.7198 | 1188789.4215
1 | 2655077.2448 | 1188788.3818
2 | 2655064.0965 | 1188797.3462
3 | 2655087.6992 | 1188781.2541
4 | 2655053.9966 | 1188782.3367
5 | 2655047.9603 | 1188808.5597
6 | 2655082.6222 | 1188822.988
7 | 2655048.1481 | 1188773.6452
8 | 2655005.3963 | 1188801.3536
9 | 2655098.3724 | 1188852.2922
10 | 2655041.8881 | 1188763.8658
11 | 2655002.6848 | 1188801.7623
12 | 2655011.4283 | 1188823.9394
13 | 2655101.7673 | 1188865.1096
14 | 2655117.2903 | 1188838.6706
15 | 2655076.015 | 1188857.849
16 | 2655146.8954 | 1188796.328
17 | 2655145.7761 | 1188797.9497
18 | 2655158.0918 | 1188778.9894
19 | 2655125.5401 | 1188827.2709
20 | 2655182.337 | 1188705.7838
21 | 2655202.504 | 1188758.129
22 | 2655269.9025 | 1188717.1962
23 | 2655206.3683 | 1188756.477
24 | 2655268.0257 | 1188680.0445
25 | 2655014.9535 | 1188706.7529
26 | 2655021.051 | 1188718.0172
27 | 2655010.4847 | 1188700.0414
28 | 2655025.1995 | 1188727.3946
29 | 2655000.103 | 1188684.4497
30 | 2655031.4424 | 1188741.6076
31 | 2654990.427 | 1188668.9196
32 | 2655039.1928 | 1188758.9143
33 | 2654951.1307 | 1188644.6454
34 | 2655024.4616 | 1188652.6948
35 | 2655057.6697 | 1188664.3132
36 | 2655067.0793 | 1188661.8959
37 | 2655075.2775 | 1188676.381
38 | 2654900.9983 | 1188628.6329
39 | 2654935.9708 | 1188657.4699
40 | 2654895.2676 | 1188626.9122
41 | 2654932.9411 | 1188659.3313
42 | 2655046.07 | 1188418.5443
43 | 2655029.129 | 1188422.5032
44 | 2655027.3684 | 1188422.8127
45 | 2654401.5724 | 1188629.9996
46 | 2654223.6359 | 1188711.3655
47 | 2654786.169 | 1188571.7826
48 | 2654514.4152 | 1188647.242
49 | 2654914.4198 | 1188449.866
50 | 2654964.316 | 1188539.4406
51 | 2654021.14 | 1188728.8905
52 | 2654019.5276 | 1188900.8501
53 | 2654077.4321 | 1188711.9444
54 | 2653920.8503 | 1188746.9082
55 | 2654227.9063 | 1188717.8161
56 | 2654076.6108 | 1188706.7826
57 | 2654556.0482 | 1188256.6949
58 | 2654547.9174 | 1188254.5328
59 | 2654771.494 | 1188680.087
60 | 2654756.8743 | 1188703.4435
61 | 2654765.5719 | 1188814.6862
62 | 2654854.2524 | 1188605.7672
63 | 2655098.4926 | 1188549.9345
64 | 2654916.7038 | 1188579.8168
65 | 2655301.7427 | 1188583.3785
66 | 2655290.5479 | 1188595.0858
67 | 2654593.2332 | 1188671.1141
68 | 2653908.5436 | 1188976.882
69 | 2654255.6537 | 1188722.9768
70 | 2654710.1227 | 1188683.3281
71 | 2654710.3447 | 1188709.1224
72 | 2654740.026 | 1188716.0047
73 | 2654776.5205 | 1188866.0374
74 | 2654883.2609 | 1188620.7222
75 | 2655264.2731 | 1188631.7593
76 | 2654903.0086 | 1188603.6143
77 | 2655059.8114 | 1188861.8764
78 | 2654942.6832 | 1188680.7771
79 | 2654887.7007 | 1188623.0111
80 | 2654953.3737 | 1188794.1944
81 | 2654997.4783 | 1188859.8513
82 | 2655013.2683 | 1188832.2005
83 | 2654996.3427 | 1188888.6057
84 | 2655014.2704 | 1188836.6994
85 | 2654396.3727 | 1188958.4587
86 | 2654395.9965 | 1188957.8153
87 | 2654400.7324 | 1188965.9138
88 | 2654371.8528 | 1188917.4911
89 | 2654396.545 | 1188917.3238
90 | 2654298.7359 | 1188963.0202
91 | 2654401.5497 | 1188917.1049
92 | 2654274.1666 | 1188980.8854
93 | 2654321.4696 | 1189012.9877
94 | 2654588.2331 | 1188681.6042
95 | 2654578.5256 | 1189007.6655
96 | 2654320.6483 | 1189050.5569
97 | 2654379.5204 | 1189059.9038
98 | 2654814.1545 | 1188897.6772
99 | 2654789.0701 | 1189012.4678
100 | 2654586.6457 | 1188940.2238
101 | 2654594.5148 | 1189067.6226
102 | 2654596.2755 | 1189073.1439
103 | 2654790.5549 | 1189032.7483
104 | 2654806.3523 | 1189038.3105
105 | 2654605.3043 | 1188957.548
106 | 2654583.9019 | 1188934.9736
107 | 2654612.5892 | 1189093.0293
108 | 2654409.1372 | 1189064.1786
109 | 2654281.2716 | 1189015.7804
110 | 2655264.1985 | 1188623.6466
111 | 2655266.3545 | 1188620.1337
112 | 2655287.6535 | 1188597.5729
113 | 2654279.2929 | 1188725.8665
114 | 2655064.0965 | 1188797.3462

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99583 | -0.029129 | 0.0029922 | 0.00074991
1 | 0.9958 | -0.029332 | 0.0029261 | 0.00073335
2 | 0.99611 | -0.027161 | 0 | 0
3 | 0.99566 | -0.030349 | 0.007985 | 0.0020012
4 | 0.99853 | -0.010232 | 0.004458 | 0.0011173
5 | 0.99503 | -0.034753 | 0.0073341 | 0.0018381
6 | 0.99425 | -0.040224 | 0.0054619 | 0.0013689
7 | 1 | 0 | -0.13175 | -0.032848
8 | 0.993 | -0.04902 | 0 | 0
9 | 0.99254 | -0.052252 | 0 | 0
10 | 0.99946 | -0.003833 | 0.0019738 | 0.00049469
11 | 0.99293 | -0.049565 | 0 | 0
12 | 0.99262 | -0.051706 | 0.0034227 | 0.0008578
13 | 0.99248 | -0.052703 | 0.0033523 | 0.00084017
14 | 0.99195 | -0.056425 | 0.0014829 | 0.00037165
15 | 0.99206 | -0.055655 | 0.0074106 | 0.0018573
16 | 0.99104 | -0.06292 | 0.0024481 | 0.00061355
17 | 0.99106 | -0.062724 | 0.0012392 | 0.00031056
18 | 0.99082 | -0.064464 | 0 | 0
19 | 0.99163 | -0.058727 | 0.0050467 | 0.0012648
20 | 0.99052 | -0.066602 | 0.00058137 | 0.00014571
21 | 0.99049 | -0.066809 | 0.00072522 | 0.00018176
22 | 0.99026 | -0.068479 | 0 | 0
23 | 0.99046 | -0.066978 | 0.0039586 | 0.00099211
24 | 0.99015 | -0.069263 | 0.00035548 | 8.9091e-05
25 | 0.99712 | -0.020546 | 0.0009166 | 0.00022972
26 | 0.99752 | -0.017624 | 0.0019859 | 0.00049771
27 | 0.99687 | -0.022311 | 0.0003141 | 7.8722e-05
28 | 0.99788 | -0.015083 | 0.001381 | 0.00034612
29 | 0.99631 | -0.026357 | 0.00085344 | 0.00021389
30 | 0.99845 | -0.011026 | 0.0025895 | 0.000649
31 | 0.99578 | -0.030156 | 0 | 0
32 | 0.99921 | -0.0055827 | 0.0023719 | 0.00059445
33 | 0.99468 | -0.038082 | 0 | 0
34 | 0.99557 | -0.031632 | 0.0015192 | 0.00038076
35 | 0.99543 | -0.032588 | 0.001478 | 0.00037041
36 | 0.99542 | -0.032676 | 0.00026208 | 6.5683e-05
37 | 0.99541 | -0.032782 | 0.00060853 | 0.00015251
38 | 0.99356 | -0.046267 | 0.00053333 | 0.00013367
39 | 0.99465 | -0.038353 | 0.00051678 | 0.00012952
40 | 0.99344 | -0.047166 | 0 | 0
41 | 0.99464 | -0.038383 | 0 | 0
42 | 0.99106 | -0.063975 | 0.0020649 | 0.0005175
43 | 0.99112 | -0.06361 | 0 | 0
44 | 0.99112 | -0.063573 | 0.0021653 | 0.00054267
45 | 0.99158 | -0.061658 | 0 | 0
46 | 0.99143 | -0.06289 | 0 | 0
47 | 0.99219 | -0.056528 | 0 | 0
48 | 0.99152 | -0.062084 | 4.3628e-05 | 1.0934e-05
49 | 0.99183 | -0.058568 | 0 | 0
50 | 0.99257 | -0.053345 | 0 | 0
51 | 0.99138 | -0.063441 | 0 | 0
52 | 0.99135 | -0.063686 | 0 | 0
53 | 0.99139 | -0.063308 | 0 | 0
54 | 0.99137 | -0.063489 | 4.0235e-05 | 1.0084e-05
55 | 0.99143 | -0.062917 | 6.6592e-05 | 1.6689e-05
56 | 0.99139 | -0.063311 | 4.7461e-05 | 1.1895e-05
57 | 0.99158 | -0.060945 | 0 | 0
58 | 0.99156 | -0.061032 | 0.001007 | 0.00025239
59 | 0.99057 | -0.06846 | 0 | 0
60 | 0.99048 | -0.069102 | 0.00027882 | 6.9878e-05
61 | 0.99005 | -0.072369 | 0.00010814 | 2.7103e-05
62 | 0.99293 | -0.050935 | 0.00057614 | 0.00014439
63 | 0.99242 | -0.054355 | 0.00073589 | 0.00018443
64 | 0.99301 | -0.050177 | 0.00040936 | 0.0001026
65 | 0.98997 | -0.070542 | 0.00013483 | 3.3791e-05
66 | 0.98997 | -0.07052 | 0.0004759 | 0.00011927
67 | 0.99148 | -0.062373 | 0.00010662 | 2.6722e-05
68 | 0.99131 | -0.06408 | 9.2713e-05 | 2.3236e-05
69 | 0.99142 | -0.062998 | 0.00014122 | 3.5392e-05
70 | 0.99038 | -0.069797 | 0 | 0
71 | 0.99036 | -0.069921 | 0.00046946 | 0.00011766
72 | 0.99041 | -0.069568 | 0.0015328 | 0.00038416
73 | 0.98986 | -0.073828 | 0 | 0
74 | 0.99328 | -0.048348 | 0.0004353 | 0.0001091
75 | 0.99003 | -0.070106 | 0.00039845 | 9.986e-05
76 | 0.99323 | -0.048654 | 0.00056725 | 0.00014217
77 | 0.99189 | -0.056868 | 0.0071605 | 0.0017946
78 | 0.99461 | -0.038581 | 0.00083313 | 0.0002088
79 | 0.99333 | -0.04793 | 0.00059328 | 0.00014869
80 | 0.99215 | -0.055021 | 0.010139 | 0.0025411
81 | 0.99199 | -0.056196 | 0.0042649 | 0.0010689
82 | 0.99253 | -0.052384 | 0.0041316 | 0.0010355
83 | 0.99177 | -0.057743 | 0.0052821 | 0.0013238
84 | 0.9925 | -0.05256 | 0.0037748 | 0.00094606
85 | 0.98705 | -0.094951 | 8.2753e-05 | 2.074e-05
86 | 0.98705 | -0.09495 | 9.9597e-05 | 2.4961e-05
87 | 0.98705 | -0.094956 | 4.9379e-05 | 1.2376e-05
88 | 0.98706 | -0.094836 | 0 | 0
89 | 0.9871 | -0.094538 | 0.00011122 | 2.7875e-05
90 | 0.98678 | -0.096944 | 0 | 0
91 | 0.98711 | -0.094471 | 8.6824e-05 | 2.176e-05
92 | 0.98677 | -0.097044 | 0.00015796 | 3.9588e-05
93 | 0.98672 | -0.097372 | 0 | 0
94 | 0.99147 | -0.062396 | 0.00019226 | 4.8184e-05
95 | 0.98749 | -0.09162 | 0 | 0
96 | 0.98672 | -0.097422 | 0 | 0
97 | 0.98665 | -0.097883 | 4.3633e-05 | 1.0936e-05
98 | 0.98985 | -0.073893 | 0.00012433 | 3.1161e-05
99 | 0.98931 | -0.077984 | 0 | 0
100 | 0.98746 | -0.091874 | 0 | 0
101 | 0.98743 | -0.092056 | 0 | 0
102 | 0.98743 | -0.092091 | 0.00012651 | 3.1707e-05
103 | 0.98931 | -0.078017 | 0.00015639 | 3.9196e-05
104 | 0.98931 | -0.077999 | 4.606e-05 | 1.1544e-05
105 | 0.98745 | -0.091915 | 0.00015651 | 3.9225e-05
106 | 0.98746 | -0.091884 | 0.00015394 | 3.8581e-05
107 | 0.98741 | -0.092215 | 0.00045667 | 0.00011445
108 | 0.98663 | -0.098058 | 0.00056669 | 0.00014203
109 | 0.98671 | -0.097489 | 0.00012048 | 3.0196e-05
110 | 0.99001 | -0.070214 | 0.0002314 | 5.7995e-05
111 | 0.99001 | -0.070259 | 0.00032794 | 8.2189e-05
112 | 0.98997 | -0.070496 | 0.00013085 | 3.2793e-05
113 | 0.99141 | -0.063031 | 0.00013452 | 3.3713e-05
114 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.010913 | 0.0027349 | -0.010912 | -0.0027348 | 3.0622e-07 | 9.3766e-08 | 0.016306 | 0.016306 | 0.016306 | 0.99583 | -0.029129 | 0.9958 | -0.029332 | 6.0393
1 | -0.013905 | -0.0034849 | 0.013909 | 0.0034861 | 3.7894e-06 | 1.2744e-06 | 0.020777 | 0.020777 | 0.020777 | 0.99583 | -0.029129 | 0.99611 | -0.027161 | 7.6952
2 | 0.0079861 | 0.0020015 | -0.007985 | -0.0020012 | 1.1244e-06 | 2.6788e-07 | 0.011934 | 0.011934 | 0.011934 | 0.9958 | -0.029332 | 0.99566 | -0.030349 | 4.4199
3 | -0.093474 | -0.023456 | 0.093694 | 0.02354 | 0.00022014 | 8.4433e-05 | 0.13964 | 0.13964 | 0.13964 | 0.99611 | -0.027161 | 0.99853 | -0.010232 | 51.7201
4 | 0.038475 | 0.0096564 | -0.038435 | -0.009641 | 4.0511e-05 | 1.5326e-05 | 0.05748 | 0.05748 | 0.05748 | 0.99611 | -0.027161 | 0.99503 | -0.034753 | 21.2889
5 | 0.041091 | 0.010313 | -0.041016 | -0.010285 | 7.4387e-05 | 2.8199e-05 | 0.061387 | 0.061388 | 0.061388 | 0.99611 | -0.027161 | 0.99425 | -0.040224 | 22.7361
6 | -0.098152 | -0.024657 | 0.098292 | 0.024711 | 0.00013989 | 5.3668e-05 | 0.14629 | 0.14629 | 0.14629 | 0.99853 | -0.010232 | 1 | 0 | 54.1805
7 | 0.0311 | 0.0078029 | -0.031039 | -0.0077799 | 6.1436e-05 | 2.3039e-05 | 0.046512 | 0.046512 | 0.046512 | 0.99503 | -0.034753 | 0.993 | -0.04902 | 17.2268
8 | 0.035554 | 0.0089162 | -0.035495 | -0.0088939 | 5.9178e-05 | 2.2327e-05 | 0.053213 | 0.053213 | 0.053213 | 0.99425 | -0.040224 | 0.99254 | -0.052252 | 19.7086
9 | 0.032663 | 0.0081365 | -0.032645 | -0.0081301 | 1.7117e-05 | 6.4311e-06 | 0.048585 | 0.048585 | 0.048585 | 1 | 0 | 0.99946 | -0.003833 | 17.9945
10 | 0.019705 | 0.0049391 | -0.019703 | -0.0049386 | 1.4875e-06 | 5.3675e-07 | 0.029528 | 0.029528 | 0.029528 | 0.993 | -0.04902 | 0.99293 | -0.049565 | 10.9363
11 | 0.011334 | 0.0028408 | -0.01133 | -0.0028395 | 4.2139e-06 | 1.318e-06 | 0.016984 | 0.016984 | 0.016984 | 0.993 | -0.04902 | 0.99262 | -0.051706 | 6.2905
12 | 0.0033525 | 0.00084008 | -0.0033523 | -0.00084017 | 2.0901e-07 | -9.097e-08 | 0.0050261 | 0.0050261 | 0.0050261 | 0.99254 | -0.052252 | 0.99248 | -0.052703 | 1.8615
13 | 0.017563 | 0.0043993 | -0.017553 | -0.0043958 | 1.013e-05 | 3.5938e-06 | 0.02633 | 0.02633 | 0.02633 | 0.99254 | -0.052252 | 0.99195 | -0.056425 | 9.7519
14 | 0.014579 | 0.0036544 | -0.014572 | -0.0036521 | 6.8677e-06 | 2.3438e-06 | 0.021857 | 0.021857 | 0.021857 | 0.99254 | -0.052252 | 0.99206 | -0.055655 | 8.0953
15 | 0.030672 | 0.0076354 | -0.030664 | -0.0076326 | 7.3298e-06 | 2.7453e-06 | 0.045646 | 0.045646 | 0.045646 | 0.99946 | -0.003833 | 0.99921 | -0.0055827 | 16.9061
16 | 0.010147 | 0.0025433 | -0.010139 | -0.0025411 | 7.6615e-06 | 2.2605e-06 | 0.015206 | 0.015206 | 0.015206 | 0.99293 | -0.049565 | 0.99215 | -0.055021 | 5.6319
17 | 0.0095569 | 0.0023952 | -0.0095481 | -0.0023928 | 8.7685e-06 | 2.4873e-06 | 0.014322 | 0.014322 | 0.014322 | 0.99293 | -0.049565 | 0.99199 | -0.056196 | 5.3046
18 | 0.0079072 | 0.0019817 | -0.0079065 | -0.0019815 | 7.4204e-07 | 1.7601e-07 | 0.011854 | 0.011854 | 0.011854 | 0.99262 | -0.051706 | 0.99253 | -0.052384 | 4.3902
19 | 0.01607 | 0.0040241 | -0.016065 | -0.0040223 | 5.1107e-06 | 1.7837e-06 | 0.024106 | 0.024106 | 0.024106 | 0.99195 | -0.056425 | 0.99163 | -0.058727 | 8.9281
20 | 0.0071616 | 0.0017948 | -0.0071604 | -0.0017946 | 1.2022e-06 | 2.4684e-07 | 0.010742 | 0.010742 | 0.010742 | 0.99206 | -0.055655 | 0.99189 | -0.056868 | 3.9785
21 | -0.0097731 | -0.002445 | 0.0097733 | 0.0024451 | 2.647e-07 | 7.6419e-08 | 0.014672 | 0.014672 | 0.014672 | 0.99104 | -0.06292 | 0.99106 | -0.062724 | 5.4342
22 | 0.0073249 | 0.0018314 | -0.0073234 | -0.0018311 | 1.5582e-06 | 3.3329e-07 | 0.010997 | 0.010997 | 0.010997 | 0.99104 | -0.06292 | 0.99082 | -0.064464 | 4.0729
23 | -0.011012 | -0.0027556 | 0.011019 | 0.0027575 | 6.0765e-06 | 1.8778e-06 | 0.016533 | 0.016533 | 0.016533 | 0.99106 | -0.062724 | 0.99163 | -0.058727 | 6.1233
24 | 0.002638 | 0.00065729 | -0.0026372 | -0.00065801 | 7.7256e-07 | -7.1912e-07 | 0.0039604 | 0.0039607 | 0.0039607 | 0.99082 | -0.064464 | 0.99052 | -0.066602 | 1.4669
25 | 0.0046854 | 0.0011738 | -0.0046839 | -0.0011738 | 1.5199e-06 | -4.8811e-08 | 0.0070364 | 0.0070366 | 0.0070366 | 0.99082 | -0.064464 | 0.99049 | -0.066809 | 2.6062
26 | 0.0020558 | 0.00051231 | -0.0020553 | -0.00051325 | 5.2926e-07 | -9.4135e-07 | 0.0030874 | 0.0030878 | 0.0030878 | 0.99052 | -0.066602 | 0.99026 | -0.068479 | 1.1436
27 | 0.0039587 | 0.00099209 | -0.0039586 | -0.00099211 | 9.275e-08 | -1.8416e-08 | 0.0059471 | 0.0059471 | 0.0059471 | 0.99049 | -0.066809 | 0.99046 | -0.066978 | 2.2026
28 | 0.0020553 | 0.00051325 | -0.0020551 | -0.00051364 | 2.2173e-07 | -3.941e-07 | 0.0030878 | 0.0030879 | 0.0030879 | 0.99026 | -0.068479 | 0.99015 | -0.069263 | 1.1437
29 | 0.0016996 | 0.00042455 | -0.0016994 | -0.0004251 | 1.9733e-07 | -5.4767e-07 | 0.0025537 | 0.0025539 | 0.0025539 | 0.99015 | -0.069263 | 0.99003 | -0.070106 | 0.9459
30 | -0.022284 | -0.005526 | 0.022292 | 0.0055292 | 8.833e-06 | 3.23e-06 | 0.033234 | 0.033233 | 0.033234 | 0.99712 | -0.020546 | 0.99752 | -0.017624 | 12.3087
31 | 0.021367 | 0.0052962 | -0.021362 | -0.0052944 | 5.109e-06 | 1.8598e-06 | 0.031866 | 0.031866 | 0.031866 | 0.99712 | -0.020546 | 0.99687 | -0.022311 | 11.8021
32 | -0.024278 | -0.0060269 | 0.024287 | 0.00603 | 8.3829e-06 | 3.0903e-06 | 0.036196 | 0.036196 | 0.036196 | 0.99752 | -0.017624 | 0.99788 | -0.015083 | 13.4059
33 | 0.021048 | 0.0052157 | -0.021036 | -0.0052115 | 1.1522e-05 | 4.1876e-06 | 0.031397 | 0.031397 | 0.031397 | 0.99687 | -0.022311 | 0.99631 | -0.026357 | 11.6285
34 | -0.025668 | -0.0063761 | 0.025682 | 0.0063814 | 1.4176e-05 | 5.2495e-06 | 0.038255 | 0.038255 | 0.038255 | 0.99788 | -0.015083 | 0.99845 | -0.011026 | 14.1686
35 | 0.020183 | 0.0049976 | -0.020172 | -0.0049938 | 1.0363e-05 | 3.7474e-06 | 0.030122 | 0.030122 | 0.030122 | 0.99631 | -0.026357 | 0.99578 | -0.030156 | 11.1564
36 | -0.028271 | -0.0070304 | 0.028292 | 0.0070382 | 2.0995e-05 | 7.8266e-06 | 0.042114 | 0.042114 | 0.042114 | 0.99845 | -0.011026 | 0.99921 | -0.0055827 | 15.5979
37 | 0.016303 | 0.0040254 | -0.016286 | -0.0040193 | 1.7359e-05 | 6.0666e-06 | 0.024341 | 0.024342 | 0.024342 | 0.99578 | -0.030156 | 0.99468 | -0.038082 | 9.0154
38 | 0.0038689 | 0.00096842 | -0.0038681 | -0.00096861 | 7.888e-07 | -1.8855e-07 | 0.005781 | 0.0057812 | 0.0057812 | 0.99578 | -0.030156 | 0.99557 | -0.031632 | 2.1412
39 | 0.014936 | 0.0036816 | -0.01492 | -0.003676 | 1.6372e-05 | 5.6141e-06 | 0.022322 | 0.022323 | 0.022323 | 0.99468 | -0.038082 | 0.99356 | -0.046267 | 8.2676
40 | 0.00135 | 0.00033774 | -0.0013499 | -0.00033798 | 5.0559e-08 | -2.3845e-07 | 0.0020193 | 0.0020194 | 0.0020194 | 0.99468 | -0.038082 | 0.99465 | -0.038353 | 0.74793
41 | 0.0023489 | 0.00058786 | -0.0023486 | -0.00058826 | 3.1024e-07 | -4.0518e-07 | 0.0035105 | 0.0035107 | 0.0035107 | 0.99557 | -0.031632 | 0.99543 | -0.032588 | 1.3002
42 | 0.00087063 | 0.00021785 | -0.00087062 | -0.00021797 | 1.0614e-08 | -1.2648e-07 | 0.0013013 | 0.0013014 | 0.0013014 | 0.99543 | -0.032588 | 0.99542 | -0.032676 | 0.48199
43 | 0.00060854 | 0.00015229 | -0.00060853 | -0.00015251 | 8.9386e-09 | -2.216e-07 | 0.0009096 | 0.00090968 | 0.00090968 | 0.99542 | -0.032676 | 0.99541 | -0.032782 | 0.33692
44 | 0.014386 | 0.0035423 | -0.014385 | -0.0035417 | 1.7297e-06 | 5.8779e-07 | 0.021524 | 0.021524 | 0.021524 | 0.99356 | -0.046267 | 0.99344 | -0.047166 | 7.9718
45 | 0.00083315 | 0.00020846 | -0.00083315 | -0.0002085 | 3.4464e-09 | -4.4825e-08 | 0.0012463 | 0.0012463 | 0.0012463 | 0.99465 | -0.038353 | 0.99464 | -0.038383 | 0.4616
46 | 0.0059533 | 0.0014869 | -0.0059521 | -0.0014868 | 1.2181e-06 | 1.5059e-07 | 0.0089154 | 0.0089155 | 0.0089155 | 0.99344 | -0.047166 | 0.99323 | -0.048654 | 3.302
47 | 0.0084313 | 0.0020548 | -0.0084305 | -0.0020546 | 8.4453e-07 | 2.146e-07 | 0.012609 | 0.012609 | 0.012609 | 0.99344 | -0.047166 | 0.99333 | -0.04793 | 4.6698
48 | 0.00083315 | 0.0002085 | -0.00083313 | -0.0002088 | 2.2825e-08 | -2.9683e-07 | 0.0012463 | 0.0012464 | 0.0012464 | 0.99464 | -0.038383 | 0.99461 | -0.038581 | 0.46164
49 | -0.0020648 | -0.0005175 | 0.002065 | 0.00051731 | 1.0434e-07 | -1.8406e-07 | 0.0031002 | 0.0031002 | 0.0031002 | 0.99106 | -0.063975 | 0.99112 | -0.06361 | 1.1482
50 | -0.002065 | -0.00051731 | 0.002065 | 0.0005173 | 1.0721e-08 | -1.8915e-08 | 0.0031002 | 0.0031001 | 0.0031002 | 0.99112 | -0.06361 | 0.99112 | -0.063573 | 1.1482
51 | -0.0042303 | -0.00106 | 0.0042332 | 0.0010596 | 2.9277e-06 | -3.7423e-07 | 0.006351 | 0.0063505 | 0.006351 | 0.99112 | -0.063573 | 0.99183 | -0.058568 | 2.3522
52 | 0.00052283 | 0.00011657 | -0.00052276 | -0.00011906 | 7.4175e-08 | -2.4904e-06 | 0.00077974 | 0.00078055 | 0.00078055 | 0.99158 | -0.061658 | 0.99143 | -0.06289 | 0.28909
53 | -0.00086537 | -0.00019955 | 0.00086588 | 0.00019334 | 5.1685e-07 | -6.2089e-06 | 0.0012927 | 0.0012907 | 0.0012927 | 0.99158 | -0.061658 | 0.99219 | -0.056528 | 0.47879
54 | 0.00034254 | 8.2982e-05 | -0.00034252 | -8.4488e-05 | 1.9285e-08 | -1.5056e-06 | 0.00051303 | 0.00051355 | 0.00051355 | 0.99158 | -0.061658 | 0.99152 | -0.062084 | 0.19021
55 | 0.00018043 | 3.4038e-05 | -0.00018042 | -3.6112e-05 | 7.1937e-09 | -2.0733e-06 | 0.00026731 | 0.00026788 | 0.00026788 | 0.99143 | -0.06289 | 0.99139 | -0.063308 | 0.099216
56 | 0.00034233 | 8.5022e-05 | -0.00034233 | -8.5121e-05 | 1.2747e-09 | -9.9399e-08 | 0.00051353 | 0.00051356 | 0.00051356 | 0.99143 | -0.06289 | 0.99143 | -0.062917 | 0.19021
57 | -0.0068179 | -0.0016508 | 0.0068228 | 0.0016518 | 4.9455e-06 | 9.1845e-07 | 0.010205 | 0.010205 | 0.010205 | 0.99219 | -0.056528 | 0.99293 | -0.050935 | 3.7796
58 | 0.0010077 | 0.00024705 | -0.001007 | -0.00025228 | 6.0276e-07 | -5.2345e-06 | 0.0015093 | 0.0015112 | 0.0015112 | 0.99219 | -0.056528 | 0.99158 | -0.060945 | 0.5597
59 | 0.0049444 | 0.0012104 | -0.0049365 | -0.0012104 | 7.8118e-06 | 6.1286e-08 | 0.0074052 | 0.0074062 | 0.0074062 | 0.99219 | -0.056528 | 0.99057 | -0.06846 | 2.743
60 | 0.00029889 | 7.3553e-05 | -0.00029888 | -7.4754e-05 | 1.1717e-08 | -1.2005e-06 | 0.00044808 | 0.0004485 | 0.0004485 | 0.99152 | -0.062084 | 0.99148 | -0.062373 | 0.16611
61 | -0.0042332 | -0.0010596 | 0.0042362 | 0.0010592 | 3.051e-06 | -3.9253e-07 | 0.0063505 | 0.0063499 | 0.0063505 | 0.99183 | -0.058568 | 0.99257 | -0.053345 | 2.352
62 | 0.000736 | 0.00018274 | -0.00073589 | -0.00018443 | 1.0194e-07 | -1.6958e-06 | 0.0011028 | 0.0011034 | 0.0011034 | 0.99257 | -0.053345 | 0.99242 | -0.054355 | 0.40866
63 | -0.0049722 | -0.0012419 | 0.0049744 | 0.001242 | 2.1652e-06 | 2.4922e-08 | 0.0074527 | 0.0074524 | 0.0074527 | 0.99257 | -0.053345 | 0.99301 | -0.050177 | 2.7603
64 | 9.272e-05 | 1.6383e-05 | -9.2718e-05 | -1.8682e-05 | 2.1014e-09 | -2.2996e-06 | 0.00013708 | 0.00013771 | 0.00013771 | 0.99138 | -0.063441 | 0.99135 | -0.063686 | 0.051003
65 | -0.00013296 | -2.5139e-05 | 0.00013296 | 2.4284e-05 | 1.604e-09 | -8.5439e-07 | 0.000197 | 0.00019678 | 0.000197 | 0.99138 | -0.063441 | 0.99139 | -0.063308 | 0.072964
66 | 4.0235e-05 | 8.7558e-06 | -4.0235e-05 | -1.0084e-05 | 2.3266e-10 | -1.328e-06 | 5.9951e-05 | 6.0392e-05 | 6.0392e-05 | 0.99138 | -0.063441 | 0.99137 | -0.063489 | 0.022367
67 | 9.2718e-05 | 1.8682e-05 | -9.2713e-05 | -2.3236e-05 | 4.2231e-09 | -4.5537e-06 | 0.00013771 | 0.00013917 | 0.00013917 | 0.99135 | -0.063686 | 0.99131 | -0.06408 | 0.051544
68 | 4.7461e-05 | 1.1828e-05 | -4.7461e-05 | -1.1895e-05 | 1.6548e-11 | -6.7389e-08 | 7.1213e-05 | 7.1237e-05 | 7.1237e-05 | 0.99139 | -0.063308 | 0.99139 | -0.063311 | 0.026384
69 | 0.00027574 | 6.8432e-05 | -0.00027574 | -6.8799e-05 | 3.0495e-09 | -3.6708e-07 | 0.00041361 | 0.00041374 | 0.00041374 | 0.99143 | -0.062917 | 0.99142 | -0.062998 | 0.15324
70 | 0.001007 | 0.00025228 | -0.001007 | -0.00025239 | 1.199e-08 | -1.0391e-07 | 0.0015112 | 0.0015112 | 0.0015112 | 0.99158 | -0.060945 | 0.99156 | -0.061032 | 0.55972
71 | 0.0022814 | 0.00057023 | -0.0022812 | -0.00057051 | 2.0191e-07 | -2.7706e-07 | 0.0034266 | 0.0034267 | 0.0034267 | 0.99057 | -0.06846 | 0.99048 | -0.069102 | 1.2691
72 | 0.0026551 | 0.00064015 | -0.0026538 | -0.00064137 | 1.3382e-06 | -1.2273e-06 | 0.0039797 | 0.0039803 | 0.0039803 | 0.99057 | -0.06846 | 0.99005 | -0.072369 | 1.4742
73 | 0.0020024 | 0.00050063 | -0.0020023 | -0.00050088 | 1.285e-07 | -2.4351e-07 | 0.0030078 | 0.0030079 | 0.0030079 | 0.99048 | -0.069102 | 0.99041 | -0.069568 | 1.114
74 | 0.0025456 | 0.00061427 | -0.0025452 | -0.00061477 | 4.7906e-07 | -4.9293e-07 | 0.0038177 | 0.003818 | 0.003818 | 0.99005 | -0.072369 | 0.98986 | -0.073828 | 1.4141
75 | -0.007399 | -0.0017961 | 0.0074015 | 0.0017967 | 2.4947e-06 | 5.3721e-07 | 0.011068 | 0.011068 | 0.011068 | 0.99293 | -0.050935 | 0.99328 | -0.048348 | 4.0992
76 | -0.0053837 | -0.0013446 | 0.0053849 | 0.0013446 | 1.1273e-06 | 7.4257e-08 | 0.0080658 | 0.0080657 | 0.0080658 | 0.99301 | -0.050177 | 0.99323 | -0.048654 | 2.9873
77 | -0.00013483 | -3.3791e-05 | 0.00013483 | 3.3582e-05 | 4.1541e-10 | -2.0833e-07 | 0.00020266 | 0.00020258 | 0.00020266 | 0.98997 | -0.070542 | 0.98997 | -0.07052 | 0.075058
78 | -0.00061072 | -0.00015285 | 0.00061073 | 0.0001528 | 2.0063e-09 | -4.8295e-08 | 0.0009179 | 0.00091788 | 0.0009179 | 0.98997 | -0.07052 | 0.98997 | -0.070496 | 0.33996
79 | 0.00019226 | 4.8032e-05 | -0.00019226 | -4.8184e-05 | 6.1131e-10 | -1.5155e-07 | 0.00028849 | 0.00028854 | 0.00028854 | 0.99148 | -0.062373 | 0.99147 | -0.062396 | 0.10687
80 | 0.00013452 | 3.3407e-05 | -0.00013452 | -3.3713e-05 | 6.0544e-10 | -3.0686e-07 | 0.00020179 | 0.0002019 | 0.0002019 | 0.99142 | -0.062998 | 0.99141 | -0.063031 | 0.074778
81 | 0.00046947 | 0.00011733 | -0.00046946 | -0.00011766 | 8.022e-09 | -3.2946e-07 | 0.00070525 | 0.00070536 | 0.00070536 | 0.99038 | -0.069797 | 0.99036 | -0.069921 | 0.26125
82 | -0.00046947 | -0.00011733 | 0.00046948 | 0.00011672 | 1.4748e-08 | -6.0601e-07 | 0.00070525 | 0.00070503 | 0.00070525 | 0.99038 | -0.069797 | 0.99041 | -0.069568 | 0.2612
83 | 0.00012433 | 3.0521e-05 | -0.00012433 | -3.116e-05 | 1.0842e-09 | -6.3972e-07 | 0.00018668 | 0.0001869 | 0.0001869 | 0.98986 | -0.073828 | 0.98985 | -0.073893 | 0.069224
84 | 0.0024208 | 0.00058424 | -0.0024195 | -0.00058577 | 1.3002e-06 | -1.5297e-06 | 0.0036313 | 0.003632 | 0.003632 | 0.98986 | -0.073828 | 0.98931 | -0.077984 | 1.3452
85 | -0.0078368 | -0.0019058 | 0.0078372 | 0.0019059 | 4.2812e-07 | 1.0001e-07 | 0.01172 | 0.01172 | 0.01172 | 0.99328 | -0.048348 | 0.99333 | -0.04793 | 4.3407
86 | 0.001301 | 0.00032524 | -0.0013009 | -0.00032534 | 1.939e-08 | -9.7076e-08 | 0.0019551 | 0.0019551 | 0.0019551 | 0.99003 | -0.070106 | 0.99001 | -0.070214 | 0.72411
87 | 0.0052832 | 0.0013239 | -0.0052821 | -0.0013238 | 1.1305e-06 | 6.2491e-08 | 0.0079249 | 0.0079251 | 0.0079251 | 0.99199 | -0.056196 | 0.99177 | -0.057743 | 2.9352
88 | 0.0037749 | 0.00094603 | -0.0037748 | -0.00094605 | 9.212e-08 | -2.4137e-08 | 0.0056594 | 0.0056594 | 0.0056594 | 0.99253 | -0.052384 | 0.9925 | -0.05256 | 2.0961
89 | -0.00013213 | -3.3005e-05 | 0.00013213 | 3.2995e-05 | 1.8369e-11 | -9.5194e-09 | 0.00019916 | 0.00019915 | 0.00019916 | 0.98705 | -0.094951 | 0.98705 | -0.09495 | 0.073761
90 | 4.9379e-05 | 1.2265e-05 | -4.9379e-05 | -1.2375e-05 | 2.9848e-11 | -1.1037e-07 | 7.4402e-05 | 7.4441e-05 | 7.4441e-05 | 0.98705 | -0.094951 | 0.98705 | -0.094956 | 0.027571
91 | -0.00023173 | -5.7956e-05 | 0.00023173 | 5.7351e-05 | 3.6111e-09 | -6.0524e-07 | 0.0003493 | 0.00034908 | 0.0003493 | 0.98705 | -0.09495 | 0.98706 | -0.094836 | 0.12937
92 | -0.0011208 | -0.00027335 | 0.0011209 | 0.00027305 | 4.3911e-08 | -2.9918e-07 | 0.001687 | 0.0016869 | 0.001687 | 0.98706 | -0.094836 | 0.9871 | -0.094538 | 0.62483
93 | 0.00088911 | 0.000216 | -0.00088887 | -0.00021873 | 2.4742e-07 | -2.7331e-06 | 0.001338 | 0.0013389 | 0.0013389 | 0.98706 | -0.094836 | 0.98678 | -0.096944 | 0.4959
94 | -0.0012321 | -0.00030092 | 0.0012321 | 0.00030086 | 1.0751e-08 | -5.9902e-08 | 0.0018546 | 0.0018546 | 0.0018546 | 0.9871 | -0.094538 | 0.98711 | -0.094471 | 0.68689
95 | 0.00015796 | 3.882e-05 | -0.00015796 | -3.9587e-05 | 2.1261e-09 | -7.6721e-07 | 0.00023792 | 0.00023819 | 0.00023819 | 0.98678 | -0.096944 | 0.98677 | -0.097044 | 0.08822
96 | 0.00073091 | 0.00017991 | -0.00073087 | -0.0001806 | 4.1965e-08 | -6.9237e-07 | 0.001101 | 0.0011013 | 0.0011013 | 0.98678 | -0.096944 | 0.98672 | -0.097372 | 0.40788
97 | -0.0013189 | -0.00032262 | 0.0013194 | 0.00032025 | 4.9344e-07 | -2.3767e-06 | 0.0019854 | 0.0019846 | 0.0019854 | 0.98711 | -0.094471 | 0.98749 | -0.09162 | 0.73535
98 | 0.00012049 | 2.9033e-05 | -0.00012049 | -2.9515e-05 | 7.7555e-10 | -4.8228e-07 | 0.00018129 | 0.00018146 | 0.00018146 | 0.98672 | -0.097372 | 0.98672 | -0.097422 | 0.067207
99 | 0.00061038 | 0.00015157 | -0.00061034 | -0.00015258 | 4.2685e-08 | -1.0155e-06 | 0.00091998 | 0.00092034 | 0.00092034 | 0.98672 | -0.097372 | 0.98665 | -0.097883 | 0.34087
100 | 0.00031046 | 7.6406e-05 | -0.00031045 | -7.7404e-05 | 1.0689e-08 | -9.9856e-07 | 0.00046732 | 0.00046768 | 0.00046768 | 0.98749 | -0.09162 | 0.98746 | -0.091874 | 0.17321
101 | -0.0022131 | -0.00054149 | 0.0022171 | 0.00053569 | 3.9468e-06 | -5.797e-06 | 0.0033302 | 0.0033277 | 0.0033302 | 0.98749 | -0.09162 | 0.98931 | -0.077984 | 1.2334
102 | 0.00058323 | 0.00014484 | -0.00058319 | -0.00014575 | 3.4788e-08 | -9.1065e-07 | 0.00087837 | 0.0008787 | 0.0008787 | 0.98749 | -0.09162 | 0.98743 | -0.092056 | 0.32544
103 | 0.00012049 | 2.9515e-05 | -0.00012048 | -3.0196e-05 | 1.0968e-09 | -6.8053e-07 | 0.00018146 | 0.0001817 | 0.0001817 | 0.98672 | -0.097422 | 0.98671 | -0.097489 | 0.067296
104 | 0.0005667 | 0.00014165 | -0.00056669 | -0.00014202 | 1.3662e-08 | -3.776e-07 | 0.00085454 | 0.00085467 | 0.00085467 | 0.98665 | -0.097883 | 0.98663 | -0.098058 | 0.31655
105 | 0.00015639 | 3.8935e-05 | -0.00015639 | -3.9196e-05 | 7.0199e-10 | -2.6089e-07 | 0.00023514 | 0.00023523 | 0.00023523 | 0.98931 | -0.077984 | 0.98931 | -0.078017 | 0.087123
106 | 4.606e-05 | 1.1145e-05 | -4.606e-05 | -1.1544e-05 | 9.2918e-11 | -3.9916e-07 | 6.914e-05 | 6.9279e-05 | 6.9279e-05 | 0.98931 | -0.077984 | 0.98931 | -0.077999 | 0.025659
107 | 0.00015651 | 3.89e-05 | -0.00015651 | -3.9225e-05 | 8.8201e-10 | -3.2489e-07 | 0.00023573 | 0.00023585 | 0.00023585 | 0.98746 | -0.091874 | 0.98745 | -0.091915 | 0.087351
108 | 0.00015394 | 3.8505e-05 | -0.00015394 | -3.858e-05 | 1.9878e-10 | -7.5667e-08 | 0.00023194 | 0.00023197 | 0.00023197 | 0.98746 | -0.091874 | 0.98746 | -0.091884 | 0.085915
109 | 0.00058319 | 0.00014575 | -0.00058319 | -0.00014582 | 2.7922e-09 | -7.3056e-08 | 0.0008787 | 0.00087872 | 0.00087872 | 0.98743 | -0.092056 | 0.98743 | -0.092091 | 0.32545
110 | 0.00045668 | 0.00011412 | -0.00045667 | -0.00011445 | 7.8228e-09 | -3.3564e-07 | 0.00068807 | 0.00068819 | 0.00068819 | 0.98743 | -0.092091 | 0.98741 | -0.092215 | 0.25489
111 | 0.0010695 | 0.00026734 | -0.0010695 | -0.00026739 | 6.6444e-09 | -5.0442e-08 | 0.0016073 | 0.0016073 | 0.0016073 | 0.99001 | -0.070214 | 0.99001 | -0.070259 | 0.5953
112 | 0.0007416 | 0.0001852 | -0.00074157 | -0.0001856 | 2.4229e-08 | -3.9263e-07 | 0.0011144 | 0.0011146 | 0.0011146 | 0.99001 | -0.070259 | 0.98997 | -0.070496 | 0.4128

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.13317 | 0.033203

## res_load
| p_mw | q_mvar
0 | 0.0029922 | 0.00074991
1 | 0.0029261 | 0.00073335
2 | 0.007985 | 0.0020012
3 | 0.004458 | 0.0011173
4 | 0.0073341 | 0.0018381
5 | 0.0054619 | 0.0013689
6 | 0.0014189 | 0.00035562
7 | 0.0019738 | 0.00049469
8 | 0.0034227 | 0.0008578
9 | 0.0033523 | 0.00084017
10 | 0.0014829 | 0.00037165
11 | 0.0074106 | 0.0018573
12 | 0.0024481 | 0.00061355
13 | 0.0012392 | 0.00031056
14 | 0.0050467 | 0.0012648
15 | 0.00058137 | 0.00014571
16 | 0.00072522 | 0.00018176
17 | 0.0039586 | 0.00099211
18 | 0.00035548 | 8.9091e-05
19 | 0.0009166 | 0.00022972
20 | 0.0019859 | 0.00049771
21 | 0.0003141 | 7.8722e-05
22 | 0.001381 | 0.00034612
23 | 0.00085344 | 0.00021389
24 | 0.0025895 | 0.000649
25 | 0.0023719 | 0.00059445
26 | 0.0015192 | 0.00038076
27 | 0.001478 | 0.00037041
28 | 0.00026208 | 6.5683e-05
29 | 0.00060853 | 0.00015251
30 | 0.00053333 | 0.00013367
31 | 0.00051678 | 0.00012952
32 | 0.0020649 | 0.0005175
33 | 0.0021653 | 0.00054267
34 | 4.3628e-05 | 1.0934e-05
35 | 4.0235e-05 | 1.0084e-05
36 | 6.6592e-05 | 1.6689e-05
37 | 4.7461e-05 | 1.1895e-05
38 | 0.001007 | 0.00025239
39 | 0.00027882 | 6.9878e-05
40 | 0.00010814 | 2.7103e-05
41 | 0.00057614 | 0.00014439
42 | 0.00073589 | 0.00018443
43 | 0.00040936 | 0.0001026
44 | 0.00013483 | 3.3791e-05
45 | 0.0004759 | 0.00011927
46 | 0.00010662 | 2.6722e-05
47 | 9.2713e-05 | 2.3236e-05
48 | 0.00014122 | 3.5392e-05
49 | 0.00046946 | 0.00011766
50 | 0.0015328 | 0.00038416
51 | 0.0004353 | 0.0001091
52 | 0.00039845 | 9.986e-05
53 | 0.00056725 | 0.00014217
54 | 0.0071605 | 0.0017946
55 | 0.00083313 | 0.0002088
56 | 0.00059328 | 0.00014869
57 | 0.010139 | 0.0025411
58 | 0.0042649 | 0.0010689
59 | 0.0041316 | 0.0010355
60 | 0.0052821 | 0.0013238
61 | 0.0037748 | 0.00094606
62 | 8.2753e-05 | 2.074e-05
63 | 9.9597e-05 | 2.4961e-05
64 | 4.9379e-05 | 1.2376e-05
65 | 0.00011122 | 2.7875e-05
66 | 8.6824e-05 | 2.176e-05
67 | 0.00015796 | 3.9588e-05
68 | 0.00019226 | 4.8184e-05
69 | 4.3633e-05 | 1.0936e-05
70 | 0.00012433 | 3.1161e-05
71 | 0.00012651 | 3.1707e-05
72 | 0.00015639 | 3.9196e-05
73 | 4.606e-05 | 1.1544e-05
74 | 0.00015651 | 3.9225e-05
75 | 0.00015394 | 3.8581e-05
76 | 0.00045667 | 0.00011445
77 | 0.00056669 | 0.00014203
78 | 0.00012048 | 3.0196e-05
79 | 0.0002314 | 5.7995e-05
80 | 0.00032794 | 8.2189e-05
81 | 0.00013085 | 3.2793e-05
82 | 0.00013452 | 3.3713e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1