## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1403-9_0_7_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1403-9_0_7_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1403-9_0_7_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1403-9_0_7_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1403-9_0_7_node_16 | 0.4 | n |  | TRUE
5 | bus_LV_1403-9_0_7_node_18 | 0.4 | n |  | TRUE
6 | bus_LV_1403-9_0_7_node_15 | 0.4 | n |  | TRUE
7 | bus_LV_1403-9_0_7_node_13 | 0.4 | n |  | TRUE
8 | bus_LV_1403-9_0_7_node_29 | 0.4 | n |  | TRUE
9 | bus_LV_1403-9_0_7_node_11 | 0.4 | n |  | TRUE
10 | bus_LV_1403-9_0_7_node_26 | 0.4 | n |  | TRUE
11 | bus_LV_1403-9_0_7_node_27 | 0.4 | n |  | TRUE
12 | bus_LV_1403-9_0_7_node_28 | 0.4 | n |  | TRUE
13 | bus_LV_1403-9_0_7_node_4 | 0.4 | n |  | TRUE
14 | bus_LV_1403-9_0_7_node_5 | 0.4 | n |  | TRUE
15 | bus_LV_1403-9_0_7_node_6 | 0.4 | n |  | TRUE
16 | bus_LV_1403-9_0_7_node_7 | 0.4 | n |  | TRUE
17 | bus_LV_1403-9_0_7_node_8 | 0.4 | n |  | TRUE
18 | bus_LV_1403-9_0_7_node_23 | 0.4 | n |  | TRUE
19 | bus_LV_1403-9_0_7_node_21 | 0.4 | n |  | TRUE
20 | bus_LV_1403-9_0_7_node_20 | 0.4 | n |  | TRUE
21 | bus_LV_1403-9_0_7_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_1403-9_0_7_node_201 | 0.4 | n |  | TRUE
23 | bus_LV_1403-9_0_7_node_38 | 0.4 | n |  | TRUE
24 | bus_LV_1403-9_0_7_node_24 | 0.4 | n |  | TRUE
25 | bus_LV_1403-9_0_7_node_9 | 0.4 | n |  | TRUE
26 | bus_LV_1403-9_0_7_node_10 | 0.4 | n |  | TRUE
27 | bus_LV_1403-9_0_7_node_12 | 0.4 | n |  | TRUE
28 | bus_LV_1403-9_0_7_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_1403-9_0_7_node_141 | 0.4 | n |  | TRUE
30 | bus_LV_1403-9_0_7_node_17 | 0.4 | n |  | TRUE
31 | bus_LV_1403-9_0_7_node_142 | 0.4 | n |  | TRUE
32 | bus_LV_1403-9_0_7_node_32 | 0.4 | n |  | TRUE
33 | bus_LV_1403-9_0_7_node_34 | 0.4 | n |  | TRUE
34 | bus_LV_1403-9_0_7_node_167 | 0.4 | n |  | TRUE
35 | bus_LV_1403-9_0_7_node_30 | 0.4 | n |  | TRUE
36 | bus_LV_1403-9_0_7_node_166 | 0.4 | n |  | TRUE
37 | bus_LV_1403-9_0_7_node_143 | 0.4 | n |  | TRUE
38 | bus_LV_1403-9_0_7_node_144 | 0.4 | n |  | TRUE
39 | bus_LV_1403-9_0_7_node_191 | 0.4 | n |  | TRUE
40 | bus_LV_1403-9_0_7_node_165 | 0.4 | n |  | TRUE
41 | bus_LV_1403-9_0_7_node_200 | 0.4 | n |  | TRUE
42 | bus_LV_1403-9_0_7_node_197 | 0.4 | n |  | TRUE
43 | bus_LV_1403-9_0_7_node_22 | 0.4 | n |  | TRUE
44 | bus_LV_1403-9_0_7_node_25 | 0.4 | n |  | TRUE
45 | bus_LV_1403-9_0_7_node_109 | 0.4 | n |  | TRUE
46 | bus_LV_1403-9_0_7_node_112 | 0.4 | n |  | TRUE
47 | bus_LV_1403-9_0_7_node_107 | 0.4 | n |  | TRUE
48 | bus_LV_1403-9_0_7_node_35 | 0.4 | n |  | TRUE
49 | bus_LV_1403-9_0_7_node_36 | 0.4 | n |  | TRUE
50 | bus_LV_1403-9_0_7_node_150 | 0.4 | n |  | TRUE
51 | bus_LV_1403-9_0_7_node_149 | 0.4 | n |  | TRUE
52 | bus_LV_1403-9_0_7_node_37 | 0.4 | n |  | TRUE
53 | bus_LV_1403-9_0_7_node_195 | 0.4 | n |  | TRUE
54 | bus_LV_1403-9_0_7_node_196 | 0.4 | n |  | TRUE
55 | bus_LV_1403-9_0_7_node_160 | 0.4 | n |  | TRUE
56 | bus_LV_1403-9_0_7_node_161 | 0.4 | n |  | TRUE
57 | bus_LV_1403-9_0_7_node_162 | 0.4 | n |  | TRUE
58 | bus_LV_1403-9_0_7_node_163 | 0.4 | n |  | TRUE
59 | bus_LV_1403-9_0_7_node_168 | 0.4 | n |  | TRUE
60 | bus_LV_1403-9_0_7_node_164 | 0.4 | n |  | TRUE
61 | bus_LV_1403-9_0_7_node_39 | 0.4 | n |  | TRUE
62 | bus_LV_1403-9_0_7_node_40 | 0.4 | n |  | TRUE
63 | bus_LV_1403-9_0_7_node_41 | 0.4 | n |  | TRUE
64 | bus_LV_1403-9_0_7_node_42 | 0.4 | n |  | TRUE
65 | bus_LV_1403-9_0_7_node_43 | 0.4 | n |  | TRUE
66 | bus_LV_1403-9_0_7_node_44 | 0.4 | n |  | TRUE
67 | bus_LV_1403-9_0_7_node_45 | 0.4 | n |  | TRUE
68 | bus_LV_1403-9_0_7_node_47 | 0.4 | n |  | TRUE
69 | bus_LV_1403-9_0_7_node_46 | 0.4 | n |  | TRUE
70 | bus_LV_1403-9_0_7_node_48 | 0.4 | n |  | TRUE
71 | bus_LV_1403-9_0_7_node_49 | 0.4 | n |  | TRUE
72 | bus_LV_1403-9_0_7_node_50 | 0.4 | n |  | TRUE
73 | bus_LV_1403-9_0_7_node_51 | 0.4 | n |  | TRUE
74 | bus_LV_1403-9_0_7_node_57 | 0.4 | n |  | TRUE
75 | bus_LV_1403-9_0_7_node_52 | 0.4 | n |  | TRUE
76 | bus_LV_1403-9_0_7_node_55 | 0.4 | n |  | TRUE
77 | bus_LV_1403-9_0_7_node_53 | 0.4 | n |  | TRUE
78 | bus_LV_1403-9_0_7_node_54 | 0.4 | n |  | TRUE
79 | bus_LV_1403-9_0_7_node_56 | 0.4 | n |  | TRUE
80 | bus_LV_1403-9_0_7_node_58 | 0.4 | n |  | TRUE
81 | bus_LV_1403-9_0_7_node_59 | 0.4 | n |  | TRUE
82 | bus_LV_1403-9_0_7_node_185 | 0.4 | n |  | TRUE
83 | bus_LV_1403-9_0_7_node_184 | 0.4 | n |  | TRUE
84 | bus_LV_1403-9_0_7_node_183 | 0.4 | n |  | TRUE
85 | bus_LV_1403-9_0_7_node_108 | 0.4 | n |  | TRUE
86 | bus_LV_1403-9_0_7_node_110 | 0.4 | n |  | TRUE
87 | bus_LV_1403-9_0_7_node_111 | 0.4 | n |  | TRUE
88 | bus_LV_1403-9_0_7_node_113 | 0.4 | n |  | TRUE
89 | bus_LV_1403-9_0_7_node_117 | 0.4 | n |  | TRUE
90 | bus_LV_1403-9_0_7_node_115 | 0.4 | n |  | TRUE
91 | bus_LV_1403-9_0_7_node_114 | 0.4 | n |  | TRUE
92 | bus_LV_1403-9_0_7_node_116 | 0.4 | n |  | TRUE
93 | bus_LV_1403-9_0_7_node_118 | 0.4 | n |  | TRUE
94 | bus_LV_1403-9_0_7_node_124 | 0.4 | n |  | TRUE
95 | bus_LV_1403-9_0_7_node_122 | 0.4 | n |  | TRUE
96 | bus_LV_1403-9_0_7_node_139 | 0.4 | n |  | TRUE
97 | bus_LV_1403-9_0_7_node_120 | 0.4 | n |  | TRUE
98 | bus_LV_1403-9_0_7_node_119 | 0.4 | n |  | TRUE
99 | bus_LV_1403-9_0_7_node_121 | 0.4 | n |  | TRUE
100 | bus_LV_1403-9_0_7_node_123 | 0.4 | n |  | TRUE
101 | bus_LV_1403-9_0_7_node_125 | 0.4 | n |  | TRUE
102 | bus_LV_1403-9_0_7_node_134 | 0.4 | n |  | TRUE
103 | bus_LV_1403-9_0_7_node_140 | 0.4 | n |  | TRUE
104 | bus_LV_1403-9_0_7_node_137 | 0.4 | n |  | TRUE
105 | bus_LV_1403-9_0_7_node_182 | 0.4 | n |  | TRUE
106 | bus_LV_1403-9_0_7_node_133 | 0.4 | n |  | TRUE
107 | bus_LV_1403-9_0_7_node_126 | 0.4 | n |  | TRUE
108 | bus_LV_1403-9_0_7_node_127 | 0.4 | n |  | TRUE
109 | bus_LV_1403-9_0_7_node_128 | 0.4 | n |  | TRUE
110 | bus_LV_1403-9_0_7_node_129 | 0.4 | n |  | TRUE
111 | bus_LV_1403-9_0_7_node_130 | 0.4 | n |  | TRUE
112 | bus_LV_1403-9_0_7_node_131 | 0.4 | n |  | TRUE
113 | bus_LV_1403-9_0_7_node_132 | 0.4 | n |  | TRUE
114 | bus_LV_1403-9_0_7_node_135 | 0.4 | n |  | TRUE
115 | bus_LV_1403-9_0_7_node_171 | 0.4 | n |  | TRUE
116 | bus_LV_1403-9_0_7_node_172 | 0.4 | n |  | TRUE
117 | bus_LV_1403-9_0_7_node_170 | 0.4 | n |  | TRUE
118 | bus_LV_1403-9_0_7_node_173 | 0.4 | n |  | TRUE
119 | bus_LV_1403-9_0_7_node_136 | 0.4 | n |  | TRUE
120 | bus_LV_1403-9_0_7_node_138 | 0.4 | n |  | TRUE
121 | bus_LV_1403-9_0_7_node_187 | 0.4 | n |  | TRUE
122 | bus_LV_1403-9_0_7_node_192 | 0.4 | n |  | TRUE
123 | bus_LV_1403-9_0_7_node_186 | 0.4 | n |  | TRUE
124 | bus_LV_1403-9_0_7_node_193 | 0.4 | n |  | TRUE
125 | bus_LV_1403-9_0_7_node_169 | 0.4 | n |  | TRUE
126 | bus_LV_1403-9_0_7_node_194 | 0.4 | n |  | TRUE
127 | bus_MV_138_0_node_256 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1403-9_0_7_load_0 | 0 | 0.00012321 | 3.088e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1403-9_0_7_load_1 | 1 | 8.2047e-05 | 2.0563e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1403-9_0_7_load_2 | 2 | 5.2031e-05 | 1.304e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1403-9_0_7_load_3 | 3 | 5.0866e-05 | 1.2748e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1403-9_0_7_load_18 | 5 | 0.00031772 | 7.9629e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1403-9_0_7_load_15 | 6 | 9.2281e-05 | 2.3128e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1403-9_0_7_load_13 | 7 | 7.2666e-05 | 1.8212e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1403-9_0_7_load_29 | 8 | 4.551e-05 | 1.1406e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1403-9_0_7_load_11 | 9 | 8.6716e-05 | 2.1733e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1403-9_0_7_load_26 | 10 | 5.5e-05 | 1.3784e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1403-9_0_7_load_27 | 11 | 0.00019049 | 4.7741e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1403-9_0_7_load_28 | 12 | 9.635e-05 | 2.4148e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1403-9_0_7_load_4 | 13 | 7.2997e-05 | 1.8295e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1403-9_0_7_load_5 | 14 | 0.00017206 | 4.3122e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1403-9_0_7_load_6 | 15 | 9.899e-05 | 2.4809e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1403-9_0_7_load_8 | 17 | 0.00012152 | 3.0457e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1403-9_0_7_load_23 | 18 | 0.0020251 | 0.00050755 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1403-9_0_7_load_21 | 19 | 0.0016475 | 0.00041289 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1403-9_0_7_load_20 | 20 | 8.7259e-05 | 2.1869e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1403-9_0_7_load_14 | 21 | 0.00012362 | 3.0981e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1403-9_0_7_load_201 | 22 | 0.00012054 | 3.0209e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1403-9_0_7_load_38 | 23 | 0.0029865 | 0.00074849 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1403-9_0_7_load_9 | 25 | 4.786e-05 | 1.1995e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1403-9_0_7_load_10 | 26 | 8.9366e-05 | 2.2397e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1403-9_0_7_load_12 | 27 | 9.9282e-05 | 2.4882e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1403-9_0_7_load_141 | 29 | 0.00013615 | 3.4124e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1403-9_0_7_load_17 | 30 | 8.9074e-05 | 2.2324e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1403-9_0_7_load_142 | 31 | 8.67e-05 | 2.1729e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1403-9_0_7_load_34 | 33 | 0.00017212 | 4.3137e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1403-9_0_7_load_167 | 34 | 0.00038362 | 9.6145e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1403-9_0_7_load_30 | 35 | 0.00019229 | 4.8192e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1403-9_0_7_load_191 | 39 | 0.00014573 | 3.6524e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1403-9_0_7_load_197 | 42 | 0.00010846 | 2.7184e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1403-9_0_7_load_25 | 44 | 0.0012762 | 0.00031984 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1403-9_0_7_load_112 | 46 | 0.002727 | 0.00068345 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1403-9_0_7_load_107 | 47 | 0.0036445 | 0.0009134 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1403-9_0_7_load_35 | 48 | 8.5572e-05 | 2.1446e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1403-9_0_7_load_36 | 49 | 0.00095378 | 0.00023904 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1403-9_0_7_load_150 | 50 | 0.00020311 | 5.0903e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1403-9_0_7_load_149 | 51 | 0.001079 | 0.00027042 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1403-9_0_7_load_195 | 53 | 0.0015017 | 0.00037637 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1403-9_0_7_load_196 | 54 | 8.4098e-05 | 2.1077e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1403-9_0_7_load_160 | 55 | 0.0037926 | 0.00095052 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1403-9_0_7_load_161 | 56 | 0.0011278 | 0.00028264 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1403-9_0_7_load_163 | 58 | 0.0033803 | 0.00084718 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1403-9_0_7_load_168 | 59 | 0.00065528 | 0.00016423 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1403-9_0_7_load_164 | 60 | 0.00046566 | 0.00011671 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1403-9_0_7_load_39 | 61 | 0.0023066 | 0.0005781 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1403-9_0_7_load_41 | 63 | 0.0076046 | 0.0019059 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1403-9_0_7_load_43 | 65 | 0.0012181 | 0.00030529 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1403-9_0_7_load_44 | 66 | 0.00092906 | 0.00023285 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1403-9_0_7_load_45 | 67 | 0.0007775 | 0.00019486 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1403-9_0_7_load_47 | 68 | 0.00077748 | 0.00019486 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1403-9_0_7_load_46 | 69 | 0.00072932 | 0.00018278 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1403-9_0_7_load_49 | 71 | 0.0010686 | 0.00026781 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1403-9_0_7_load_50 | 72 | 0.00060454 | 0.00015151 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1403-9_0_7_load_51 | 73 | 0.0014432 | 0.00036171 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1403-9_0_7_load_57 | 74 | 0.0012413 | 0.0003111 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1403-9_0_7_load_52 | 75 | 0.00052708 | 0.0001321 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1403-9_0_7_load_53 | 77 | 0.0019649 | 0.00049245 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1403-9_0_7_load_54 | 78 | 0.0021258 | 0.00053276 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1403-9_0_7_load_56 | 79 | 0.00086907 | 0.00021781 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1403-9_0_7_load_58 | 80 | 0.0010936 | 0.00027408 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1403-9_0_7_load_59 | 81 | 0.0017563 | 0.00044018 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1403-9_0_7_load_185 | 82 | 0.00025482 | 6.3863e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1403-9_0_7_load_184 | 83 | 0.00026613 | 6.6697e-05 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1403-9_0_7_load_183 | 84 | 0.00081537 | 0.00020435 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1403-9_0_7_load_110 | 86 | 0.0028579 | 0.00071627 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1403-9_0_7_load_111 | 87 | 0.0020823 | 0.00052189 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1403-9_0_7_load_113 | 88 | 0.0039671 | 0.00099425 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1403-9_0_7_load_117 | 89 | 0.00086086 | 0.00021575 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1403-9_0_7_load_114 | 91 | 0.0023877 | 0.00059841 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1403-9_0_7_load_116 | 92 | 0.0011831 | 0.00029652 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1403-9_0_7_load_124 | 94 | 0.0003415 | 8.5587e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1403-9_0_7_load_122 | 95 | 0.0020492 | 0.00051357 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1403-9_0_7_load_120 | 97 | 0.0019766 | 0.00049539 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1403-9_0_7_load_119 | 98 | 0.0027437 | 0.00068764 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1403-9_0_7_load_121 | 99 | 0.0022813 | 0.00057174 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1403-9_0_7_load_123 | 100 | 0.0025527 | 0.00063976 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1403-9_0_7_load_125 | 101 | 0.00232 | 0.00058144 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1403-9_0_7_load_134 | 102 | 0.0024011 | 0.00060177 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1403-9_0_7_load_182 | 105 | 0.0017328 | 0.00043429 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1403-9_0_7_load_133 | 106 | 0.0031472 | 0.00078875 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1403-9_0_7_load_126 | 107 | 0.0010878 | 0.00027263 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1403-9_0_7_load_127 | 108 | 0.0030985 | 0.00077655 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1403-9_0_7_load_129 | 110 | 0.0027719 | 0.00069471 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1403-9_0_7_load_130 | 111 | 0.0010364 | 0.00025973 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1403-9_0_7_load_131 | 112 | 0.0011723 | 0.00029382 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1403-9_0_7_load_132 | 113 | 0.0022562 | 0.00056546 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1403-9_0_7_load_135 | 114 | 0.0031128 | 0.00078014 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1403-9_0_7_load_171 | 115 | 0.00092323 | 0.00023138 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1403-9_0_7_load_172 | 116 | 0.00095646 | 0.00023971 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1403-9_0_7_load_170 | 117 | 0.00080353 | 0.00020138 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1403-9_0_7_load_173 | 118 | 0.000578 | 0.00014486 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1403-9_0_7_load_136 | 119 | 0.0007625 | 0.0001911 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1403-9_0_7_load_138 | 120 | 0.00052078 | 0.00013052 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1403-9_0_7_load_192 | 122 | 0.00025465 | 6.382e-05 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1403-9_0_7_load_186 | 123 | 0.00033734 | 8.4546e-05 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1403-9_0_7_load_193 | 124 | 0.00018546 | 4.648e-05 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1403-9_0_7_load_169 | 125 | 0.002145 | 0.00053758 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1403-9_0_7_load_194 | 126 | 0.0018834 | 0.00047203 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 85 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1403-9_0_7_line_0 | NAYY 4x150 SE | 0 | 1 | 0.056669 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1403-9_0_7_line_1 | NAYY 4x150 SE | 0 | 2 | 0.013171 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1403-9_0_7_line_2 | NAYY 4x150 SE | 1 | 3 | 0.061665 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1403-9_0_7_line_3 | NAYY 4x150 SE | 3 | 7 | 0.013862 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1403-9_0_7_line_4 | NAYY 4x150 SE | 3 | 8 | 0.27475 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1403-9_0_7_line_5 | NAYY 4x150 SE | 4 | 5 | 0.1129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1403-9_0_7_line_6 | NAYY 4x150 SE | 4 | 6 | 0.028433 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1403-9_0_7_line_7 | NAYY 4x150 SE | 5 | 36 | 0.019704 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1403-9_0_7_line_8 | NAYY 4x150 SE | 6 | 30 | 0.013509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1403-9_0_7_line_9 | NAYY 4x150 SE | 7 | 9 | 0.060464 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1403-9_0_7_line_10 | NAYY 4x150 SE | 8 | 12 | 0.016206 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1403-9_0_7_line_11 | NAYY 4x150 SE | 9 | 25 | 0.087498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1403-9_0_7_line_12 | NAYY 4x150 SE | 10 | 11 | 0.05222 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1403-9_0_7_line_13 | NAYY 4x150 SE | 10 | 12 | 0.015277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1403-9_0_7_line_14 | NAYY 4x150 SE | 13 | 14 | 0.030138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
15 | LV_1403-9_0_7_line_15 | NAYY 4x150 SE | 13 | 15 | 0.0046973 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
16 | LV_1403-9_0_7_line_16 | NAYY 4x150 SE | 14 | 16 | 0.049829 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
17 | LV_1403-9_0_7_line_17 | NAYY 4x150 SE | 15 | 17 | 0.051702 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1403-9_0_7_line_18 | NAYY 4x150 SE | 15 | 18 | 0.18166 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
19 | LV_1403-9_0_7_line_19 | NAYY 4x150 SE | 16 | 20 | 0.033578 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
20 | LV_1403-9_0_7_line_20 | NAYY 4x150 SE | 17 | 21 | 0.0034696 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1403-9_0_7_line_21 | NAYY 4x150 SE | 18 | 19 | 0.0053396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
22 | LV_1403-9_0_7_line_22 | NAYY 4x150 SE | 19 | 43 | 0.021686 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
23 | LV_1403-9_0_7_line_23 | NAYY 4x150 SE | 20 | 22 | 0.11513 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
24 | LV_1403-9_0_7_line_24 | NAYY 4x150 SE | 22 | 41 | 0.048535 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
25 | LV_1403-9_0_7_line_25 | NAYY 4x150 SE | 23 | 24 | 0.027184 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1403-9_0_7_line_26 | NAYY 4x150 SE | 24 | 43 | 0.008797 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1403-9_0_7_line_27 | NAYY 4x150 SE | 25 | 26 | 0.036037 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1403-9_0_7_line_28 | NAYY 4x150 SE | 26 | 27 | 0.023048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1403-9_0_7_line_29 | NAYY 4x150 SE | 27 | 28 | 0.14165 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1403-9_0_7_line_30 | NAYY 4x150 SE | 28 | 29 | 0.17341 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1403-9_0_7_line_31 | NAYY 4x150 SE | 29 | 31 | 0.035136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1403-9_0_7_line_32 | NAYY 4x150 SE | 30 | 31 | 0.14169 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1403-9_0_7_line_33 | NAYY 4x150 SE | 31 | 37 | 0.061967 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1403-9_0_7_line_34 | NAYY 4x150 SE | 32 | 33 | 0.12815 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1403-9_0_7_line_35 | NAYY 4x150 SE | 32 | 34 | 0.20828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1403-9_0_7_line_36 | NAYY 4x150 SE | 32 | 35 | 0.045412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1403-9_0_7_line_37 | NAYY 4x150 SE | 33 | 48 | 0.084401 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1403-9_0_7_line_38 | NAYY 4x150 SE | 34 | 40 | 0.062472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1403-9_0_7_line_39 | NAYY 4x150 SE | 35 | 42 | 0.095693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
40 | LV_1403-9_0_7_line_40 | NAYY 4x150 SE | 36 | 39 | 0.022857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1403-9_0_7_line_41 | NAYY 4x150 SE | 36 | 40 | 0.065796 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1403-9_0_7_line_42 | NAYY 4x150 SE | 37 | 38 | 0.081901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1403-9_0_7_line_43 | NAYY 4x150 SE | 38 | 50 | 0.10463 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1403-9_0_7_line_44 | NAYY 4x150 SE | 41 | 42 | 0.15369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
45 | LV_1403-9_0_7_line_45 | NAYY 4x150 SE | 43 | 44 | 0.16459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
46 | LV_1403-9_0_7_line_46 | NAYY 4x150 SE | 44 | 45 | 0.016646 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
47 | LV_1403-9_0_7_line_47 | NAYY 4x150 SE | 45 | 46 | 0.046329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1403-9_0_7_line_48 | NAYY 4x150 SE | 45 | 47 | 0.039033 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
49 | LV_1403-9_0_7_line_49 | NAYY 4x150 SE | 47 | 85 | 0.029347 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
50 | LV_1403-9_0_7_line_50 | NAYY 4x150 SE | 48 | 49 | 0.092216 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1403-9_0_7_line_51 | NAYY 4x150 SE | 49 | 52 | 0.017217 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1403-9_0_7_line_52 | NAYY 4x150 SE | 50 | 51 | 0.094208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1403-9_0_7_line_53 | NAYY 4x150 SE | 52 | 53 | 0.094881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1403-9_0_7_line_54 | NAYY 4x150 SE | 52 | 54 | 0.081199 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1403-9_0_7_line_55 | NAYY 4x150 SE | 53 | 59 | 0.16039 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1403-9_0_7_line_56 | NAYY 4x150 SE | 55 | 56 | 0.024552 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1403-9_0_7_line_57 | NAYY 4x150 SE | 55 | 57 | 0.055933 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1403-9_0_7_line_58 | NAYY 4x150 SE | 56 | 58 | 0.017327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1403-9_0_7_line_59 | NAYY 4x150 SE | 57 | 60 | 0.039382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1403-9_0_7_line_60 | NAYY 4x150 SE | 59 | 125 | 0.17981 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1403-9_0_7_line_61 | NAYY 4x150 SE | 59 | 60 | 0.0046134 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1403-9_0_7_line_62 | NAYY 4x150 SE | 61 | 62 | 0.15229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1403-9_0_7_line_63 | NAYY 4x150 SE | 61 | 63 | 0.017518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1403-9_0_7_line_64 | NAYY 4x150 SE | 62 | 64 | 0.042566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1403-9_0_7_line_65 | NAYY 4x150 SE | 64 | 65 | 0.091264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1403-9_0_7_line_66 | NAYY 4x150 SE | 65 | 66 | 0.020748 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1403-9_0_7_line_67 | NAYY 4x150 SE | 66 | 67 | 0.022315 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1403-9_0_7_line_68 | NAYY 4x150 SE | 67 | 68 | 0.0083889 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1403-9_0_7_line_69 | NAYY 4x150 SE | 68 | 69 | 0.0084478 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1403-9_0_7_line_70 | NAYY 4x150 SE | 69 | 70 | 0.096142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1403-9_0_7_line_71 | NAYY 4x150 SE | 70 | 71 | 0.020711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1403-9_0_7_line_72 | NAYY 4x150 SE | 70 | 72 | 0.01073 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1403-9_0_7_line_73 | NAYY 4x150 SE | 71 | 73 | 0.00040581 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1403-9_0_7_line_74 | NAYY 4x150 SE | 72 | 74 | 0.015318 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1403-9_0_7_line_75 | NAYY 4x150 SE | 73 | 75 | 0.008125 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1403-9_0_7_line_76 | NAYY 4x150 SE | 74 | 76 | 0.0087063 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1403-9_0_7_line_77 | NAYY 4x150 SE | 76 | 80 | 0.07168 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1403-9_0_7_line_78 | NAYY 4x150 SE | 76 | 77 | 0.016329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1403-9_0_7_line_79 | NAYY 4x150 SE | 77 | 78 | 0.029957 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1403-9_0_7_line_80 | NAYY 4x150 SE | 78 | 79 | 0.042589 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1403-9_0_7_line_81 | NAYY 4x150 SE | 79 | 81 | 0.014374 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
82 | LV_1403-9_0_7_line_82 | NAYY 4x150 SE | 81 | 82 | 0.23424 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
83 | LV_1403-9_0_7_line_83 | NAYY 4x150 SE | 82 | 83 | 0.0067387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
84 | LV_1403-9_0_7_line_84 | NAYY 4x150 SE | 83 | 84 | 0.023936 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
85 | LV_1403-9_0_7_line_85 | NAYY 4x150 SE | 84 | 105 | 0.022171 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
86 | LV_1403-9_0_7_line_86 | NAYY 4x150 SE | 85 | 86 | 0.070011 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1403-9_0_7_line_87 | NAYY 4x150 SE | 85 | 87 | 0.031991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
88 | LV_1403-9_0_7_line_88 | NAYY 4x150 SE | 86 | 88 | 0.0038435 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1403-9_0_7_line_89 | NAYY 4x150 SE | 87 | 89 | 0.014145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
90 | LV_1403-9_0_7_line_90 | NAYY 4x150 SE | 89 | 90 | 0.0026042 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
91 | LV_1403-9_0_7_line_91 | NAYY 4x150 SE | 90 | 93 | 0.035861 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
92 | LV_1403-9_0_7_line_92 | NAYY 4x150 SE | 90 | 91 | 0.02454 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1403-9_0_7_line_93 | NAYY 4x150 SE | 91 | 92 | 0.0053194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1403-9_0_7_line_94 | NAYY 4x150 SE | 93 | 94 | 0.17001 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
95 | LV_1403-9_0_7_line_95 | NAYY 4x150 SE | 93 | 95 | 0.015271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1403-9_0_7_line_96 | NAYY 4x150 SE | 94 | 96 | 0.082495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
97 | LV_1403-9_0_7_line_97 | NAYY 4x150 SE | 95 | 97 | 0.014232 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1403-9_0_7_line_98 | NAYY 4x150 SE | 96 | 103 | 0.13386 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
99 | LV_1403-9_0_7_line_99 | NAYY 4x150 SE | 96 | 104 | 0.040152 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1403-9_0_7_line_100 | NAYY 4x150 SE | 97 | 98 | 0.0018989 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1403-9_0_7_line_101 | NAYY 4x150 SE | 98 | 99 | 0.024965 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1403-9_0_7_line_102 | NAYY 4x150 SE | 99 | 100 | 0.029426 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1403-9_0_7_line_103 | NAYY 4x150 SE | 100 | 101 | 0.04223 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1403-9_0_7_line_104 | NAYY 4x150 SE | 101 | 102 | 0.011723 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1403-9_0_7_line_105 | NAYY 4x150 SE | 102 | 106 | 0.0035241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1403-9_0_7_line_106 | NAYY 4x150 SE | 103 | 121 | 0.13793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1403-9_0_7_line_107 | NAYY 4x150 SE | 103 | 122 | 0.086907 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
108 | LV_1403-9_0_7_line_108 | NAYY 4x150 SE | 104 | 120 | 0.024134 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1403-9_0_7_line_109 | NAYY 4x150 SE | 104 | 119 | 0.051008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1403-9_0_7_line_110 | NAYY 4x150 SE | 105 | 126 | 0.24195 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
111 | LV_1403-9_0_7_line_111 | NAYY 4x150 SE | 106 | 113 | 0.018242 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_1403-9_0_7_line_112 | NAYY 4x150 SE | 107 | 108 | 0.021857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_1403-9_0_7_line_113 | NAYY 4x150 SE | 107 | 109 | 0.034582 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_1403-9_0_7_line_114 | NAYY 4x150 SE | 108 | 110 | 0.024544 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_1403-9_0_7_line_115 | NAYY 4x150 SE | 109 | 111 | 0.0049752 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_1403-9_0_7_line_116 | NAYY 4x150 SE | 109 | 112 | 0.032335 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_1403-9_0_7_line_117 | NAYY 4x150 SE | 110 | 113 | 0.011217 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_1403-9_0_7_line_118 | NAYY 4x150 SE | 111 | 114 | 0.021254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_1403-9_0_7_line_119 | NAYY 4x150 SE | 115 | 116 | 0.015065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_1403-9_0_7_line_120 | NAYY 4x150 SE | 115 | 117 | 0.16015 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_1403-9_0_7_line_121 | NAYY 4x150 SE | 116 | 118 | 0.015345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_1403-9_0_7_line_122 | NAYY 4x150 SE | 117 | 125 | 0.019292 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_1403-9_0_7_line_123 | NAYY 4x150 SE | 121 | 123 | 0.064229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_1403-9_0_7_line_124 | NAYY 4x150 SE | 122 | 124 | 0.00060627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
125 | LV_1403-9_0_7_line_125 | NAYY 4x150 SE | 124 | 126 | 0.0095835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1403-9_0_7_trafo_108 | 0.25 MVA 20/0.4 kV | 127 | 85 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28
0 | 2653603.8562 | 1189123.6755 | 2653608.108 | 1189124.8134 | 2653616.6376 | 1189129.648 | 2653619.7632 | 1189135.7794 | 2653628.3371 | 1189149.2748 | 2653638.4015 | 1189159.8709 | 2653642.9326 | 1189161.9325
1 | 2653591.1327 | 1189120.2701 | 2653603.8562 | 1189123.6755
2 | 2653703.1025 | 1189169.7015 | 2653699.0541 | 1189168.0966 | 2653676.1498 | 1189168.9919 | 2653665.0152 | 1189168.8921 | 2653650.7147 | 1189165.4732 | 2653642.9326 | 1189161.9325
3 | 2653708.2576 | 1189181.7873 | 2653707.2021 | 1189174.64 | 2653704.4197 | 1189170.2237 | 2653703.1025 | 1189169.7015
4 | 2653703.1025 | 1189169.7015 | 2653953.4898 | 1189056.5979
5 | 2654084.5842 | 1189349.7445 | 2654099.8414 | 1189344.2792 | 2654107.7204 | 1189342.5383 | 2654115.3734 | 1189342.1739 | 2654122.8337 | 1189342.875 | 2654128.9567 | 1189344.7091 | 2654138.3969 | 1189348.2742 | 2654151.6643 | 1189355.387 | 2654174.5445 | 1189370.5802 | 2654187.4275 | 1189377.1691
6 | 2654084.5842 | 1189349.7445 | 2654092.9448 | 1189376.9207
7 | 2654204.7624 | 1189386.518 | 2654198.9971 | 1189383.0862 | 2654187.4275 | 1189377.1691
8 | 2654098.5668 | 1189389.1151 | 2654095.507 | 1189384.2181 | 2654093.0899 | 1189377.3924 | 2654092.9448 | 1189376.9207
9 | 2653708.2576 | 1189181.7873 | 2653711.5882 | 1189204.3404 | 2653719.5938 | 1189225.891 | 2653722.7487 | 1189240.2246
10 | 2653947.337 | 1189041.6986 | 2653949.3951 | 1189048.8567 | 2653953.4898 | 1189056.5979
11 | 2653722.7487 | 1189240.2246 | 2653727.4789 | 1189261.7151 | 2653731.564 | 1189269.6895 | 2653741.1652 | 1189278.3138 | 2653754.0849 | 1189284.2886 | 2653770.3296 | 1189288.5924 | 2653782.2359 | 1189292.6782
12 | 2653942.5825 | 1189027.2675 | 2653939.9529 | 1189023.4241 | 2653920.1434 | 1189010.0494 | 2653916.7574 | 1189006.6059 | 2653913.7721 | 1188990.8591 | 2653912.7893 | 1188988.2318
13 | 2653942.5825 | 1189027.2675 | 2653943.6266 | 1189028.7935 | 2653947.337 | 1189041.6986
14 | 2654753.1082 | 1189246.6769 | 2654752.2984 | 1189244.4175 | 2654744.6592 | 1189232.4076 | 2654739.2565 | 1189223.5422 | 2654737.9365 | 1189220.7125
15 | 2654754.6932 | 1189251.0987 | 2654753.1082 | 1189246.6769
16 | 2654719.0972 | 1189175.2642 | 2654721.9549 | 1189178.8701 | 2654724.7302 | 1189191.4914 | 2654728.05 | 1189201.2828 | 2654730.2789 | 1189207.7624 | 2654734.7982 | 1189213.9849 | 2654737.9365 | 1189220.7125
17 | 2654754.6932 | 1189251.0987 | 2654754.6932 | 1189251.0987 | 2654753.952 | 1189254.5828 | 2654751.4291 | 1189257.7393 | 2654746.3988 | 1189263.1964 | 2654745.4103 | 1189265.3775 | 2654745.206 | 1189267.6991 | 2654748.9864 | 1189283.8316 | 2654751.641 | 1189291.2823 | 2654752.9368 | 1189294.7072 | 2654754.4058 | 1189298.224
18 | 2654935.942 | 1189263.3428 | 2654754.6932 | 1189251.0987
19 | 2654719.0972 | 1189175.2642 | 2654723.939 | 1189154.5523 | 2654725.8292 | 1189142.3903
20 | 2654755.743 | 1189301.4255 | 2654754.4058 | 1189298.224
21 | 2654935.942 | 1189263.3428 | 2654939.7769 | 1189267.0582
22 | 2654958.4806 | 1189277.3574 | 2654952.5626 | 1189275.6355 | 2654948.3467 | 1189273.7846 | 2654942.0124 | 1189269.224 | 2654939.7769 | 1189267.0582
23 | 2654725.8292 | 1189142.3903 | 2654615.709 | 1189108.7834
24 | 2654594.5148 | 1189067.6226 | 2654596.769 | 1189074.6916 | 2654599.0489 | 1189078.1032 | 2654603.2108 | 1189081.732 | 2654608.5931 | 1189085.3498 | 2654609.8767 | 1189086.7734 | 2654610.9327 | 1189088.9064 | 2654614.7884 | 1189098.5025 | 2654615.599 | 1189101.6117 | 2654615.8279 | 1189104.1152 | 2654615.709 | 1189108.7834
25 | 2654959.2093 | 1189268.5925 | 2654947.8445 | 1189265.342 | 2654944.1399 | 1189263.4514 | 2654941.6128 | 1189260.4154 | 2654939.2967 | 1189253.5411
26 | 2654958.4806 | 1189277.3574 | 2654959.2093 | 1189268.5925
27 | 2653816.5929 | 1189303.4747 | 2653804.6287 | 1189300.3625 | 2653782.2359 | 1189292.6782
28 | 2653816.5929 | 1189303.4747 | 2653827.4711 | 1189306.3044 | 2653832.9585 | 1189308.4327 | 2653837.5756 | 1189312.1408
29 | 2653894.6215 | 1189438.071 | 2653880.3764 | 1189413.3289 | 2653873.1081 | 1189391.2956 | 2653872.1801 | 1189371.5206 | 2653869.0835 | 1189362.2098 | 2653860.837 | 1189353.1083 | 2653851.3911 | 1189341.6725 | 2653845.7902 | 1189325.024 | 2653841.1062 | 1189314.9762 | 2653837.5756 | 1189312.1408
30 | 2654039.445 | 1189533.4585 | 2653894.6215 | 1189438.071
31 | 2654039.445 | 1189533.4585 | 2654046.5289 | 1189539.5632 | 2654048.7857 | 1189540.4841 | 2654051.3997 | 1189540.6967 | 2654053.7226 | 1189540.2062 | 2654055.5126 | 1189538.766 | 2654066.5956 | 1189527.1524
32 | 2654098.5668 | 1189389.1151 | 2654066.5956 | 1189527.1524
33 | 2654124.6541 | 1189532.1088 | 2654115.6572 | 1189528.4699 | 2654109.5291 | 1189525.5352 | 2654102.9854 | 1189523.008 | 2654097.9718 | 1189521.6508 | 2654091.5714 | 1189520.9927 | 2654083.2057 | 1189520.9171 | 2654075.8403 | 1189521.5509 | 2654071.8483 | 1189522.76 | 2654069.0713 | 1189524.5582 | 2654066.5956 | 1189527.1524
34 | 2654396.812 | 1189248.826 | 2654403.6233 | 1189258.849 | 2654412.2239 | 1189270.8894 | 2654418.5735 | 1189277.9955 | 2654425.3997 | 1189285.5396 | 2654446.011 | 1189305.2824 | 2654453.4984 | 1189313.9109 | 2654464.5812 | 1189329.7316 | 2654478.7355 | 1189345.7805 | 2654479.148 | 1189346.5265
35 | 2654396.812 | 1189248.826 | 2654227.4938 | 1189370.1146
36 | 2654396.812 | 1189248.826 | 2654393.4237 | 1189208.7505 | 2654392.8806 | 1189203.5852
37 | 2654538.6503 | 1189401.5263 | 2654535.6302 | 1189396.1709 | 2654520.8099 | 1189381.261 | 2654510.0343 | 1189375.2818 | 2654500.2404 | 1189372.0575 | 2654494.6732 | 1189370.3392 | 2654491.7013 | 1189368.3889 | 2654487.1624 | 1189360.9434 | 2654484.4305 | 1189356.0825 | 2654479.148 | 1189346.5265
38 | 2654227.4938 | 1189370.1146 | 2654239.6791 | 1189393.9383 | 2654248.8443 | 1189409.3299 | 2654258.9308 | 1189424.0406
39 | 2654392.8806 | 1189203.5852 | 2654454.0575 | 1189130.0015
40 | 2654204.7624 | 1189386.518 | 2654206.8398 | 1189391.2506 | 2654215.9996 | 1189406.3976
41 | 2654204.7624 | 1189386.518 | 2654210.2773 | 1189389.8031 | 2654224.6299 | 1189400.0165 | 2654256.1165 | 1189422.3586 | 2654258.9308 | 1189424.0406
42 | 2654124.6541 | 1189532.1088 | 2654123.3342 | 1189537.2331 | 2654121.0518 | 1189547.585 | 2654120.5356 | 1189553.2279 | 2654120.5181 | 1189559.3757 | 2654121.0921 | 1189565.0618 | 2654122.4926 | 1189570.4331 | 2654127.0315 | 1189583.8038 | 2654131.8538 | 1189594.5089 | 2654136.2931 | 1189602.0199 | 2654139.2319 | 1189605.9487 | 2654141.5963 | 1189608.4604
43 | 2654141.5963 | 1189608.4604 | 2654142.0374 | 1189611.9663 | 2654143.1018 | 1189614.8665 | 2654145.789 | 1189617.1031 | 2654165.5557 | 1189633.2353 | 2654167.4626 | 1189635.7318 | 2654168.5328 | 1189638.8321 | 2654168.2659 | 1189641.3533 | 2654167.383 | 1189643.6911 | 2654164.2486 | 1189646.2086 | 2654158.7514 | 1189648.5824 | 2654152.7233 | 1189649.7842 | 2654146.084 | 1189650.2578 | 2654136.2326 | 1189650.8802 | 2654131.3428 | 1189651.8699 | 2654127.1624 | 1189653.6776 | 2654121.2372 | 1189657.8375 | 2654118.7186 | 1189660.5829 | 2654118.2577 | 1189662.6355 | 2654118.9323 | 1189664.7761 | 2654118.9323 | 1189664.7761
44 | 2654454.0575 | 1189130.0015 | 2654594.5148 | 1189067.6226
45 | 2654958.4806 | 1189277.3574 | 2654958.8615 | 1189280.7295 | 2654960.0145 | 1189284.7312 | 2654962.8815 | 1189290.6275 | 2654965.7716 | 1189294.8341 | 2654970.0615 | 1189299.4316 | 2654984.5409 | 1189312.3273 | 2655041.3708 | 1189360.2206 | 2655046.3385 | 1189365.736 | 2655048.4994 | 1189369.6136 | 2655057.664 | 1189396.4574 | 2655058.5325 | 1189401.5349
46 | 2655054.392 | 1189417.2057 | 2655056.9782 | 1189412.9826 | 2655058.1718 | 1189409.2471 | 2655058.7842 | 1189405.684 | 2655058.5325 | 1189401.5349
47 | 2655023.8268 | 1189382.8833 | 2655029.2092 | 1189387.2574 | 2655030.8976 | 1189389.4408 | 2655032.1124 | 1189391.6866 | 2655033.6355 | 1189395.2582 | 2655036.4688 | 1189398.9974 | 2655044.2164 | 1189407.4178 | 2655054.392 | 1189417.2057
48 | 2655054.392 | 1189417.2057 | 2655050.7608 | 1189421.4525 | 2655037.6908 | 1189436.1407 | 2655033.0055 | 1189442.2233 | 2655030.0278 | 1189447.5545
49 | 2655032.4894 | 1189475.9597 | 2655029.8284 | 1189469.2537 | 2655028.4239 | 1189463.571 | 2655027.9524 | 1189458.4415 | 2655028.4829 | 1189452.9989 | 2655030.0278 | 1189447.5545
50 | 2654576.6533 | 1189483.942 | 2654568.1879 | 1189474.9228 | 2654557.5324 | 1189457.4715 | 2654550.8826 | 1189433.9532 | 2654545.9653 | 1189414.4975 | 2654538.6503 | 1189401.5263
51 | 2654589.4551 | 1189495.3836 | 2654581.5648 | 1189489.1749 | 2654576.6533 | 1189483.942
52 | 2654197.1131 | 1189708.1583 | 2654187.0803 | 1189699.5006 | 2654175.9744 | 1189687.9047 | 2654173.7523 | 1189686.5394 | 2654170.4914 | 1189686.1875 | 2654166.4122 | 1189686.9288 | 2654162.9218 | 1189687.4976 | 2654157.7977 | 1189688.2517 | 2654153.9105 | 1189687.9942 | 2654149.9648 | 1189686.6244 | 2654145.0188 | 1189683.7114 | 2654134.1781 | 1189674.8306 | 2654127.9029 | 1189670.4715 | 2654121.2398 | 1189666.8314 | 2654118.9323 | 1189664.7761
53 | 2654589.4551 | 1189495.3836 | 2654591.245 | 1189497.3232 | 2654594.9318 | 1189501.9928 | 2654598.6672 | 1189507.1964 | 2654618.1897 | 1189532.4553 | 2654639.1724 | 1189558.1388 | 2654650.6552 | 1189567.6378
54 | 2654589.4551 | 1189495.3836 | 2654588.2753 | 1189486.768 | 2654580.5572 | 1189476.7254 | 2654578.7202 | 1189469.9159 | 2654578.0303 | 1189460.2598 | 2654573.9337 | 1189449.5053 | 2654571.5406 | 1189437.6101 | 2654569.3373 | 1189418.2681
55 | 2654650.6552 | 1189567.6378 | 2654512.473 | 1189649.0616
56 | 2654436.1699 | 1189588.939 | 2654421.814 | 1189572.6017 | 2654420.1481 | 1189570.3467
57 | 2654476.7576 | 1189623.4964 | 2654474.0517 | 1189624.1721 | 2654471.0988 | 1189624.3343 | 2654468.0047 | 1189623.25 | 2654465.2308 | 1189621.3348 | 2654461.4807 | 1189617.7431 | 2654436.1699 | 1189588.939
58 | 2654420.1481 | 1189570.3467 | 2654418.0847 | 1189567.5538 | 2654410.8801 | 1189555.7193
59 | 2654476.7576 | 1189623.4964 | 2654492.9637 | 1189634.4055 | 2654509.1721 | 1189645.8579
60 | 2654512.473 | 1189649.0616 | 2654517.5828 | 1189654.4074 | 2654534.1778 | 1189670.323 | 2654559.1306 | 1189687.9823 | 2654568.1773 | 1189693.6457 | 2654597.5829 | 1189711.3903 | 2654618.6995 | 1189726.5247 | 2654625.2551 | 1189729.3638 | 2654630.6877 | 1189729.0687 | 2654634.4791 | 1189730.6153 | 2654637.9499 | 1189738.0511 | 2654640.2119 | 1189749.2447 | 2654637.8613 | 1189752.7697 | 2654631.3141 | 1189756.035
61 | 2654509.1721 | 1189645.8579 | 2654509.9074 | 1189646.3775 | 2654512.473 | 1189649.0616
62 | 2655127.3965 | 1189125.4907 | 2655106.0409 | 1189137.0562 | 2655077.875 | 1189152.706 | 2655061.4037 | 1189163.9721 | 2655055.5021 | 1189172.0779 | 2655053.7433 | 1189184.1797 | 2655055.9291 | 1189197.7963 | 2655057.9826 | 1189208.3767 | 2655060.5005 | 1189217.3938 | 2655071.2624 | 1189230.6446 | 2655072.8704 | 1189232.6491
63 | 2655083.8324 | 1189246.3135 | 2655072.8704 | 1189232.6491
64 | 2655145.2159 | 1189161.6639 | 2655129.3396 | 1189143.9078 | 2655127.5161 | 1189135.6975 | 2655126.708 | 1189128.197 | 2655127.3965 | 1189125.4907
65 | 2655145.2159 | 1189161.6639 | 2655208.0104 | 1189227.8903
66 | 2655208.0104 | 1189227.8903 | 2655216.6351 | 1189236.9864 | 2655221.9419 | 1189243.2549
67 | 2655236.3602 | 1189260.2863 | 2655221.9419 | 1189243.2549
68 | 2655241.7805 | 1189266.6889 | 2655236.3602 | 1189260.2863
69 | 2655241.7805 | 1189266.6889 | 2655242.7399 | 1189267.8222 | 2655247.6525 | 1189272.7568
70 | 2655330.5756 | 1189319.3952 | 2655270.0846 | 1189292.3771 | 2655259.3726 | 1189284.5295 | 2655247.6525 | 1189272.7568
71 | 2655330.5756 | 1189319.3952 | 2655329.6086 | 1189320.8649 | 2655327.3015 | 1189325.4017 | 2655320.979 | 1189337.7379
72 | 2655330.5756 | 1189319.3952 | 2655340.2792 | 1189323.9744
73 | 2655320.7939 | 1189338.0991 | 2655320.979 | 1189337.7379
74 | 2655354.1324 | 1189330.5117 | 2655340.2792 | 1189323.9744
75 | 2655317.0881 | 1189345.3297 | 2655320.7939 | 1189338.0991
76 | 2655362.0061 | 1189334.2273 | 2655354.1324 | 1189330.5117
77 | 2655362.0061 | 1189334.2273 | 2655367.8483 | 1189322.6748 | 2655402.1836 | 1189289.7959 | 2655409.8336 | 1189284.0079 | 2655410.7204 | 1189282.6727
78 | 2655362.0061 | 1189334.2273 | 2655376.6806 | 1189341.3896
79 | 2655376.6806 | 1189341.3896 | 2655403.6023 | 1189354.5295
80 | 2655441.8759 | 1189373.21 | 2655403.6023 | 1189354.5295
81 | 2655454.7939 | 1189379.5149 | 2655441.8759 | 1189373.21
82 | 2655454.7939 | 1189379.5149 | 2655368.1015 | 1189597.1207
83 | 2655368.1015 | 1189597.1207 | 2655367.8309 | 1189600.8202 | 2655366.7979 | 1189603.6679
84 | 2655349.3552 | 1189619.4267 | 2655353.7502 | 1189613.4306 | 2655356.6674 | 1189610.5337 | 2655360.4962 | 1189608.0232 | 2655365.8774 | 1189605.0601 | 2655366.7979 | 1189603.6679
85 | 2655345.7461 | 1189640.4782 | 2655344.5146 | 1189635.6911 | 2655344.5681 | 1189631.5559 | 2655346.1372 | 1189625.9895 | 2655349.3552 | 1189619.4267
86 | 2655032.4894 | 1189475.9597 | 2655046.2325 | 1189482.612 | 2655055.4791 | 1189485.5986 | 2655069.2151 | 1189488.8712 | 2655092.1566 | 1189493.7849 | 2655099.5745 | 1189494.3957
87 | 2655032.4894 | 1189475.9597 | 2655044.7825 | 1189505.4942
88 | 2655103.405 | 1189494.7111 | 2655099.5745 | 1189494.3957
89 | 2655044.7825 | 1189505.4942 | 2655050.2179 | 1189518.5529
90 | 2655051.2186 | 1189520.9572 | 2655050.2179 | 1189518.5529
91 | 2655070.1744 | 1189551.2373 | 2655063.0922 | 1189542.634 | 2655056.3908 | 1189531.5885 | 2655051.2186 | 1189520.9572
92 | 2655051.2186 | 1189520.9572 | 2655056.4935 | 1189523.7405 | 2655059.5259 | 1189525.7251 | 2655071.3731 | 1189534.8458
93 | 2655075.5882 | 1189538.0908 | 2655071.3731 | 1189534.8458
94 | 2655070.1744 | 1189551.2373 | 2655092.6328 | 1189561.3829 | 2655096.0513 | 1189563.6712 | 2655099.3018 | 1189566.814 | 2655102.2081 | 1189570.8874 | 2655104.3342 | 1189575.2205 | 2655105.9413 | 1189581.2498 | 2655109.3788 | 1189602.1821 | 2655110.4241 | 1189605.4491 | 2655112.2458 | 1189608.8789 | 2655114.6142 | 1189611.7357 | 2655117.7627 | 1189614.355 | 2655127.4757 | 1189620.4923 | 2655131.2174 | 1189623.295 | 2655133.4884 | 1189625.9618 | 2655135.1278 | 1189629.301 | 2655136.7658 | 1189634.4523 | 2655137.7373 | 1189639.931 | 2655137.7856 | 1189644.623 | 2655137.262 | 1189648.487 | 2655136.3608 | 1189651.1024 | 2655134.7386 | 1189654.1781 | 2655132.7621 | 1189656.7947 | 2655129.0141 | 1189659.6507 | 2655125.3667 | 1189661.5182 | 2655115.4297 | 1189664.8064 | 2655110.736 | 1189666.8422 | 2655106.8914 | 1189669.4193 | 2655104.8923 | 1189671.4276
95 | 2655070.1744 | 1189551.2373 | 2655061.3666 | 1189557.7712 | 2655057.453 | 1189559.5638
96 | 2655055.9747 | 1189736.8892 | 2655060.0141 | 1189732.1903 | 2655070.4717 | 1189722.8701 | 2655076.5317 | 1189716.5556 | 2655078.997 | 1189713.0318 | 2655094.2417 | 1189684.8895 | 2655098.2882 | 1189678.6009 | 2655102.8887 | 1189673.4403 | 2655104.8923 | 1189671.4276
97 | 2655057.453 | 1189559.5638 | 2655056.6794 | 1189559.9182 | 2655051.6157 | 1189561.5392 | 2655045.5392 | 1189562.1726 | 2655043.5951 | 1189561.9665
98 | 2655078.3135 | 1189844.5107 | 2655075.4055 | 1189846.4295 | 2655072.8005 | 1189847.7507 | 2655070.0265 | 1189848.37 | 2655066.6144 | 1189847.8828 | 2655063.8191 | 1189846.6787 | 2655056.4286 | 1189840.952 | 2655054.7032 | 1189838.6682 | 2655052.9815 | 1189835.9841 | 2655051.7783 | 1189831.6484 | 2655051.5808 | 1189828.2447 | 2655052.6108 | 1189824.0407 | 2655059.6191 | 1189809.1411 | 2655060.7313 | 1189805.9607 | 2655061.3152 | 1189802.175 | 2655061.4974 | 1189797.2851 | 2655060.946 | 1189790.9097 | 2655052.7115 | 1189755.8699 | 2655052.3612 | 1189750.8416 | 2655053.1041 | 1189744.6894 | 2655054.351 | 1189740.1316 | 2655055.9747 | 1189736.8892
99 | 2655055.9747 | 1189736.8892 | 2655053.392 | 1189733.2856 | 2655052.346 | 1189730.9302 | 2655051.9903 | 1189728.1476 | 2655052.0983 | 1189725.5249 | 2655053.2689 | 1189720.9664 | 2655060.9385 | 1189702.1708 | 2655061.725 | 1189699.5765
100 | 2655041.7068 | 1189561.7663 | 2655043.5951 | 1189561.9665
101 | 2655041.7068 | 1189561.7663 | 2655038.9943 | 1189561.4788 | 2655032.8502 | 1189560.3328 | 2655017.9682 | 1189554.4906
102 | 2655017.9682 | 1189554.4906 | 2655007.9402 | 1189550.554 | 2654990.6431 | 1189543.5728
103 | 2654953.6676 | 1189543.2962 | 2654953.6676 | 1189543.2962 | 2654956.5042 | 1189538.3639 | 2654962.0913 | 1189535.3802 | 2654969.6063 | 1189535.0823 | 2654990.6431 | 1189543.5728
104 | 2654953.6676 | 1189543.2962 | 2654953.6426 | 1189549.3439 | 2654955.7831 | 1189554.5998 | 2654955.7831 | 1189554.5998
105 | 2654955.7831 | 1189554.5998 | 2654957.9242 | 1189557.3989
106 | 2655078.3135 | 1189844.5107 | 2655082.9053 | 1189842.7631 | 2655085.8403 | 1189842.0563 | 2655088.7773 | 1189841.9499 | 2655141.1766 | 1189845.3006 | 2655146.8096 | 1189846.4309 | 2655151.6033 | 1189848.4317 | 2655155.9255 | 1189851.1175 | 2655177.5771 | 1189870.8836 | 2655180.848 | 1189875.0939 | 2655189.7846 | 1189890.118 | 2655194.0152 | 1189895.2933
107 | 2655078.3135 | 1189844.5107 | 2655092.6181 | 1189828.1775 | 2655109.186 | 1189816.1676 | 2655129.5765 | 1189801.4803 | 2655145.776 | 1189793.058 | 2655147.1021 | 1189792.8347
108 | 2655061.725 | 1189699.5765 | 2655063.7571 | 1189696.7047 | 2655066.4398 | 1189691.0929 | 2655067.9535 | 1189686.5487 | 2655068.3681 | 1189683.762 | 2655068.1699 | 1189680.4361 | 2655066.8035 | 1189677.2551
109 | 2655061.725 | 1189699.5765 | 2655061.8247 | 1189696.1978 | 2655060.9512 | 1189691.665 | 2655059.3767 | 1189687.8928 | 2655055.9714 | 1189683.3479 | 2655050.2536 | 1189677.3252 | 2655046.4569 | 1189673.8662 | 2655043.6367 | 1189672.0392 | 2655040.817 | 1189670.9905 | 2655037.6313 | 1189670.75 | 2655034.9699 | 1189671.5593 | 2655028.5661 | 1189675.3832
110 | 2655157.2465 | 1189792.1631 | 2655345.7461 | 1189640.4782
111 | 2654970.9136 | 1189570.1683 | 2654959.3628 | 1189559.2797 | 2654957.9242 | 1189557.3989
112 | 2655011.3407 | 1189610.7898 | 2655011.0666 | 1189609.5382 | 2655007.9653 | 1189605.0961 | 2654996.9352 | 1189594.6983
113 | 2654989.5967 | 1189622.137 | 2654993.5517 | 1189624.9749 | 2654997.7089 | 1189626.5473 | 2655002.799 | 1189626.1939 | 2655007.7853 | 1189623.8605 | 2655011.4372 | 1189619.8363 | 2655012.2963 | 1189615.1526 | 2655011.3407 | 1189610.7898
114 | 2654996.9352 | 1189594.6983 | 2654979.0757 | 1189577.8626
115 | 2654989.5967 | 1189622.137 | 2654985.5572 | 1189619.2328
116 | 2654977.5879 | 1189645.9068 | 2654982.4739 | 1189642.8611 | 2654985.735 | 1189639.8671 | 2654989.2252 | 1189635.1854 | 2654984.4854 | 1189628.9495 | 2654989.5967 | 1189622.137
117 | 2654970.9136 | 1189570.1683 | 2654979.0757 | 1189577.8626
118 | 2654968.3005 | 1189606.8261 | 2654985.5572 | 1189619.2328
119 | 2654779.3114 | 1189828.2579 | 2654773.4577 | 1189814.3761 | 2654773.4577 | 1189814.3761
120 | 2654636.8168 | 1189765.6728 | 2654639.3377 | 1189766.4798 | 2654650.1185 | 1189774.3048 | 2654664.826 | 1189793.9056 | 2654679.8751 | 1189809.4961 | 2654695.5841 | 1189820.4568 | 2654722.3951 | 1189819.9348 | 2654756.1131 | 1189812.9834 | 2654769.3761 | 1189812.8824 | 2654773.4577 | 1189814.3761
121 | 2654779.3114 | 1189828.2579 | 2654780.5263 | 1189831.1391 | 2654785.2434 | 1189842.41
122 | 2654636.8168 | 1189765.6728 | 2654629.3992 | 1189763.2985 | 2654626.3627 | 1189760.925 | 2654626.9595 | 1189758.2067 | 2654631.3141 | 1189756.035
123 | 2655194.0152 | 1189895.2933 | 2655184.1058 | 1189888.1757 | 2655174.0677 | 1189878.4778 | 2655165.45 | 1189875.1743 | 2655154.9682 | 1189874.722 | 2655147.6366 | 1189876.6889 | 2655142.6627 | 1189881.8349 | 2655140.8304 | 1189884.9369
124 | 2655147.7 | 1189792.7341 | 2655147.1021 | 1189792.8347
125 | 2655157.2465 | 1189792.1631 | 2655150.2214 | 1189792.3096 | 2655147.7 | 1189792.7341

## bus_geodata
| x | y | coords
0 | 2653603.8562 | 1189123.6755
1 | 2653642.9326 | 1189161.9325
2 | 2653591.1327 | 1189120.2701
3 | 2653703.1025 | 1189169.7015
4 | 2654084.5842 | 1189349.7445
5 | 2654187.4275 | 1189377.1691
6 | 2654092.9448 | 1189376.9207
7 | 2653708.2576 | 1189181.7873
8 | 2653953.4898 | 1189056.5979
9 | 2653722.7487 | 1189240.2246
10 | 2653942.5825 | 1189027.2675
11 | 2653912.7893 | 1188988.2318
12 | 2653947.337 | 1189041.6986
13 | 2654753.1082 | 1189246.6769
14 | 2654737.9365 | 1189220.7125
15 | 2654754.6932 | 1189251.0987
16 | 2654719.0972 | 1189175.2642
17 | 2654754.4058 | 1189298.224
18 | 2654935.942 | 1189263.3428
19 | 2654939.7769 | 1189267.0582
20 | 2654725.8292 | 1189142.3903
21 | 2654755.743 | 1189301.4255
22 | 2654615.709 | 1189108.7834
23 | 2654939.2967 | 1189253.5411
24 | 2654959.2093 | 1189268.5925
25 | 2653782.2359 | 1189292.6782
26 | 2653816.5929 | 1189303.4747
27 | 2653837.5756 | 1189312.1408
28 | 2653894.6215 | 1189438.071
29 | 2654039.445 | 1189533.4585
30 | 2654098.5668 | 1189389.1151
31 | 2654066.5956 | 1189527.1524
32 | 2654396.812 | 1189248.826
33 | 2654479.148 | 1189346.5265
34 | 2654227.4938 | 1189370.1146
35 | 2654392.8806 | 1189203.5852
36 | 2654204.7624 | 1189386.518
37 | 2654124.6541 | 1189532.1088
38 | 2654141.5963 | 1189608.4604
39 | 2654215.9996 | 1189406.3976
40 | 2654258.9308 | 1189424.0406
41 | 2654594.5148 | 1189067.6226
42 | 2654454.0575 | 1189130.0015
43 | 2654958.4806 | 1189277.3574
44 | 2655058.5325 | 1189401.5349
45 | 2655054.392 | 1189417.2057
46 | 2655023.8268 | 1189382.8833
47 | 2655030.0278 | 1189447.5545
48 | 2654538.6503 | 1189401.5263
49 | 2654576.6533 | 1189483.942
50 | 2654118.9323 | 1189664.7761
51 | 2654197.1131 | 1189708.1583
52 | 2654589.4551 | 1189495.3836
53 | 2654650.6552 | 1189567.6378
54 | 2654569.3373 | 1189418.2681
55 | 2654436.1699 | 1189588.939
56 | 2654420.1481 | 1189570.3467
57 | 2654476.7576 | 1189623.4964
58 | 2654410.8801 | 1189555.7193
59 | 2654512.473 | 1189649.0616
60 | 2654509.1721 | 1189645.8579
61 | 2655072.8704 | 1189232.6491
62 | 2655127.3965 | 1189125.4907
63 | 2655083.8324 | 1189246.3135
64 | 2655145.2159 | 1189161.6639
65 | 2655208.0104 | 1189227.8903
66 | 2655221.9419 | 1189243.2549
67 | 2655236.3602 | 1189260.2863
68 | 2655241.7805 | 1189266.6889
69 | 2655247.6525 | 1189272.7568
70 | 2655330.5756 | 1189319.3952
71 | 2655320.979 | 1189337.7379
72 | 2655340.2792 | 1189323.9744
73 | 2655320.7939 | 1189338.0991
74 | 2655354.1324 | 1189330.5117
75 | 2655317.0881 | 1189345.3297
76 | 2655362.0061 | 1189334.2273
77 | 2655376.6806 | 1189341.3896
78 | 2655403.6023 | 1189354.5295
79 | 2655441.8759 | 1189373.21
80 | 2655410.7204 | 1189282.6727
81 | 2655454.7939 | 1189379.5149
82 | 2655368.1015 | 1189597.1207
83 | 2655366.7979 | 1189603.6679
84 | 2655349.3552 | 1189619.4267
85 | 2655032.4894 | 1189475.9597
86 | 2655099.5745 | 1189494.3957
87 | 2655044.7825 | 1189505.4942
88 | 2655103.405 | 1189494.7111
89 | 2655050.2179 | 1189518.5529
90 | 2655051.2186 | 1189520.9572
91 | 2655071.3731 | 1189534.8458
92 | 2655075.5882 | 1189538.0908
93 | 2655070.1744 | 1189551.2373
94 | 2655104.8923 | 1189671.4276
95 | 2655057.453 | 1189559.5638
96 | 2655055.9747 | 1189736.8892
97 | 2655043.5951 | 1189561.9665
98 | 2655041.7068 | 1189561.7663
99 | 2655017.9682 | 1189554.4906
100 | 2654990.6431 | 1189543.5728
101 | 2654953.6676 | 1189543.2962
102 | 2654955.7831 | 1189554.5998
103 | 2655078.3135 | 1189844.5107
104 | 2655061.725 | 1189699.5765
105 | 2655345.7461 | 1189640.4782
106 | 2654957.9242 | 1189557.3989
107 | 2655011.3407 | 1189610.7898
108 | 2654996.9352 | 1189594.6983
109 | 2654989.5967 | 1189622.137
110 | 2654979.0757 | 1189577.8626
111 | 2654985.5572 | 1189619.2328
112 | 2654977.5879 | 1189645.9068
113 | 2654970.9136 | 1189570.1683
114 | 2654968.3005 | 1189606.8261
115 | 2654773.4577 | 1189814.3761
116 | 2654779.3114 | 1189828.2579
117 | 2654636.8168 | 1189765.6728
118 | 2654785.2434 | 1189842.41
119 | 2655028.5661 | 1189675.3832
120 | 2655066.8035 | 1189677.2551
121 | 2655194.0152 | 1189895.2932
122 | 2655147.1021 | 1189792.8347
123 | 2655140.8304 | 1189884.9369
124 | 2655147.7 | 1189792.7341
125 | 2654631.3141 | 1189756.035
126 | 2655157.2465 | 1189792.1631
127 | 2655051.2186 | 1189520.9572

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98268 | -0.12405 | 0.00012321 | 3.088e-05
1 | 0.98269 | -0.12395 | 8.2047e-05 | 2.0563e-05
2 | 0.98268 | -0.12406 | 5.2031e-05 | 1.304e-05
3 | 0.98271 | -0.12378 | 5.0866e-05 | 1.2748e-05
4 | 0.98424 | -0.11217 | 0 | 0
5 | 0.9847 | -0.10876 | 0.00031772 | 7.9629e-05
6 | 0.98413 | -0.11303 | 9.2281e-05 | 2.3128e-05
7 | 0.98273 | -0.12367 | 7.2666e-05 | 1.8212e-05
8 | 0.98256 | -0.12494 | 4.551e-05 | 1.1406e-05
9 | 0.9828 | -0.12316 | 8.6716e-05 | 2.1733e-05
10 | 0.98255 | -0.12503 | 5.5e-05 | 1.3784e-05
11 | 0.98253 | -0.12514 | 0.00019049 | 4.7741e-05
12 | 0.98255 | -0.12499 | 9.635e-05 | 2.4148e-05
13 | 0.99393 | -0.04266 | 7.2997e-05 | 1.8295e-05
14 | 0.99361 | -0.044932 | 0.00017206 | 4.3122e-05
15 | 0.99399 | -0.042305 | 9.899e-05 | 2.4809e-05
16 | 0.99308 | -0.048661 | 0 | 0
17 | 0.99397 | -0.042434 | 0.00012152 | 3.0457e-05
18 | 0.99596 | -0.028364 | 0.0020251 | 0.00050755
19 | 0.99603 | -0.027919 | 0.0016475 | 0.00041289
20 | 0.99273 | -0.051175 | 8.7259e-05 | 2.1869e-05
21 | 0.99397 | -0.042439 | 0.00012362 | 3.0981e-05
22 | 0.99151 | -0.059766 | 0.00012054 | 3.0209e-05
23 | 0.99615 | -0.02707 | 0.0029865 | 0.00074849
24 | 0.99626 | -0.026254 | 0 | 0
25 | 0.9829 | -0.12233 | 4.786e-05 | 1.1995e-05
26 | 0.98295 | -0.12197 | 8.9366e-05 | 2.2397e-05
27 | 0.98298 | -0.12172 | 9.9282e-05 | 2.4882e-05
28 | 0.98321 | -0.12002 | 0 | 0
29 | 0.98348 | -0.1179 | 0.00013615 | 3.4124e-05
30 | 0.98408 | -0.11343 | 8.9074e-05 | 2.2324e-05
31 | 0.98354 | -0.11742 | 8.67e-05 | 2.1729e-05
32 | 0.98648 | -0.095451 | 0 | 0
33 | 0.98317 | -0.11883 | 0.00017212 | 4.3137e-05
34 | 0.98539 | -0.1036 | 0.00038362 | 9.6145e-05
35 | 0.98789 | -0.085424 | 0.00019229 | 4.8192e-05
36 | 0.98478 | -0.1081 | 0 | 0
37 | 0.98343 | -0.11826 | 0 | 0
38 | 0.98328 | -0.11937 | 0 | 0
39 | 0.98478 | -0.10814 | 0.00014573 | 3.6524e-05
40 | 0.98509 | -0.1058 | 0 | 0
41 | 0.991 | -0.06337 | 0 | 0
42 | 0.98939 | -0.074791 | 0.00010846 | 2.7184e-05
43 | 0.9963 | -0.025989 | 0 | 0
44 | 0.99861 | -0.0097224 | 0.0012762 | 0.00031984
45 | 0.99886 | -0.0080092 | 0 | 0
46 | 0.99868 | -0.0092743 | 0.002727 | 0.00068345
47 | 0.99948 | -0.003639 | 0.0036445 | 0.0009134
48 | 0.98101 | -0.13416 | 8.5572e-05 | 2.1446e-05
49 | 0.97866 | -0.15089 | 0.00095378 | 0.00023904
50 | 0.98308 | -0.12077 | 0.00020311 | 5.0903e-05
51 | 0.98293 | -0.12182 | 0.001079 | 0.00027042
52 | 0.97824 | -0.15385 | 0 | 0
53 | 0.97597 | -0.17011 | 0.0015017 | 0.00037637
54 | 0.97823 | -0.15392 | 8.4098e-05 | 2.1077e-05
55 | 0.97126 | -0.20401 | 0.0037926 | 0.00095052
56 | 0.9711 | -0.20518 | 0.0011278 | 0.00028264
57 | 0.97194 | -0.1991 | 0 | 0
58 | 0.97101 | -0.2058 | 0.0033803 | 0.00084718
59 | 0.97248 | -0.19522 | 0.00065528 | 0.00016423
60 | 0.97242 | -0.19564 | 0.00046566 | 0.00011671
61 | 0.97045 | -0.20915 | 0.0023066 | 0.0005781
62 | 0.97266 | -0.19318 | 0 | 0
63 | 0.97025 | -0.21056 | 0.0076046 | 0.0019059
64 | 0.97328 | -0.18872 | 0 | 0
65 | 0.97461 | -0.17918 | 0.0012181 | 0.00030529
66 | 0.97495 | -0.17675 | 0.00092906 | 0.00023285
67 | 0.97535 | -0.17392 | 0.0007775 | 0.00019486
68 | 0.9755 | -0.17279 | 0.00077748 | 0.00019486
69 | 0.97567 | -0.17158 | 0.00072932 | 0.00018278
70 | 0.9777 | -0.15711 | 0 | 0
71 | 0.9776 | -0.15777 | 0.0010686 | 0.00026781
72 | 0.97797 | -0.15516 | 0.00060454 | 0.00015151
73 | 0.9776 | -0.15778 | 0.0014432 | 0.00036171
74 | 0.97837 | -0.15228 | 0.0012413 | 0.0003111
75 | 0.9776 | -0.15782 | 0.00052708 | 0.0001321
76 | 0.97862 | -0.15053 | 0 | 0
77 | 0.9791 | -0.14707 | 0.0019649 | 0.00049245
78 | 0.98008 | -0.1401 | 0.0021258 | 0.00053276
79 | 0.9816 | -0.12929 | 0.00086907 | 0.00021781
80 | 0.9785 | -0.15135 | 0.0010936 | 0.00027408
81 | 0.98187 | -0.1274 | 0.0017563 | 0.00044018
82 | 0.98495 | -0.10554 | 0.00025482 | 6.3863e-05
83 | 0.98504 | -0.1049 | 0.00026613 | 6.6697e-05
84 | 0.98536 | -0.10263 | 0.00081537 | 0.00020435
85 | 1 | 0 | -0.12079 | -0.030146
86 | 0.99932 | -0.0047747 | 0.0028579 | 0.00071627
87 | 0.99885 | -0.0080289 | 0.0020823 | 0.00052189
88 | 0.9993 | -0.0049271 | 0.0039671 | 0.00099425
89 | 0.99835 | -0.011486 | 0.00086086 | 0.00021575
90 | 0.99826 | -0.012116 | 0 | 0
91 | 0.99813 | -0.012994 | 0.0023877 | 0.00059841
92 | 0.99812 | -0.013057 | 0.0011831 | 0.00029652
93 | 0.99708 | -0.020365 | 0 | 0
94 | 0.99424 | -0.040193 | 0.0003415 | 8.5587e-05
95 | 0.99633 | -0.025587 | 0.0020492 | 0.00051357
96 | 0.99287 | -0.049751 | 0 | 0
97 | 0.99568 | -0.030167 | 0.0019766 | 0.00049539
98 | 0.9956 | -0.03074 | 0.0027437 | 0.00068764
99 | 0.99462 | -0.0376 | 0.0022813 | 0.00057174
100 | 0.99356 | -0.045024 | 0.0025527 | 0.00063976
101 | 0.9922 | -0.054611 | 0.00232 | 0.00058144
102 | 0.99186 | -0.057001 | 0.0024011 | 0.00060177
103 | 0.99074 | -0.064713 | 0 | 0
104 | 0.9928 | -0.050276 | 0 | 0
105 | 0.98567 | -0.10047 | 0.0017328 | 0.00043429
106 | 0.99177 | -0.057634 | 0.0031472 | 0.00078875
107 | 0.99066 | -0.065529 | 0.0010878 | 0.00027263
108 | 0.99086 | -0.064103 | 0.0030985 | 0.00077655
109 | 0.99039 | -0.067404 | 0 | 0
110 | 0.99119 | -0.061728 | 0.0027719 | 0.00069471
111 | 0.99036 | -0.067614 | 0.0010364 | 0.00025973
112 | 0.99034 | -0.06779 | 0.0011723 | 0.00029382
113 | 0.99139 | -0.060328 | 0.0022562 | 0.00056546
114 | 0.99027 | -0.068288 | 0.0031128 | 0.00078014
115 | 0.97038 | -0.2104 | 0.00092323 | 0.00023138
116 | 0.97035 | -0.21064 | 0.00095646 | 0.00023971
117 | 0.97096 | -0.20621 | 0.00080353 | 0.00020138
118 | 0.97034 | -0.21074 | 0.000578 | 0.00014486
119 | 0.99274 | -0.050671 | 0.0007625 | 0.0001911
120 | 0.99278 | -0.050403 | 0.00052078 | 0.00013052
121 | 0.99067 | -0.065204 | 0 | 0
122 | 0.98937 | -0.074347 | 0.00025465 | 6.382e-05
123 | 0.99064 | -0.065426 | 0.00033734 | 8.4546e-05
124 | 0.98936 | -0.074414 | 0.00018546 | 4.648e-05
125 | 0.97105 | -0.20554 | 0.002145 | 0.00053758
126 | 0.98921 | -0.075463 | 0.0018834 | 0.00047203
127 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00017524 | -4.3753e-05 | 0.00017525 | 4.3036e-05 | 2.4865e-09 | -7.1697e-07 | 0.0002653 | 0.00026505 | 0.0002653 | 0.98268 | -0.12405 | 0.98269 | -0.12395 | 0.09826
1 | 5.2031e-05 | 1.2873e-05 | -5.2031e-05 | -1.304e-05 | 5.0982e-11 | -1.6684e-07 | 7.8729e-05 | 7.8788e-05 | 7.8788e-05 | 0.98268 | -0.12405 | 0.98268 | -0.12406 | 0.029181
2 | -0.00025729 | -6.3599e-05 | 0.0002573 | 6.282e-05 | 5.8271e-09 | -7.7902e-07 | 0.00038928 | 0.00038901 | 0.00038928 | 0.98269 | -0.12395 | 0.98271 | -0.12378 | 0.14418
3 | -0.00069558 | -0.00016813 | 0.00069559 | 0.00016796 | 9.555e-09 | -1.7195e-07 | 0.0010511 | 0.001051 | 0.0010511 | 0.98271 | -0.12378 | 0.98273 | -0.12367 | 0.38928
4 | 0.00038742 | 9.2564e-05 | -0.00038736 | -9.6022e-05 | 5.88e-08 | -3.4578e-06 | 0.00058504 | 0.00058625 | 0.00058625 | 0.98271 | -0.12378 | 0.98256 | -0.12494 | 0.21713
5 | -0.0027812 | -0.00067736 | 0.0027824 | 0.00067641 | 1.2413e-06 | -9.5813e-07 | 0.0041978 | 0.0041973 | 0.0041978 | 0.98424 | -0.11217 | 0.9847 | -0.10876 | 1.5547
6 | 0.0027812 | 0.00067736 | -0.0027809 | -0.0006776 | 3.1265e-07 | -2.4107e-07 | 0.0041978 | 0.0041979 | 0.0041979 | 0.98424 | -0.11217 | 0.98413 | -0.11303 | 1.5548
7 | -0.0031001 | -0.00075603 | 0.0031004 | 0.00075589 | 2.6899e-07 | -1.4722e-07 | 0.0046774 | 0.0046773 | 0.0046774 | 0.9847 | -0.10876 | 0.98478 | -0.1081 | 1.7324
8 | 0.0026886 | 0.00065448 | -0.0026884 | -0.0006546 | 1.3884e-07 | -1.1824e-07 | 0.0040584 | 0.0040584 | 0.0040584 | 0.98413 | -0.11303 | 0.98408 | -0.11343 | 1.5031
9 | -0.00076826 | -0.00018617 | 0.00076831 | 0.00018543 | 5.0847e-08 | -7.4658e-07 | 0.001161 | 0.0011608 | 0.001161 | 0.98273 | -0.12367 | 0.9828 | -0.12316 | 0.43001
10 | 0.00034185 | 8.4616e-05 | -0.00034184 | -8.482e-05 | 2.7067e-09 | -2.0421e-07 | 0.00051733 | 0.0005174 | 0.0005174 | 0.98256 | -0.12494 | 0.98255 | -0.12499 | 0.19163
11 | -0.00085502 | -0.00020716 | 0.00085511 | 0.00020608 | 9.112e-08 | -1.0738e-06 | 0.0012921 | 0.0012917 | 0.0012921 | 0.9828 | -0.12316 | 0.9829 | -0.12233 | 0.47854
12 | 0.00019049 | 4.7081e-05 | -0.00019049 | -4.7741e-05 | 2.7098e-09 | -6.6034e-07 | 0.00028826 | 0.00028849 | 0.00028849 | 0.98255 | -0.12503 | 0.98253 | -0.12514 | 0.10685
13 | -0.00024549 | -6.0866e-05 | 0.0002455 | 6.0673e-05 | 1.3158e-09 | -1.9298e-07 | 0.00037155 | 0.00037148 | 0.00037155 | 0.98255 | -0.12503 | 0.98255 | -0.12499 | 0.13761
14 | 0.022353 | 0.005598 | -0.022346 | -0.0055965 | 7.02e-06 | 1.5285e-06 | 0.033464 | 0.033464 | 0.033464 | 0.99393 | -0.04266 | 0.99361 | -0.044932 | 4.1314
15 | -0.022426 | -0.0056163 | 0.022428 | 0.0056166 | 1.1013e-06 | 2.4091e-07 | 0.033573 | 0.033573 | 0.033573 | 0.99393 | -0.04266 | 0.99399 | -0.042305 | 4.1448
16 | 0.022174 | 0.0055534 | -0.022163 | -0.0055509 | 1.1429e-05 | 2.4605e-06 | 0.033207 | 0.033207 | 0.033207 | 0.99361 | -0.044932 | 0.99308 | -0.048661 | 4.0997
17 | 0.00024515 | 6.0725e-05 | -0.00024514 | -6.1393e-05 | 4.3419e-09 | -6.6848e-07 | 0.00036674 | 0.00036697 | 0.00036697 | 0.99399 | -0.042305 | 0.99397 | -0.042434 | 0.13592
18 | -0.022772 | -0.0057021 | 0.022816 | 0.0057119 | 4.3903e-05 | 9.8077e-06 | 0.034088 | 0.034085 | 0.034088 | 0.99399 | -0.042305 | 0.99596 | -0.028364 | 4.2084
19 | 0.022163 | 0.0055509 | -0.022155 | -0.0055493 | 7.7018e-06 | 1.6594e-06 | 0.033207 | 0.033208 | 0.033208 | 0.99308 | -0.048661 | 0.99273 | -0.051175 | 4.0997
20 | 0.00012362 | 3.0937e-05 | -0.00012362 | -3.0981e-05 | 7.4168e-11 | -4.4943e-08 | 0.00018505 | 0.00018506 | 0.00018506 | 0.99397 | -0.042434 | 0.99397 | -0.042439 | 0.068541
21 | -0.024841 | -0.0062195 | 0.024842 | 0.0062198 | 1.5296e-06 | 3.7983e-07 | 0.037111 | 0.037111 | 0.037111 | 0.99596 | -0.028364 | 0.99603 | -0.027919 | 4.5816
22 | -0.02649 | -0.0066327 | 0.026497 | 0.0066346 | 7.0634e-06 | 1.8697e-06 | 0.039572 | 0.039572 | 0.039572 | 0.99603 | -0.027919 | 0.9963 | -0.025989 | 4.8855
23 | 0.022068 | 0.0055274 | -0.022042 | -0.0055218 | 2.6202e-05 | 5.6175e-06 | 0.033077 | 0.033078 | 0.033078 | 0.99273 | -0.051175 | 0.99151 | -0.059766 | 4.0838
24 | 0.021921 | 0.0054916 | -0.02191 | -0.0054892 | 1.0926e-05 | 2.3253e-06 | 0.032898 | 0.032898 | 0.032898 | 0.99151 | -0.059766 | 0.991 | -0.06337 | 4.0615
25 | -0.0029865 | -0.00074849 | 0.0029868 | 0.00074826 | 3.3758e-07 | -2.2409e-07 | 0.0044612 | 0.004461 | 0.0044612 | 0.99615 | -0.02707 | 0.99626 | -0.026254 | 1.6523
26 | -0.0029868 | -0.00074826 | 0.0029869 | 0.00074819 | 1.0924e-07 | -7.2538e-08 | 0.004461 | 0.004461 | 0.004461 | 0.99626 | -0.026254 | 0.9963 | -0.025989 | 1.6522
27 | -0.00090297 | -0.00021808 | 0.00090302 | 0.00021764 | 4.184e-08 | -4.4068e-07 | 0.0013641 | 0.001364 | 0.0013641 | 0.9829 | -0.12233 | 0.98295 | -0.12197 | 0.50523
28 | -0.00099238 | -0.00024004 | 0.00099241 | 0.00023976 | 3.2324e-08 | -2.7972e-07 | 0.0014992 | 0.0014991 | 0.0014992 | 0.98295 | -0.12197 | 0.98298 | -0.12172 | 0.55528
29 | -0.0010917 | -0.00026464 | 0.0010919 | 0.00026294 | 2.4039e-07 | -1.7036e-06 | 0.0016494 | 0.0016488 | 0.0016494 | 0.98298 | -0.12172 | 0.98321 | -0.12002 | 0.6109
30 | -0.0010919 | -0.00026294 | 0.0010922 | 0.00026085 | 2.9405e-07 | -2.0868e-06 | 0.0016488 | 0.0016481 | 0.0016488 | 0.98321 | -0.12002 | 0.98348 | -0.1179 | 0.61067
31 | -0.0012284 | -0.00029497 | 0.0012285 | 0.00029456 | 7.5361e-08 | -4.169e-07 | 0.0018541 | 0.0018539 | 0.0018541 | 0.98348 | -0.1179 | 0.98354 | -0.11742 | 0.68669
32 | 0.0025994 | 0.00063227 | -0.002598 | -0.00063355 | 1.3614e-06 | -1.2756e-06 | 0.0039237 | 0.0039244 | 0.0039244 | 0.98408 | -0.11343 | 0.98354 | -0.11742 | 1.4535
33 | 0.0012828 | 0.00031726 | -0.0012827 | -0.00031799 | 1.4545e-07 | -7.3039e-07 | 0.0019393 | 0.0019396 | 0.0019396 | 0.98354 | -0.11742 | 0.98343 | -0.11826 | 0.71837
34 | 0.017878 | 0.0044995 | -0.017819 | -0.0044788 | 5.8183e-05 | 2.0747e-05 | 0.026974 | 0.026974 | 0.026974 | 0.98648 | -0.095451 | 0.98317 | -0.11883 | 9.9904
35 | 0.0036356 | 0.00088621 | -0.0036317 | -0.00088737 | 3.8967e-06 | -1.1574e-06 | 0.0054752 | 0.0054761 | 0.0054761 | 0.98648 | -0.095451 | 0.98539 | -0.1036 | 2.0282
36 | -0.021513 | -0.0053857 | 0.021543 | 0.0053966 | 2.9836e-05 | 1.0895e-05 | 0.032449 | 0.032448 | 0.032449 | 0.98648 | -0.095451 | 0.98789 | -0.085424 | 12.018
37 | 0.017647 | 0.0044356 | -0.01761 | -0.0044223 | 3.7584e-05 | 1.3387e-05 | 0.026714 | 0.026714 | 0.026714 | 0.98317 | -0.11883 | 0.98101 | -0.13416 | 9.8941
38 | 0.0032481 | 0.00079123 | -0.0032471 | -0.00079166 | 9.3481e-07 | -4.3603e-07 | 0.0048968 | 0.0048971 | 0.0048971 | 0.98539 | -0.1036 | 0.98509 | -0.1058 | 1.8137
39 | -0.021735 | -0.0054448 | 0.021767 | 0.0054547 | 3.1999e-05 | 9.853e-06 | 0.032738 | 0.032737 | 0.032738 | 0.98789 | -0.085424 | 0.98939 | -0.074791 | 6.0626
40 | 0.00014573 | 3.6233e-05 | -0.00014573 | -3.6524e-05 | 6.9127e-10 | -2.9054e-07 | 0.0002201 | 0.0002202 | 0.0002202 | 0.98478 | -0.1081 | 0.98478 | -0.10814 | 0.081557
41 | -0.0032461 | -0.00079212 | 0.0032471 | 0.00079166 | 9.8466e-07 | -4.5867e-07 | 0.0048974 | 0.0048971 | 0.0048974 | 0.98478 | -0.1081 | 0.98509 | -0.1058 | 1.8138
42 | 0.0012827 | 0.00031799 | -0.0012825 | -0.00031896 | 1.923e-07 | -9.6504e-07 | 0.0019396 | 0.00194 | 0.00194 | 0.98343 | -0.11826 | 0.98328 | -0.11937 | 0.7185
43 | 0.0012825 | 0.00031896 | -0.0012823 | -0.00032019 | 2.4577e-07 | -1.2323e-06 | 0.00194 | 0.0019404 | 0.0019404 | 0.98328 | -0.11937 | 0.98308 | -0.12077 | 0.71868
44 | 0.02191 | 0.0054892 | -0.021876 | -0.0054819 | 3.46e-05 | 7.3768e-06 | 0.032898 | 0.0329 | 0.0329 | 0.991 | -0.06337 | 0.98939 | -0.074791 | 4.0618
45 | -0.029484 | -0.0073828 | 0.02955 | 0.0074019 | 6.6376e-05 | 1.9084e-05 | 0.044033 | 0.044031 | 0.044033 | 0.9963 | -0.025989 | 0.99861 | -0.0097224 | 5.4362
46 | -0.030826 | -0.0077217 | 0.030834 | 0.0077239 | 7.3046e-06 | 2.156e-06 | 0.045932 | 0.045932 | 0.045932 | 0.99861 | -0.0097224 | 0.99886 | -0.0080092 | 5.6707
47 | 0.0027275 | 0.00068303 | -0.002727 | -0.00068345 | 4.7725e-07 | -4.2275e-07 | 0.004063 | 0.0040632 | 0.0040632 | 0.99886 | -0.0080092 | 0.99868 | -0.0092743 | 1.5049
48 | -0.033561 | -0.0084069 | 0.033581 | 0.0084132 | 2.0293e-05 | 6.2713e-06 | 0.049995 | 0.049995 | 0.049995 | 0.99886 | -0.0080092 | 0.99948 | -0.003639 | 6.1722
49 | -0.037226 | -0.0093266 | 0.037245 | 0.0093326 | 1.8749e-05 | 6.0565e-06 | 0.05542 | 0.05542 | 0.05542 | 0.99948 | -0.003639 | 1 | 0 | 6.842
50 | 0.017524 | 0.0044008 | -0.017483 | -0.0043863 | 4.0668e-05 | 1.448e-05 | 0.026584 | 0.026585 | 0.026585 | 0.98101 | -0.13416 | 0.97866 | -0.15089 | 9.8462
51 | 0.01653 | 0.0041473 | -0.016523 | -0.0041449 | 6.7871e-06 | 2.3942e-06 | 0.025134 | 0.025135 | 0.025135 | 0.97866 | -0.15089 | 0.97824 | -0.15385 | 9.3091
52 | 0.0010791 | 0.00026929 | -0.001079 | -0.00027042 | 1.568e-07 | -1.134e-06 | 0.001633 | 0.0016334 | 0.0016334 | 0.98308 | -0.12077 | 0.98293 | -0.12182 | 0.60497
53 | 0.016439 | 0.0041248 | -0.016402 | -0.0041118 | 3.7025e-05 | 1.3052e-05 | 0.025007 | 0.025007 | 0.025007 | 0.97824 | -0.15385 | 0.97597 | -0.17011 | 9.262
54 | 8.4099e-05 | 2.0058e-05 | -8.4098e-05 | -2.1077e-05 | 8.2682e-10 | -1.0191e-06 | 0.00012757 | 0.00012792 | 0.00012792 | 0.97824 | -0.15385 | 0.97823 | -0.15392 | 0.047379
55 | 0.0149 | 0.0037354 | -0.014848 | -0.0037176 | 5.1654e-05 | 1.787e-05 | 0.022718 | 0.022719 | 0.022719 | 0.97597 | -0.17011 | 0.97248 | -0.19522 | 8.4143
56 | 0.0045091 | 0.0011297 | -0.0045083 | -0.0011297 | 7.3111e-07 | -2.2611e-08 | 0.006908 | 0.0069081 | 0.0069081 | 0.97126 | -0.20401 | 0.9711 | -0.20518 | 2.5585
57 | -0.0083017 | -0.0020802 | 0.0083073 | 0.0020817 | 5.6456e-06 | 1.4787e-06 | 0.012718 | 0.012718 | 0.012718 | 0.97126 | -0.20401 | 0.97194 | -0.1991 | 4.7105
58 | 0.0033806 | 0.00084708 | -0.0033803 | -0.00084718 | 2.9013e-07 | -1.0277e-07 | 0.00518 | 0.0051801 | 0.0051801 | 0.9711 | -0.20518 | 0.97101 | -0.2058 | 1.9186
59 | -0.0083073 | -0.0020817 | 0.0083113 | 0.0020827 | 3.9749e-06 | 1.0405e-06 | 0.012718 | 0.012718 | 0.012718 | 0.97194 | -0.1991 | 0.97242 | -0.19564 | 4.7104
60 | 0.0054156 | 0.0013537 | -0.0054079 | -0.001353 | 7.7032e-06 | 7.3507e-07 | 0.0082853 | 0.0082861 | 0.0082861 | 0.97248 | -0.19522 | 0.97105 | -0.20554 | 3.0689
61 | 0.0087775 | 0.0021996 | -0.008777 | -0.0021994 | 5.1927e-07 | 1.4248e-07 | 0.013431 | 0.013431 | 0.013431 | 0.97248 | -0.19522 | 0.97242 | -0.19564 | 4.9743
62 | -0.0099127 | -0.0024843 | 0.0099346 | 0.0024909 | 2.1953e-05 | 6.5575e-06 | 0.015199 | 0.015199 | 0.015199 | 0.97045 | -0.20915 | 0.97266 | -0.19318 | 5.6294
63 | 0.0076061 | 0.0019062 | -0.0076046 | -0.0019059 | 1.4868e-06 | 3.5546e-07 | 0.011663 | 0.011663 | 0.011663 | 0.97045 | -0.20915 | 0.97025 | -0.21056 | 4.3195
64 | -0.0099346 | -0.0024909 | 0.0099408 | 0.0024927 | 6.1356e-06 | 1.8312e-06 | 0.015199 | 0.015199 | 0.015199 | 0.97266 | -0.19318 | 0.97328 | -0.18872 | 5.6292
65 | -0.0099408 | -0.0024927 | 0.0099539 | 0.0024967 | 1.3155e-05 | 3.9237e-06 | 0.015199 | 0.015198 | 0.015199 | 0.97328 | -0.18872 | 0.97461 | -0.17918 | 5.6291
66 | -0.011172 | -0.0028019 | 0.011176 | 0.0028031 | 3.7672e-06 | 1.1903e-06 | 0.017058 | 0.017058 | 0.017058 | 0.97461 | -0.17918 | 0.97495 | -0.17675 | 6.3178
67 | -0.012105 | -0.003036 | 0.01211 | 0.0030375 | 4.7532e-06 | 1.5498e-06 | 0.018476 | 0.018476 | 0.018476 | 0.97495 | -0.17675 | 0.97535 | -0.17392 | 6.8429
68 | -0.012887 | -0.0032324 | 0.012889 | 0.0032331 | 2.0237e-06 | 6.7362e-07 | 0.019662 | 0.019662 | 0.019662 | 0.97535 | -0.17392 | 0.9755 | -0.17279 | 7.2822
69 | -0.013667 | -0.0034279 | 0.013669 | 0.0034287 | 2.2911e-06 | 7.7572e-07 | 0.020848 | 0.020848 | 0.020848 | 0.9755 | -0.17279 | 0.97567 | -0.17158 | 7.7214
70 | -0.014398 | -0.0036115 | 0.014427 | 0.0036214 | 2.8931e-05 | 9.9239e-06 | 0.02196 | 0.02196 | 0.02196 | 0.97567 | -0.17158 | 0.9777 | -0.15711 | 8.1334
71 | 0.0030392 | 0.00076136 | -0.0030389 | -0.00076151 | 2.765e-07 | -1.5336e-07 | 0.0046254 | 0.0046255 | 0.0046255 | 0.9777 | -0.15711 | 0.9776 | -0.15777 | 1.7131
72 | -0.017466 | -0.0043828 | 0.017471 | 0.0043844 | 4.7321e-06 | 1.6854e-06 | 0.026585 | 0.026585 | 0.026585 | 0.9777 | -0.15711 | 0.97797 | -0.15516 | 9.8463
73 | 0.0019703 | 0.0004937 | -0.0019703 | -0.00049371 | 2.2775e-09 | -4.2122e-09 | 0.002999 | 0.002999 | 0.002999 | 0.9776 | -0.15777 | 0.9776 | -0.15778 | 1.1107
74 | -0.018076 | -0.004536 | 0.018083 | 0.0045385 | 7.2312e-06 | 2.5889e-06 | 0.027505 | 0.027505 | 0.027505 | 0.97797 | -0.15516 | 0.97837 | -0.15228 | 10.187
75 | 0.00052708 | 0.000132 | -0.00052708 | -0.0001321 | 3.2631e-09 | -1.0062e-07 | 0.00080224 | 0.00080228 | 0.00080228 | 0.9776 | -0.15778 | 0.9776 | -0.15782 | 0.29714
76 | -0.019324 | -0.0048496 | 0.019329 | 0.0048513 | 4.6935e-06 | 1.6958e-06 | 0.029393 | 0.029393 | 0.029393 | 0.97837 | -0.15228 | 0.97862 | -0.15053 | 10.8862
77 | 0.0010937 | 0.00027323 | -0.0010936 | -0.00027408 | 1.2368e-07 | -8.5293e-07 | 0.0016627 | 0.001663 | 0.001663 | 0.97862 | -0.15053 | 0.9785 | -0.15135 | 0.61594
78 | -0.020423 | -0.0051246 | 0.020432 | 0.0051281 | 9.827e-06 | 3.5743e-06 | 0.031055 | 0.031055 | 0.031055 | 0.97862 | -0.15053 | 0.9791 | -0.14707 | 11.502
79 | -0.022397 | -0.0056206 | 0.022419 | 0.0056286 | 2.1662e-05 | 7.9545e-06 | 0.034042 | 0.034041 | 0.034042 | 0.9791 | -0.14707 | 0.98008 | -0.1401 | 12.608
80 | -0.024545 | -0.0061613 | 0.024582 | 0.006175 | 3.6912e-05 | 1.366e-05 | 0.037269 | 0.037269 | 0.037269 | 0.98008 | -0.1401 | 0.9816 | -0.12929 | 13.8033
81 | -0.025451 | -0.0063928 | 0.025457 | 0.006395 | 6.6774e-06 | 2.2047e-06 | 0.038586 | 0.038586 | 0.038586 | 0.9816 | -0.12929 | 0.98187 | -0.1274 | 7.1456
82 | -0.027214 | -0.0068352 | 0.027297 | 0.0068581 | 8.2887e-05 | 2.2964e-05 | 0.041248 | 0.041244 | 0.041248 | 0.98187 | -0.1274 | 0.98495 | -0.10554 | 5.0923
83 | -0.027551 | -0.006922 | 0.027554 | 0.0069227 | 2.4291e-06 | 6.7693e-07 | 0.041629 | 0.041629 | 0.041629 | 0.98495 | -0.10554 | 0.98504 | -0.1049 | 5.1394
84 | -0.02782 | -0.0069894 | 0.027829 | 0.0069918 | 8.7955e-06 | 2.4685e-06 | 0.042031 | 0.042031 | 0.042031 | 0.98504 | -0.1049 | 0.98536 | -0.10263 | 5.1891
85 | -0.028644 | -0.0071962 | 0.028653 | 0.0071987 | 8.6312e-06 | 2.4722e-06 | 0.043262 | 0.043262 | 0.043262 | 0.98536 | -0.10263 | 0.98567 | -0.10047 | 5.341
86 | 0.0068296 | 0.0017113 | -0.0068251 | -0.0017105 | 4.5119e-06 | 8.1749e-07 | 0.010162 | 0.010163 | 0.010163 | 1 | 0 | 0.99932 | -0.0047747 | 3.764
87 | 0.075918 | 0.019102 | -0.075833 | -0.01907 | 8.4957e-05 | 3.1418e-05 | 0.11299 | 0.11299 | 0.11299 | 1 | 0 | 0.99885 | -0.0080289 | 13.9499
88 | 0.0039672 | 0.00099423 | -0.0039671 | -0.00099425 | 8.3691e-08 | -1.8165e-08 | 0.0059072 | 0.0059072 | 0.0059072 | 0.99932 | -0.0047747 | 0.9993 | -0.0049271 | 2.1879
89 | 0.073751 | 0.018549 | -0.073716 | -0.018535 | 3.553e-05 | 1.311e-05 | 0.10989 | 0.10989 | 0.10989 | 0.99885 | -0.0080289 | 0.99835 | -0.011486 | 13.567
90 | 0.072855 | 0.01832 | -0.072848 | -0.018317 | 6.3896e-06 | 2.3554e-06 | 0.10861 | 0.10861 | 0.10861 | 0.99835 | -0.011486 | 0.99826 | -0.012116 | 13.4086
91 | 0.069277 | 0.017423 | -0.069197 | -0.017393 | 7.9574e-05 | 2.9201e-05 | 0.10329 | 0.10329 | 0.10329 | 0.99826 | -0.012116 | 0.99708 | -0.020365 | 12.7515
92 | 0.0035713 | 0.00089471 | -0.0035708 | -0.00089487 | 4.3393e-07 | -1.5389e-07 | 0.0053232 | 0.0053234 | 0.0053234 | 0.99826 | -0.012116 | 0.99813 | -0.012994 | 1.9716
93 | 0.0011831 | 0.00029645 | -0.0011831 | -0.00029652 | 1.0326e-08 | -6.5555e-08 | 0.0017638 | 0.0017638 | 0.0017638 | 0.99813 | -0.012994 | 0.99812 | -0.013057 | 0.65326
94 | 0.035038 | 0.0088161 | -0.034942 | -0.0087855 | 9.674e-05 | 3.0574e-05 | 0.052303 | 0.052305 | 0.052305 | 0.99708 | -0.020365 | 0.99424 | -0.040193 | 6.4574
95 | 0.034159 | 0.0085773 | -0.034134 | -0.008568 | 2.477e-05 | 9.3279e-06 | 0.050984 | 0.050984 | 0.050984 | 0.99708 | -0.020365 | 0.99633 | -0.025587 | 18.8829
96 | 0.0346 | 0.0087 | -0.034554 | -0.0086855 | 4.6032e-05 | 1.45e-05 | 0.051794 | 0.051795 | 0.051795 | 0.99424 | -0.040193 | 0.99287 | -0.049751 | 6.3945
97 | 0.032085 | 0.0080544 | -0.032065 | -0.0080467 | 2.0396e-05 | 7.6595e-06 | 0.047923 | 0.047924 | 0.047924 | 0.99633 | -0.025587 | 0.99568 | -0.030167 | 17.7495
98 | 0.033271 | 0.0083653 | -0.033202 | -0.0083438 | 6.9253e-05 | 2.1454e-05 | 0.049872 | 0.049874 | 0.049874 | 0.99287 | -0.049751 | 0.99074 | -0.064713 | 6.1573
99 | 0.0012834 | 0.00032018 | -0.0012833 | -0.00032067 | 9.2655e-08 | -4.8361e-07 | 0.0019229 | 0.0019231 | 0.0019231 | 0.99287 | -0.049751 | 0.9928 | -0.050276 | 0.71227
100 | 0.030088 | 0.0075513 | -0.030086 | -0.0075504 | 2.3962e-06 | 8.9692e-07 | 0.04497 | 0.04497 | 0.04497 | 0.99568 | -0.030167 | 0.9956 | -0.03074 | 16.6554
101 | 0.027342 | 0.0068628 | -0.027316 | -0.0068531 | 2.602e-05 | 9.6834e-06 | 0.040869 | 0.040869 | 0.040869 | 0.9956 | -0.03074 | 0.99462 | -0.0376 | 15.1366
102 | 0.025035 | 0.0062814 | -0.025009 | -0.0062719 | 2.5761e-05 | 9.5264e-06 | 0.037456 | 0.037456 | 0.037456 | 0.99462 | -0.0376 | 0.99356 | -0.045024 | 13.8726
103 | 0.022456 | 0.0056321 | -0.022426 | -0.0056212 | 2.9809e-05 | 1.0919e-05 | 0.033633 | 0.033633 | 0.033633 | 0.99356 | -0.045024 | 0.9922 | -0.054611 | 12.4568
104 | 0.020106 | 0.0050397 | -0.0201 | -0.0050373 | 6.6513e-06 | 2.4068e-06 | 0.030154 | 0.030154 | 0.030154 | 0.9922 | -0.054611 | 0.99186 | -0.057001 | 11.1682
105 | 0.017699 | 0.0044356 | -0.017697 | -0.004435 | 1.5503e-06 | 5.508e-07 | 0.026552 | 0.026552 | 0.026552 | 0.99186 | -0.057001 | 0.99177 | -0.057634 | 9.834
106 | 0.00033738 | 8.1956e-05 | -0.00033735 | -8.3723e-05 | 2.2047e-08 | -1.7676e-06 | 0.00050581 | 0.00050642 | 0.00050642 | 0.99074 | -0.064713 | 0.99067 | -0.065204 | 0.18756
107 | 0.032864 | 0.0082619 | -0.03282 | -0.0082483 | 4.4058e-05 | 1.3593e-05 | 0.049368 | 0.04937 | 0.04937 | 0.99074 | -0.064713 | 0.98937 | -0.074347 | 6.095
108 | 0.00052079 | 0.00013021 | -0.00052078 | -0.00013052 | 9.1743e-09 | -3.0854e-07 | 0.00078046 | 0.00078057 | 0.00078057 | 0.9928 | -0.050276 | 0.99278 | -0.050403 | 0.2891
109 | 0.00076254 | 0.00019046 | -0.0007625 | -0.0001911 | 4.1567e-08 | -6.4356e-07 | 0.0011427 | 0.0011429 | 0.0011429 | 0.9928 | -0.050276 | 0.99274 | -0.050671 | 0.4233
110 | -0.030386 | -0.007633 | 0.030492 | 0.0076644 | 0.00010592 | 3.1453e-05 | 0.045878 | 0.045875 | 0.045878 | 0.98567 | -0.10047 | 0.98921 | -0.075463 | 5.664
111 | 0.01455 | 0.0036463 | -0.014545 | -0.0036444 | 5.4246e-06 | 1.8511e-06 | 0.02183 | 0.02183 | 0.02183 | 0.99177 | -0.057634 | 0.99139 | -0.060328 | 8.0852
112 | -0.0064112 | -0.0016058 | 0.0064124 | 0.001606 | 1.2647e-06 | 2.0495e-07 | 0.0096295 | 0.0096294 | 0.0096295 | 0.99066 | -0.065529 | 0.99086 | -0.064103 | 3.5665
113 | 0.0053233 | 0.0013332 | -0.005322 | -0.0013331 | 1.3796e-06 | 8.5471e-08 | 0.0079956 | 0.0079957 | 0.0079957 | 0.99066 | -0.065529 | 0.99039 | -0.067404 | 2.9614
114 | -0.0095109 | -0.0023826 | 0.009514 | 0.0023835 | 3.1242e-06 | 8.8536e-07 | 0.014283 | 0.014282 | 0.014283 | 0.99086 | -0.064103 | 0.99119 | -0.061728 | 5.2898
115 | 0.0041495 | 0.0010397 | -0.0041494 | -0.0010397 | 1.2067e-07 | -1.7611e-08 | 0.0062344 | 0.0062344 | 0.0062344 | 0.99039 | -0.067404 | 0.99036 | -0.067614 | 2.309
116 | 0.0011724 | 0.00029343 | -0.0011723 | -0.00029382 | 6.2601e-08 | -3.92e-07 | 0.0017613 | 0.0017615 | 0.0017615 | 0.99039 | -0.067404 | 0.99034 | -0.06779 | 0.6524
117 | -0.012286 | -0.0030782 | 0.012288 | 0.003079 | 2.381e-06 | 7.7116e-07 | 0.018444 | 0.018444 | 0.018444 | 0.99119 | -0.061728 | 0.99139 | -0.060328 | 6.831
118 | 0.0031131 | 0.00077998 | -0.0031128 | -0.00078014 | 2.9015e-07 | -1.6186e-07 | 0.0046773 | 0.0046774 | 0.0046774 | 0.99036 | -0.067614 | 0.99027 | -0.068288 | 1.7324
119 | 0.0015345 | 0.00038422 | -0.0015345 | -0.00038438 | 5.2048e-08 | -1.6609e-07 | 0.0023529 | 0.002353 | 0.002353 | 0.97038 | -0.2104 | 0.97035 | -0.21064 | 0.87148
120 | -0.0024577 | -0.0006156 | 0.0024592 | 0.00061417 | 1.4191e-06 | -1.4338e-06 | 0.0037687 | 0.0037679 | 0.0037687 | 0.97038 | -0.2104 | 0.97096 | -0.20621 | 1.3958
121 | 0.00057801 | 0.00014467 | -0.000578 | -0.00014486 | 7.5222e-09 | -1.8666e-07 | 0.0008863 | 0.00088637 | 0.00088637 | 0.97035 | -0.21064 | 0.97034 | -0.21074 | 0.32828
122 | -0.0032627 | -0.00081555 | 0.003263 | 0.00081543 | 3.0087e-07 | -1.2291e-07 | 0.0049994 | 0.0049993 | 0.0049994 | 0.97096 | -0.20621 | 0.97105 | -0.20554 | 1.8516
123 | 0.00033735 | 8.3723e-05 | -0.00033734 | -8.4546e-05 | 1.0285e-08 | -8.2302e-07 | 0.00050642 | 0.00050671 | 0.00050671 | 0.99067 | -0.065204 | 0.99064 | -0.065426 | 0.18767
124 | 0.032565 | 0.0081845 | -0.032565 | -0.0081844 | 3.0261e-07 | 9.3032e-08 | 0.048987 | 0.048987 | 0.048987 | 0.98937 | -0.074347 | 0.98936 | -0.074414 | 6.0477
125 | 0.03238 | 0.0081379 | -0.032375 | -0.0081364 | 4.7292e-06 | 1.4498e-06 | 0.048708 | 0.048708 | 0.048708 | 0.98936 | -0.074414 | 0.98921 | -0.075463 | 6.0133

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.12079 | 0.030146

## res_load
| p_mw | q_mvar
0 | 0.00012321 | 3.088e-05
1 | 8.2047e-05 | 2.0563e-05
2 | 5.2031e-05 | 1.304e-05
3 | 5.0866e-05 | 1.2748e-05
4 | 0.00031772 | 7.9629e-05
5 | 9.2281e-05 | 2.3128e-05
6 | 7.2666e-05 | 1.8212e-05
7 | 4.551e-05 | 1.1406e-05
8 | 8.6716e-05 | 2.1733e-05
9 | 5.5e-05 | 1.3784e-05
10 | 0.00019049 | 4.7741e-05
11 | 9.635e-05 | 2.4148e-05
12 | 7.2997e-05 | 1.8295e-05
13 | 0.00017206 | 4.3122e-05
14 | 9.899e-05 | 2.4809e-05
15 | 0.00012152 | 3.0457e-05
16 | 0.0020251 | 0.00050755
17 | 0.0016475 | 0.00041289
18 | 8.7259e-05 | 2.1869e-05
19 | 0.00012362 | 3.0981e-05
20 | 0.00012054 | 3.0209e-05
21 | 0.0029865 | 0.00074849
22 | 4.786e-05 | 1.1995e-05
23 | 8.9366e-05 | 2.2397e-05
24 | 9.9282e-05 | 2.4882e-05
25 | 0.00013615 | 3.4124e-05
26 | 8.9074e-05 | 2.2324e-05
27 | 8.67e-05 | 2.1729e-05
28 | 0.00017212 | 4.3137e-05
29 | 0.00038362 | 9.6145e-05
30 | 0.00019229 | 4.8192e-05
31 | 0.00014573 | 3.6524e-05
32 | 0.00010846 | 2.7184e-05
33 | 0.0012762 | 0.00031984
34 | 0.002727 | 0.00068345
35 | 0.0036445 | 0.0009134
36 | 8.5572e-05 | 2.1446e-05
37 | 0.00095378 | 0.00023904
38 | 0.00020311 | 5.0903e-05
39 | 0.001079 | 0.00027042
40 | 0.0015017 | 0.00037637
41 | 8.4098e-05 | 2.1077e-05
42 | 0.0037926 | 0.00095052
43 | 0.0011278 | 0.00028264
44 | 0.0033803 | 0.00084718
45 | 0.00065528 | 0.00016423
46 | 0.00046566 | 0.00011671
47 | 0.0023066 | 0.0005781
48 | 0.0076046 | 0.0019059
49 | 0.0012181 | 0.00030529
50 | 0.00092906 | 0.00023285
51 | 0.0007775 | 0.00019486
52 | 0.00077748 | 0.00019486
53 | 0.00072932 | 0.00018278
54 | 0.0010686 | 0.00026781
55 | 0.00060454 | 0.00015151
56 | 0.0014432 | 0.00036171
57 | 0.0012413 | 0.0003111
58 | 0.00052708 | 0.0001321
59 | 0.0019649 | 0.00049245
60 | 0.0021258 | 0.00053276
61 | 0.00086907 | 0.00021781
62 | 0.0010936 | 0.00027408
63 | 0.0017563 | 0.00044018
64 | 0.00025482 | 6.3863e-05
65 | 0.00026613 | 6.6697e-05
66 | 0.00081537 | 0.00020435
67 | 0.0028579 | 0.00071627
68 | 0.0020823 | 0.00052189
69 | 0.0039671 | 0.00099425
70 | 0.00086086 | 0.00021575
71 | 0.0023877 | 0.00059841
72 | 0.0011831 | 0.00029652
73 | 0.0003415 | 8.5587e-05
74 | 0.0020492 | 0.00051357
75 | 0.0019766 | 0.00049539
76 | 0.0027437 | 0.00068764
77 | 0.0022813 | 0.00057174
78 | 0.0025527 | 0.00063976
79 | 0.00232 | 0.00058144
80 | 0.0024011 | 0.00060177
81 | 0.0017328 | 0.00043429
82 | 0.0031472 | 0.00078875
83 | 0.0010878 | 0.00027263
84 | 0.0030985 | 0.00077655
85 | 0.0027719 | 0.00069471
86 | 0.0010364 | 0.00025973
87 | 0.0011723 | 0.00029382
88 | 0.0022562 | 0.00056546
89 | 0.0031128 | 0.00078014
90 | 0.00092323 | 0.00023138
91 | 0.00095646 | 0.00023971
92 | 0.00080353 | 0.00020138
93 | 0.000578 | 0.00014486
94 | 0.0007625 | 0.0001911
95 | 0.00052078 | 0.00013052
96 | 0.00025465 | 6.382e-05
97 | 0.00033734 | 8.4546e-05
98 | 0.00018546 | 4.648e-05
99 | 0.002145 | 0.00053758
100 | 0.0018834 | 0.00047203

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1