## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1404-11_2_2_node_54 | 0.4 | n |  | TRUE
1 | bus_LV_1404-11_2_2_node_105 | 0.4 | n |  | TRUE
2 | bus_LV_1404-11_2_2_node_45 | 0.4 | n |  | TRUE
3 | bus_LV_1404-11_2_2_node_24 | 0.4 | n |  | TRUE
4 | bus_LV_1404-11_2_2_node_25 | 0.4 | n |  | TRUE
5 | bus_LV_1404-11_2_2_node_26 | 0.4 | n |  | TRUE
6 | bus_LV_1404-11_2_2_node_27 | 0.4 | n |  | TRUE
7 | bus_LV_1404-11_2_2_node_28 | 0.4 | n |  | TRUE
8 | bus_LV_1404-11_2_2_node_29 | 0.4 | n |  | TRUE
9 | bus_LV_1404-11_2_2_node_36 | 0.4 | n |  | TRUE
10 | bus_LV_1404-11_2_2_node_59 | 0.4 | n |  | TRUE
11 | bus_LV_1404-11_2_2_node_33 | 0.4 | n |  | TRUE
12 | bus_LV_1404-11_2_2_node_30 | 0.4 | n |  | TRUE
13 | bus_LV_1404-11_2_2_node_34 | 0.4 | n |  | TRUE
14 | bus_LV_1404-11_2_2_node_103 | 0.4 | n |  | TRUE
15 | bus_LV_1404-11_2_2_node_56 | 0.4 | n |  | TRUE
16 | bus_LV_1404-11_2_2_node_31 | 0.4 | n |  | TRUE
17 | bus_LV_1404-11_2_2_node_32 | 0.4 | n |  | TRUE
18 | bus_LV_1404-11_2_2_node_38 | 0.4 | n |  | TRUE
19 | bus_LV_1404-11_2_2_node_39 | 0.4 | n |  | TRUE
20 | bus_LV_1404-11_2_2_node_35 | 0.4 | n |  | TRUE
21 | bus_LV_1404-11_2_2_node_37 | 0.4 | n |  | TRUE
22 | bus_LV_1404-11_2_2_node_46 | 0.4 | n |  | TRUE
23 | bus_LV_1404-11_2_2_node_52 | 0.4 | n |  | TRUE
24 | bus_LV_1404-11_2_2_node_40 | 0.4 | n |  | TRUE
25 | bus_LV_1404-11_2_2_node_41 | 0.4 | n |  | TRUE
26 | bus_LV_1404-11_2_2_node_42 | 0.4 | n |  | TRUE
27 | bus_LV_1404-11_2_2_node_43 | 0.4 | n |  | TRUE
28 | bus_LV_1404-11_2_2_node_44 | 0.4 | n |  | TRUE
29 | bus_LV_1404-11_2_2_node_53 | 0.4 | n |  | TRUE
30 | bus_LV_1404-11_2_2_node_50 | 0.4 | n |  | TRUE
31 | bus_LV_1404-11_2_2_node_47 | 0.4 | n |  | TRUE
32 | bus_LV_1404-11_2_2_node_48 | 0.4 | n |  | TRUE
33 | bus_LV_1404-11_2_2_node_49 | 0.4 | n |  | TRUE
34 | bus_LV_1404-11_2_2_node_51 | 0.4 | n |  | TRUE
35 | bus_LV_1404-11_2_2_node_55 | 0.4 | n |  | TRUE
36 | bus_LV_1404-11_2_2_node_57 | 0.4 | n |  | TRUE
37 | bus_LV_1404-11_2_2_node_58 | 0.4 | n |  | TRUE
38 | bus_LV_1404-11_2_2_node_60 | 0.4 | n |  | TRUE
39 | bus_LV_1404-11_2_2_node_100 | 0.4 | n |  | TRUE
40 | bus_LV_1404-11_2_2_node_99 | 0.4 | n |  | TRUE
41 | bus_LV_1404-11_2_2_node_62 | 0.4 | n |  | TRUE
42 | bus_LV_1404-11_2_2_node_61 | 0.4 | n |  | TRUE
43 | bus_LV_1404-11_2_2_node_63 | 0.4 | n |  | TRUE
44 | bus_LV_1404-11_2_2_node_101 | 0.4 | n |  | TRUE
45 | bus_LV_1404-11_2_2_node_66 | 0.4 | n |  | TRUE
46 | bus_LV_1404-11_2_2_node_64 | 0.4 | n |  | TRUE
47 | bus_LV_1404-11_2_2_node_65 | 0.4 | n |  | TRUE
48 | bus_LV_1404-11_2_2_node_67 | 0.4 | n |  | TRUE
49 | bus_LV_1404-11_2_2_node_97 | 0.4 | n |  | TRUE
50 | bus_LV_1404-11_2_2_node_95 | 0.4 | n |  | TRUE
51 | bus_LV_1404-11_2_2_node_98 | 0.4 | n |  | TRUE
52 | bus_LV_1404-11_2_2_node_102 | 0.4 | n |  | TRUE
53 | bus_MV_0_node_40 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1404-11_2_2_load_105 | 1 | 0.0027338 | 0.00068516 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1404-11_2_2_load_24 | 3 | 0.0011516 | 0.00028862 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1404-11_2_2_load_25 | 4 | 0.00018538 | 4.6462e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1404-11_2_2_load_26 | 5 | 6.8611e-05 | 1.7196e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1404-11_2_2_load_27 | 6 | 0.00024595 | 6.1641e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1404-11_2_2_load_36 | 9 | 0.00015587 | 3.9064e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1404-11_2_2_load_33 | 11 | 0.00018285 | 4.5827e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1404-11_2_2_load_30 | 12 | 8.7993e-05 | 2.2053e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1404-11_2_2_load_34 | 13 | 0.0001551 | 3.8872e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1404-11_2_2_load_103 | 14 | 0.00034119 | 8.551e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1404-11_2_2_load_31 | 16 | 0.00015543 | 3.8955e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1404-11_2_2_load_32 | 17 | 0.00053722 | 0.00013464 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1404-11_2_2_load_38 | 18 | 0.00050911 | 0.0001276 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1404-11_2_2_load_39 | 19 | 0.00048929 | 0.00012263 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1404-11_2_2_load_35 | 20 | 0.00033106 | 8.2972e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1404-11_2_2_load_37 | 21 | 0.00050294 | 0.00012605 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1404-11_2_2_load_46 | 22 | 0.0005224 | 0.00013093 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1404-11_2_2_load_52 | 23 | 0.00052589 | 0.0001318 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1404-11_2_2_load_40 | 24 | 0.00054546 | 0.0001367 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1404-11_2_2_load_41 | 25 | 0.00053204 | 0.00013334 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1404-11_2_2_load_42 | 26 | 0.00050806 | 0.00012733 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1404-11_2_2_load_43 | 27 | 0.00048782 | 0.00012226 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1404-11_2_2_load_53 | 29 | 0.00046721 | 0.00011709 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1404-11_2_2_load_50 | 30 | 0.00047077 | 0.00011799 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1404-11_2_2_load_47 | 31 | 0.00048273 | 0.00012098 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1404-11_2_2_load_48 | 32 | 0.00043314 | 0.00010856 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1404-11_2_2_load_49 | 33 | 0.00056637 | 0.00014195 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1404-11_2_2_load_51 | 34 | 0.00051682 | 0.00012953 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1404-11_2_2_load_55 | 35 | 0.00041621 | 0.00010431 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1404-11_2_2_load_60 | 38 | 0.00056543 | 0.00014171 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1404-11_2_2_load_100 | 39 | 0.00012092 | 3.0304e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1404-11_2_2_load_99 | 40 | 0.00058351 | 0.00014624 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1404-11_2_2_load_62 | 41 | 0.00016823 | 4.2162e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1404-11_2_2_load_101 | 44 | 6.0896e-05 | 1.5262e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1404-11_2_2_load_66 | 45 | 0.00024772 | 6.2086e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1404-11_2_2_load_64 | 46 | 0.00027917 | 6.9967e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1404-11_2_2_load_65 | 47 | 0.00010129 | 2.5386e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1404-11_2_2_load_95 | 50 | 0.00022426 | 5.6205e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1404-11_2_2_load_98 | 51 | 0.00018874 | 4.7302e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1404-11_2_2_load_102 | 52 | 0.00037062 | 9.2886e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 24 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1404-11_2_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.023886 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1404-11_2_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.18282 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1404-11_2_2_line_2 | NAYY 4x150 SE | 2 | 29 | 0.032112 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1404-11_2_2_line_3 | NAYY 4x150 SE | 2 | 28 | 0.070168 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1404-11_2_2_line_4 | NAYY 4x150 SE | 3 | 4 | 0.011122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1404-11_2_2_line_5 | NAYY 4x150 SE | 3 | 5 | 0.032657 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1404-11_2_2_line_6 | NAYY 4x150 SE | 4 | 6 | 0.00074857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1404-11_2_2_line_7 | NAYY 4x150 SE | 5 | 7 | 0.055593 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1404-11_2_2_line_8 | NAYY 4x150 SE | 6 | 8 | 0.010657 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1404-11_2_2_line_9 | NAYY 4x150 SE | 7 | 9 | 0.14793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1404-11_2_2_line_10 | NAYY 4x150 SE | 7 | 10 | 0.05022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1404-11_2_2_line_11 | NAYY 4x150 SE | 8 | 11 | 0.016537 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1404-11_2_2_line_12 | NAYY 4x150 SE | 8 | 12 | 0.014869 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1404-11_2_2_line_13 | NAYY 4x150 SE | 9 | 13 | 0.11527 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1404-11_2_2_line_14 | NAYY 4x150 SE | 10 | 14 | 0.017478 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1404-11_2_2_line_15 | NAYY 4x150 SE | 10 | 15 | 0.059679 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1404-11_2_2_line_16 | NAYY 4x150 SE | 12 | 16 | 0.050075 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1404-11_2_2_line_17 | NAYY 4x150 SE | 13 | 20 | 0.31368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1404-11_2_2_line_18 | NAYY 4x150 SE | 15 | 37 | 0.25889 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1404-11_2_2_line_19 | NAYY 4x150 SE | 15 | 35 | 0.1634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1404-11_2_2_line_20 | NAYY 4x150 SE | 16 | 17 | 0.10903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1404-11_2_2_line_21 | NAYY 4x150 SE | 17 | 18 | 0.042714 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1404-11_2_2_line_22 | NAYY 4x150 SE | 18 | 19 | 0.033137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1404-11_2_2_line_23 | NAYY 4x150 SE | 19 | 24 | 0.028118 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1404-11_2_2_line_24 | NAYY 4x150 SE | 20 | 21 | 0.02872 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1404-11_2_2_line_25 | NAYY 4x150 SE | 21 | 22 | 0.019524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1404-11_2_2_line_26 | NAYY 4x150 SE | 22 | 23 | 0.029547 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1404-11_2_2_line_27 | NAYY 4x150 SE | 24 | 25 | 0.028634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1404-11_2_2_line_28 | NAYY 4x150 SE | 25 | 26 | 0.029202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1404-11_2_2_line_29 | NAYY 4x150 SE | 26 | 27 | 0.02958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1404-11_2_2_line_30 | NAYY 4x150 SE | 27 | 28 | 0.17621 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1404-11_2_2_line_31 | NAYY 4x150 SE | 29 | 30 | 0.028127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1404-11_2_2_line_32 | NAYY 4x150 SE | 30 | 32 | 0.033742 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1404-11_2_2_line_33 | NAYY 4x150 SE | 31 | 32 | 0.029774 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1404-11_2_2_line_34 | NAYY 4x150 SE | 31 | 33 | 0.036728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1404-11_2_2_line_35 | NAYY 4x150 SE | 33 | 34 | 0.041895 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1404-11_2_2_line_36 | NAYY 4x150 SE | 35 | 36 | 0.0094546 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1404-11_2_2_line_37 | NAYY 4x150 SE | 36 | 38 | 0.043781 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1404-11_2_2_line_38 | NAYY 4x150 SE | 37 | 39 | 0.022907 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1404-11_2_2_line_39 | NAYY 4x150 SE | 37 | 40 | 0.017391 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1404-11_2_2_line_40 | NAYY 4x150 SE | 38 | 41 | 0.040391 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1404-11_2_2_line_41 | NAYY 4x150 SE | 39 | 44 | 0.23777 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1404-11_2_2_line_42 | NAYY 4x150 SE | 41 | 42 | 0.0077886 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1404-11_2_2_line_43 | NAYY 4x150 SE | 42 | 43 | 0.23028 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1404-11_2_2_line_44 | NAYY 4x150 SE | 43 | 45 | 0.11359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1404-11_2_2_line_45 | NAYY 4x150 SE | 44 | 52 | 0.067054 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1404-11_2_2_line_46 | NAYY 4x150 SE | 45 | 48 | 0.33118 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1404-11_2_2_line_47 | NAYY 4x150 SE | 46 | 47 | 0.0040601 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1404-11_2_2_line_48 | NAYY 4x150 SE | 47 | 48 | 0.21051 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1404-11_2_2_line_49 | NAYY 4x150 SE | 48 | 49 | 0.24406 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1404-11_2_2_line_50 | NAYY 4x150 SE | 49 | 51 | 0.2651 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1404-11_2_2_line_51 | NAYY 4x150 SE | 49 | 50 | 0.051992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1404-11_2_2_trafo_40 | 0.25 MVA 20/0.4 kV | 53 | 24 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15
0 | 2664447.7963 | 1184491.153 | 2664444.6502 | 1184483.4593 | 2664442.8947 | 1184482.0285 | 2664436.9795 | 1184480.5529 | 2664432.9842 | 1184480.8435 | 2664429.9119 | 1184481.8999
1 | 2664343.205 | 1184602.0595 | 2664342.8095 | 1184582.0216 | 2664342.0679 | 1184574.3204 | 2664340.5426 | 1184567.0887 | 2664338.3484 | 1184560.3057 | 2664335.4197 | 1184553.6816 | 2664330.7782 | 1184544.4932 | 2664363.262 | 1184529.1443 | 2664400.1636 | 1184515.3994 | 2664411.8333 | 1184510.5776 | 2664415.694 | 1184507.8953 | 2664419.4086 | 1184504.6 | 2664424.3216 | 1184497.7712 | 2664426.6147 | 1184493.2154 | 2664428.4465 | 1184484.7191 | 2664429.9119 | 1184481.8999
2 | 2664343.205 | 1184602.0595 | 2664351.4326 | 1184611.3754 | 2664357.0751 | 1184612.6478 | 2664366.4374 | 1184622.9209
3 | 2664343.1919 | 1184672.2107 | 2664343.205 | 1184602.0595
4 | 2664448.345 | 1185221.9963 | 2664446.4827 | 1185211.3402 | 2664446.4326 | 1185211.0402
5 | 2664448.345 | 1185221.9963 | 2664448.805 | 1185224.6284 | 2664451.2898 | 1185251.8929 | 2664451.3952 | 1185254.498
6 | 2664446.4326 | 1185211.0402 | 2664446.3093 | 1185210.3019
7 | 2664473.118 | 1185302.2566 | 2664464.3362 | 1185295.6027 | 2664460.0045 | 1185291.0313 | 2664457.2002 | 1185287.0766 | 2664455.2312 | 1185282.8086 | 2664453.2765 | 1185276.5062 | 2664451.977 | 1185268.8878 | 2664451.3952 | 1185254.498
8 | 2664444.5539 | 1185199.7906 | 2664446.3093 | 1185210.3019
9 | 2664473.118 | 1185302.2566 | 2664480.5839 | 1185280.1242 | 2664482.6763 | 1185268.6735 | 2664484.3094 | 1185255.2278 | 2664484.7518 | 1185200.6568 | 2664485.2242 | 1185155.841
10 | 2664514.3659 | 1185330.9947 | 2664502.6117 | 1185321.8407 | 2664486.5475 | 1185311.7732 | 2664473.118 | 1185302.2566
11 | 2664444.5539 | 1185199.7906 | 2664428.1103 | 1185201.55
12 | 2664444.5539 | 1185199.7906 | 2664442.4887 | 1185185.0656
13 | 2664458.3369 | 1185046.3531 | 2664466.2669 | 1185080.0333 | 2664484.302 | 1185111.2785 | 2664485.4694 | 1185132.5811 | 2664485.2242 | 1185155.841
14 | 2664514.3659 | 1185330.9947 | 2664520.0746 | 1185314.4748
15 | 2664514.3659 | 1185330.9947 | 2664524.6161 | 1185341.6111 | 2664531.8233 | 1185350.5939 | 2664537.4704 | 1185359.8711 | 2664542.7323 | 1185370.1781 | 2664546.2681 | 1185380.6111
16 | 2664442.4887 | 1185185.0656 | 2664438.2592 | 1185154.9083 | 2664436.1868 | 1185135.3955
17 | 2664458.3369 | 1185046.3531 | 2664458.0556 | 1185045.1583 | 2664460.0395 | 1184990.5929 | 2664456.6877 | 1184949.5555 | 2664443.6637 | 1184844.7888 | 2664467.3922 | 1184783.2643 | 2664465.937 | 1184738.1236
18 | 2664546.2681 | 1185380.6111 | 2664551.0982 | 1185375.0377 | 2664559.8405 | 1185352.052 | 2664562.7888 | 1185336.2636 | 2664570.5108 | 1185303.15 | 2664571.4654 | 1185275.4889 | 2664575.3419 | 1185267.0591 | 2664586.3609 | 1185250.9575 | 2664622.9713 | 1185216.4546 | 2664669.1688 | 1185163.5336
19 | 2664546.2681 | 1185380.6111 | 2664547.9812 | 1185386.6552 | 2664549.6741 | 1185394.578 | 2664550.6486 | 1185402.5931 | 2664550.9022 | 1185410.9339 | 2664549.1807 | 1185435.4072 | 2664547.9525 | 1185451.6477 | 2664547.9639 | 1185459.797 | 2664551.0383 | 1185500.987 | 2664550.8272 | 1185509.2451 | 2664549.928 | 1185515.4945 | 2664548.5961 | 1185521.5281 | 2664546.7975 | 1185527.6678 | 2664543.8102 | 1185535.7513 | 2664540.8395 | 1185541.5885
20 | 2664407.5685 | 1185031.1751 | 2664418.5916 | 1185056.1515 | 2664428.9816 | 1185084.3348 | 2664431.0062 | 1185090.5379 | 2664432.195 | 1185097.8104 | 2664436.1868 | 1185135.3955
21 | 2664407.5685 | 1185031.1751 | 2664396.9686 | 1185007.1577 | 2664393.3029 | 1184993.1547 | 2664392.8522 | 1184991.2198
22 | 2664392.8522 | 1184991.2198 | 2664390.0635 | 1184979.2453 | 2664388.0533 | 1184958.5008
23 | 2664388.0533 | 1184958.5008 | 2664387.0061 | 1184947.6944 | 2664385.3624 | 1184935.1585 | 2664384.5295 | 1184930.6162
24 | 2664465.937 | 1184738.1236 | 2664465.0116 | 1184709.4186 | 2664465.0116 | 1184709.4186
25 | 2664465.0116 | 1184709.4186 | 2664470.891 | 1184690.8005
26 | 2664470.891 | 1184690.8005 | 2664479.7887 | 1184662.6247
27 | 2664384.5295 | 1184930.6162 | 2664383.3075 | 1184923.9522 | 2664377.7441 | 1184902.8129
28 | 2664377.7441 | 1184902.8129 | 2664370.312 | 1184874.5728
29 | 2664370.312 | 1184874.5728 | 2664362.7836 | 1184845.9671
30 | 2664343.1919 | 1184672.2107 | 2664343.7329 | 1184735.5527 | 2664344.2506 | 1184776.893 | 2664352.0234 | 1184805.0815 | 2664362.7836 | 1184845.9671
31 | 2664364.0805 | 1184650.9488 | 2664366.4374 | 1184622.9209 | 2664366.4374 | 1184622.9209
32 | 2664360.7312 | 1184684.5164 | 2664362.2193 | 1184673.0821 | 2664364.0805 | 1184650.9488
33 | 2664356.8885 | 1184714.0415 | 2664360.7312 | 1184684.5164
34 | 2664356.8885 | 1184714.0415 | 2664354.1409 | 1184735.1531 | 2664352.1232 | 1184750.4592
35 | 2664352.1232 | 1184750.4592 | 2664351.0661 | 1184758.4779 | 2664352.1793 | 1184776.3556 | 2664356.1397 | 1184791.7493
36 | 2664536.5512 | 1185550.0147 | 2664540.8395 | 1185541.5885
37 | 2664536.5512 | 1185550.0147 | 2664540.4449 | 1185555.5487 | 2664541.3089 | 1185558.2373 | 2664541.109 | 1185561.2035 | 2664539.1364 | 1185564.373 | 2664522.6386 | 1185586.3551
38 | 2664669.1688 | 1185163.5336 | 2664671.376 | 1185159.8665 | 2664676.2668 | 1185141.8936
39 | 2664669.1688 | 1185163.5336 | 2664684.5777 | 1185171.5958
40 | 2664498.2302 | 1185618.1635 | 2664498.2302 | 1185618.1635 | 2664500.609 | 1185616.9662 | 2664501.9941 | 1185615.2023 | 2664510.5646 | 1185602.4428 | 2664522.6386 | 1185586.3551
41 | 2664676.2668 | 1185141.8936 | 2664677.8613 | 1185136.0339 | 2664677.9878 | 1185126.4409 | 2664666.6968 | 1185053.8663 | 2664652.0994 | 1184983.513 | 2664642.0983 | 1184933.5098 | 2664637.6341 | 1184919.9872 | 2664635.8053 | 1184908.5676
42 | 2664490.5978 | 1185616.8028 | 2664494.5089 | 1185617.8788 | 2664498.2302 | 1185618.1635
43 | 2664490.5978 | 1185616.8028 | 2664487.9248 | 1185626.1905 | 2664485.2336 | 1185642.2263 | 2664483.7862 | 1185658.2866 | 2664485.1701 | 1185675.0667 | 2664487.9049 | 1185710.9723 | 2664483.5397 | 1185769.7924 | 2664483.4794 | 1185783.1883 | 2664485.3383 | 1185804.0425 | 2664490.9581 | 1185845.5935
44 | 2664490.9581 | 1185845.5935 | 2664600.6098 | 1185815.9478
45 | 2664626.8427 | 1184842.2831 | 2664630.3293 | 1184857.0501 | 2664631.6916 | 1184882.8796 | 2664635.8053 | 1184908.5676
46 | 2664858.0132 | 1185610.1083 | 2664759.8415 | 1185669.7031 | 2664751.6169 | 1185675.1285 | 2664600.6098 | 1185815.9478
47 | 2664669.0195 | 1185517.3906 | 2664665.4091 | 1185519.2479
48 | 2664669.0195 | 1185517.3906 | 2664858.0132 | 1185610.1083
49 | 2664858.0132 | 1185610.1083 | 2665100.9112 | 1185586.306
50 | 2665100.9112 | 1185586.306 | 2665125.0028 | 1185587.2128 | 2665156.2531 | 1185570.5873 | 2665258.099 | 1185518.9213 | 2665282.8107 | 1185482.5695 | 2665294.6328 | 1185465.0549 | 2665300.8536 | 1185460.7869 | 2665307.1116 | 1185461.5111 | 2665310.3169 | 1185465.0258 | 2665311.884 | 1185468.3003 | 2665313.1579 | 1185472.1687
51 | 2665100.9112 | 1185586.306 | 2665113.5131 | 1185549.6441 | 2665114.747 | 1185536.4773

## bus_geodata
| x | y | coords
0 | 2664429.9119 | 1184481.8999
1 | 2664447.7963 | 1184491.153
2 | 2664343.205 | 1184602.0595
3 | 2664448.345 | 1185221.9963
4 | 2664446.4326 | 1185211.0402
5 | 2664451.3952 | 1185254.498
6 | 2664446.3093 | 1185210.3019
7 | 2664473.118 | 1185302.2566
8 | 2664444.5539 | 1185199.7906
9 | 2664485.2242 | 1185155.841
10 | 2664514.3659 | 1185330.9947
11 | 2664428.1103 | 1185201.55
12 | 2664442.4887 | 1185185.0656
13 | 2664458.3369 | 1185046.3531
14 | 2664520.0746 | 1185314.4748
15 | 2664546.2681 | 1185380.6111
16 | 2664436.1868 | 1185135.3955
17 | 2664407.5685 | 1185031.1751
18 | 2664392.8522 | 1184991.2198
19 | 2664388.0533 | 1184958.5008
20 | 2664465.937 | 1184738.1236
21 | 2664465.0116 | 1184709.4186
22 | 2664470.891 | 1184690.8005
23 | 2664479.7887 | 1184662.6247
24 | 2664384.5295 | 1184930.6162
25 | 2664377.7441 | 1184902.8129
26 | 2664370.312 | 1184874.5728
27 | 2664362.7836 | 1184845.9671
28 | 2664343.1919 | 1184672.2107
29 | 2664366.4374 | 1184622.9209
30 | 2664364.0805 | 1184650.9488
31 | 2664356.8885 | 1184714.0415
32 | 2664360.7312 | 1184684.5164
33 | 2664352.1232 | 1184750.4592
34 | 2664356.1397 | 1184791.7493
35 | 2664540.8395 | 1185541.5885
36 | 2664536.5512 | 1185550.0147
37 | 2664669.1688 | 1185163.5336
38 | 2664522.6386 | 1185586.3551
39 | 2664676.2668 | 1185141.8936
40 | 2664684.5777 | 1185171.5958
41 | 2664498.2302 | 1185618.1635
42 | 2664490.5978 | 1185616.8028
43 | 2664490.9581 | 1185845.5935
44 | 2664635.8053 | 1184908.5676
45 | 2664600.6098 | 1185815.9478
46 | 2664665.4091 | 1185519.2479
47 | 2664669.0195 | 1185517.3906
48 | 2664858.0132 | 1185610.1083
49 | 2665100.9112 | 1185586.306
50 | 2665114.747 | 1185536.4773
51 | 2665313.1579 | 1185472.1687
52 | 2664626.8427 | 1184842.2831
53 | 2664384.5295 | 1184930.6162

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99645 | -0.025046 | 0 | 0
1 | 0.99636 | -0.025703 | 0.0027338 | 0.00068516
2 | 0.99717 | -0.020006 | 0 | 0
3 | 0.99648 | -0.025619 | 0.0011516 | 0.00028862
4 | 0.99659 | -0.024793 | 0.00018538 | 4.6462e-05
5 | 0.99621 | -0.027667 | 6.8611e-05 | 1.7196e-05
6 | 0.9966 | -0.024736 | 0.00024595 | 6.1641e-05
7 | 0.99574 | -0.031115 | 0 | 0
8 | 0.99672 | -0.023899 | 0 | 0
9 | 0.99527 | -0.034466 | 0.00015587 | 3.9064e-05
10 | 0.99548 | -0.033088 | 0 | 0
11 | 0.99671 | -0.023929 | 0.00018285 | 4.5827e-05
12 | 0.99688 | -0.022702 | 8.7993e-05 | 2.2053e-05
13 | 0.99494 | -0.036884 | 0.0001551 | 3.8872e-05
14 | 0.99547 | -0.033149 | 0.00034119 | 8.551e-05
15 | 0.99519 | -0.035225 | 0 | 0
16 | 0.99744 | -0.018631 | 0.00015543 | 3.8955e-05
17 | 0.99868 | -0.0096041 | 0.00053722 | 0.00013464
18 | 0.99919 | -0.0058412 | 0.00050911 | 0.0001276
19 | 0.99962 | -0.0027549 | 0.00048929 | 0.00012263
20 | 0.99409 | -0.042914 | 0.00033106 | 8.2972e-05
21 | 0.99403 | -0.043366 | 0.00050294 | 0.00012605
22 | 0.994 | -0.043573 | 0.0005224 | 0.00013093
23 | 0.99398 | -0.04373 | 0.00052589 | 0.0001318
24 | 1 | 0 | -0.017534 | -0.0041468
25 | 0.99971 | -0.0020782 | 0.00053204 | 0.00013334
26 | 0.99943 | -0.0040427 | 0.00050806 | 0.00012733
27 | 0.99917 | -0.0058827 | 0.00048782 | 0.00012226
28 | 0.99774 | -0.015984 | 0 | 0
29 | 0.99703 | -0.020958 | 0.00046721 | 0.00011709
30 | 0.99694 | -0.02166 | 0.00047077 | 0.00011799
31 | 0.99677 | -0.022813 | 0.00048273 | 0.00012098
32 | 0.99684 | -0.022342 | 0.00043314 | 0.00010856
33 | 0.99672 | -0.023215 | 0.00056637 | 0.00014195
34 | 0.99668 | -0.023433 | 0.00051682 | 0.00012953
35 | 0.99468 | -0.039095 | 0.00041621 | 0.00010431
36 | 0.99466 | -0.039279 | 0 | 0
37 | 0.99477 | -0.03831 | 0 | 0
38 | 0.99455 | -0.040128 | 0.00056543 | 0.00014171
39 | 0.99475 | -0.038445 | 0.00012092 | 3.0304e-05
40 | 0.99476 | -0.038413 | 0.00058351 | 0.00014624
41 | 0.99448 | -0.040679 | 0.00016823 | 4.2162e-05
42 | 0.99446 | -0.040772 | 0 | 0
43 | 0.99412 | -0.043492 | 0 | 0
44 | 0.99461 | -0.039523 | 6.0896e-05 | 1.5262e-05
45 | 0.99395 | -0.044816 | 0.00024772 | 6.2086e-05
46 | 0.99346 | -0.04862 | 0.00027917 | 6.9967e-05
47 | 0.99346 | -0.048608 | 0.00010129 | 2.5386e-05
48 | 0.99358 | -0.047776 | 0 | 0
49 | 0.99343 | -0.0489 | 0 | 0
50 | 0.99342 | -0.049019 | 0.00022426 | 5.6205e-05
51 | 0.99336 | -0.04944 | 0.00018874 | 4.7302e-05
52 | 0.99457 | -0.039776 | 0.00037062 | 9.2886e-05
53 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0027341 | 0.00068495 | -0.0027338 | -0.00068516 | 2.4845e-07 | -2.1556e-07 | 0.0040827 | 0.0040828 | 0.0040828 | 0.99645 | -0.025046 | 0.99636 | -0.025703 | 1.5122
1 | -0.0027341 | -0.00068495 | 0.002736 | 0.00068329 | 1.9011e-06 | -1.6519e-06 | 0.0040827 | 0.0040819 | 0.0040827 | 0.99645 | -0.025046 | 0.99717 | -0.020006 | 1.5121
2 | 0.002938 | 0.00073383 | -0.0029376 | -0.0007341 | 3.8502e-07 | -2.7077e-07 | 0.0043834 | 0.0043835 | 0.0043835 | 0.99717 | -0.020006 | 0.99703 | -0.020958 | 1.6235
3 | -0.005674 | -0.0014171 | 0.0056771 | 0.0014174 | 3.1375e-06 | 2.9087e-07 | 0.0084653 | 0.0084649 | 0.0084653 | 0.99717 | -0.020006 | 0.99774 | -0.015984 | 3.1353
4 | -0.007094 | -0.0017382 | 0.0070948 | 0.0017384 | 7.7675e-07 | 1.5385e-07 | 0.010579 | 0.010579 | 0.010579 | 0.99648 | -0.025619 | 0.99659 | -0.024793 | 3.9183
5 | 0.0059424 | 0.0014496 | -0.0059408 | -0.0014494 | 1.5996e-06 | 1.8993e-07 | 0.0088599 | 0.00886 | 0.00886 | 0.99648 | -0.025619 | 0.99621 | -0.027667 | 3.2815
6 | -0.0072802 | -0.0017848 | 0.0072803 | 0.0017848 | 5.5052e-08 | 1.142e-08 | 0.010856 | 0.010856 | 0.010856 | 0.99659 | -0.024793 | 0.9966 | -0.024736 | 4.0208
7 | 0.0058722 | 0.0014322 | -0.0058696 | -0.0014319 | 2.6606e-06 | 2.9983e-07 | 0.0087575 | 0.0087578 | 0.0087578 | 0.99621 | -0.027667 | 0.99574 | -0.031115 | 3.2436
8 | -0.0075262 | -0.0018465 | 0.007527 | 0.0018467 | 8.3765e-07 | 1.833e-07 | 0.011223 | 0.011223 | 0.011223 | 0.9966 | -0.024736 | 0.99672 | -0.023899 | 4.1568
9 | 0.0021966 | 0.00054247 | -0.0021956 | -0.00054402 | 9.9318e-07 | -1.5414e-06 | 0.0032798 | 0.0032804 | 0.0032804 | 0.99574 | -0.031115 | 0.99527 | -0.034466 | 1.215
10 | 0.0036729 | 0.00088944 | -0.003672 | -0.00088973 | 9.4043e-07 | -2.9137e-07 | 0.005478 | 0.0054782 | 0.0054782 | 0.99574 | -0.031115 | 0.99548 | -0.033088 | 2.029
11 | 0.00018285 | 4.5612e-05 | -0.00018285 | -4.5827e-05 | 7.6879e-10 | -2.1524e-07 | 0.00027291 | 0.00027298 | 0.00027298 | 0.99672 | -0.023899 | 0.99671 | -0.023929 | 0.10111
12 | -0.0077099 | -0.0018923 | 0.0077111 | 0.0018926 | 1.2263e-06 | 2.7781e-07 | 0.011496 | 0.011496 | 0.011496 | 0.99672 | -0.023899 | 0.99688 | -0.022702 | 4.2579
13 | 0.0020398 | 0.00050495 | -0.0020391 | -0.00050619 | 6.6811e-07 | -1.2406e-06 | 0.0030474 | 0.0030479 | 0.0030479 | 0.99527 | -0.034466 | 0.99494 | -0.036884 | 1.1289
14 | 0.00034119 | 8.5284e-05 | -0.00034119 | -8.551e-05 | 2.8364e-09 | -2.2614e-07 | 0.00050993 | 0.00051001 | 0.00051001 | 0.99548 | -0.033088 | 0.99547 | -0.033149 | 0.18889
15 | 0.0033308 | 0.00080444 | -0.0033299 | -0.00080486 | 9.1928e-07 | -4.2209e-07 | 0.0049683 | 0.0049686 | 0.0049686 | 0.99548 | -0.033088 | 0.99519 | -0.035225 | 1.8402
16 | -0.0077991 | -0.0019146 | 0.0078033 | 0.0019156 | 4.2245e-06 | 9.7159e-07 | 0.011628 | 0.011627 | 0.011628 | 0.99688 | -0.022702 | 0.99744 | -0.018631 | 4.3065
17 | 0.001884 | 0.00046732 | -0.0018824 | -0.00047079 | 1.5529e-06 | -3.473e-06 | 0.002816 | 0.0028174 | 0.0028174 | 0.99494 | -0.036884 | 0.99409 | -0.042914 | 1.0435
18 | 0.0011365 | 0.00027707 | -0.001136 | -0.00028025 | 4.6533e-07 | -3.1835e-06 | 0.0016966 | 0.0016978 | 0.0016978 | 0.99519 | -0.035225 | 0.99477 | -0.03831 | 0.6288
19 | 0.0021934 | 0.0005278 | -0.0021923 | -0.0005295 | 1.0918e-06 | -1.7021e-06 | 0.003272 | 0.0032727 | 0.0032727 | 0.99519 | -0.035225 | 0.99468 | -0.039095 | 1.2121
20 | -0.0079588 | -0.0019545 | 0.0079683 | 0.0019568 | 9.568e-06 | 2.2552e-06 | 0.011859 | 0.011859 | 0.011859 | 0.99744 | -0.018631 | 0.99868 | -0.0096041 | 4.3923
21 | -0.0085056 | -0.0020914 | 0.0085098 | 0.0020925 | 4.2713e-06 | 1.0836e-06 | 0.012659 | 0.012659 | 0.012659 | 0.99868 | -0.0096041 | 0.99919 | -0.0058412 | 4.6886
22 | -0.0090189 | -0.0022201 | 0.0090227 | 0.0022211 | 3.7223e-06 | 9.9743e-07 | 0.013417 | 0.013417 | 0.013417 | 0.99919 | -0.0058412 | 0.99962 | -0.0027549 | 4.9693
23 | -0.009512 | -0.0023437 | 0.0095155 | 0.0023447 | 3.5107e-06 | 9.8152e-07 | 0.014145 | 0.014145 | 0.014145 | 0.99962 | -0.0027549 | 1 | 0 | 5.239
24 | 0.0015514 | 0.00038782 | -0.0015513 | -0.00038816 | 9.6617e-08 | -3.3516e-07 | 0.0023218 | 0.002322 | 0.002322 | 0.99409 | -0.042914 | 0.99403 | -0.043366 | 0.85999
25 | 0.0010483 | 0.00026211 | -0.0010483 | -0.00026235 | 2.9997e-08 | -2.4155e-07 | 0.0015691 | 0.0015692 | 0.0015692 | 0.99403 | -0.043366 | 0.994 | -0.043573 | 0.58118
26 | 0.00052591 | 0.00013142 | -0.00052589 | -0.0001318 | 1.1426e-08 | -3.786e-07 | 0.00078715 | 0.00078728 | 0.00078728 | 0.994 | -0.043573 | 0.99398 | -0.04373 | 0.29159
27 | 0.0072184 | 0.001802 | -0.0072163 | -0.0018016 | 2.0605e-06 | 4.1695e-07 | 0.010739 | 0.010739 | 0.010739 | 1 | 0 | 0.99971 | -0.0020782 | 3.9773
28 | 0.0066843 | 0.0016683 | -0.0066825 | -0.001668 | 1.8029e-06 | 3.1064e-07 | 0.0099468 | 0.0099469 | 0.0099469 | 0.99971 | -0.0020782 | 0.99943 | -0.0040427 | 3.684
29 | 0.0061744 | 0.0015406 | -0.0061729 | -0.0015404 | 1.5591e-06 | 2.1212e-07 | 0.0091905 | 0.0091906 | 0.0091906 | 0.99943 | -0.0040427 | 0.99917 | -0.0058827 | 3.4039
30 | 0.005685 | 0.0014181 | -0.0056771 | -0.0014174 | 7.8779e-06 | 7.2542e-07 | 0.0084641 | 0.0084649 | 0.0084649 | 0.99917 | -0.0058827 | 0.99774 | -0.015984 | 3.1352
31 | 0.0024704 | 0.00061701 | -0.0024702 | -0.00061729 | 2.385e-07 | -2.7505e-07 | 0.0036862 | 0.0036864 | 0.0036864 | 0.99703 | -0.020958 | 0.99694 | -0.02166 | 1.3653
32 | 0.0019994 | 0.0004993 | -0.0019992 | -0.00049967 | 1.8745e-07 | -3.6783e-07 | 0.0029837 | 0.0029838 | 0.0029838 | 0.99694 | -0.02166 | 0.99684 | -0.022342 | 1.1051
33 | -0.001566 | -0.00039146 | 0.0015661 | 0.00039111 | 1.015e-07 | -3.4908e-07 | 0.0023374 | 0.0023373 | 0.0023374 | 0.99677 | -0.022813 | 0.99684 | -0.022342 | 0.86571
34 | 0.0010833 | 0.00027048 | -0.0010832 | -0.00027093 | 5.9914e-08 | -4.5567e-07 | 0.0016168 | 0.0016169 | 0.0016169 | 0.99677 | -0.022813 | 0.99672 | -0.023215 | 0.59887
35 | 0.00051683 | 0.00012899 | -0.00051682 | -0.00012953 | 1.556e-08 | -5.4003e-07 | 0.0007714 | 0.00077159 | 0.00077159 | 0.99672 | -0.023215 | 0.99668 | -0.023433 | 0.28577
36 | 0.0017761 | 0.00042519 | -0.0017761 | -0.00042529 | 4.1434e-08 | -1.0678e-07 | 0.0026501 | 0.0026501 | 0.0026501 | 0.99468 | -0.039095 | 0.99466 | -0.039279 | 0.98153
37 | 0.0017761 | 0.00042529 | -0.0017759 | -0.00042579 | 1.9188e-07 | -4.9439e-07 | 0.0026501 | 0.0026503 | 0.0026503 | 0.99466 | -0.039279 | 0.99455 | -0.040128 | 0.98161
38 | 0.00055252 | 0.00013423 | -0.00055251 | -0.00013452 | 9.7299e-09 | -2.9364e-07 | 0.000825 | 0.0008251 | 0.0008251 | 0.99477 | -0.03831 | 0.99475 | -0.038445 | 0.30559
39 | 0.00058352 | 0.00014602 | -0.00058351 | -0.00014624 | 8.2668e-09 | -2.2259e-07 | 0.00087277 | 0.00087285 | 0.00087285 | 0.99477 | -0.03831 | 0.99476 | -0.038413 | 0.32328
40 | 0.0012104 | 0.00028408 | -0.0012103 | -0.00028457 | 8.2071e-08 | -4.9254e-07 | 0.0018044 | 0.0018046 | 0.0018046 | 0.99455 | -0.040128 | 0.99448 | -0.040679 | 0.66837
41 | 0.00043159 | 0.00010422 | -0.00043153 | -0.00010728 | 6.1678e-08 | -3.0625e-06 | 0.00064423 | 0.0006453 | 0.0006453 | 0.99475 | -0.038445 | 0.99461 | -0.039523 | 0.239
42 | 0.0010421 | 0.00024241 | -0.0010421 | -0.00024251 | 1.172e-08 | -9.6547e-08 | 0.0015529 | 0.0015529 | 0.0015529 | 0.99448 | -0.040679 | 0.99446 | -0.040772 | 0.57516
43 | 0.0010421 | 0.00024251 | -0.0010418 | -0.00024536 | 3.4676e-07 | -2.8534e-06 | 0.0015529 | 0.0015539 | 0.0015539 | 0.99446 | -0.040772 | 0.99412 | -0.043492 | 0.57553
44 | 0.0010418 | 0.00024536 | -0.0010416 | -0.00024677 | 1.7121e-07 | -1.4066e-06 | 0.0015539 | 0.0015544 | 0.0015544 | 0.99412 | -0.043492 | 0.99395 | -0.044816 | 0.57571
45 | 0.00037063 | 9.2021e-05 | -0.00037062 | -9.2886e-05 | 1.2858e-08 | -8.6526e-07 | 0.00055419 | 0.0005545 | 0.0005545 | 0.99461 | -0.039523 | 0.99457 | -0.039776 | 0.20537
46 | 0.00079387 | 0.00018468 | -0.00079358 | -0.00018886 | 2.8985e-07 | -4.1793e-06 | 0.0011836 | 0.001185 | 0.001185 | 0.99395 | -0.044816 | 0.99358 | -0.047776 | 0.4389
47 | -0.00027917 | -6.9966e-05 | 0.00027917 | 6.9914e-05 | 4.4295e-10 | -5.2401e-08 | 0.00041814 | 0.00041812 | 0.00041814 | 0.99346 | -0.04862 | 0.99346 | -0.048608 | 0.15487
48 | -0.00038046 | -9.53e-05 | 0.0003805 | 9.259e-05 | 4.2583e-08 | -2.7097e-06 | 0.00056984 | 0.00056889 | 0.00056984 | 0.99346 | -0.048608 | 0.99358 | -0.047776 | 0.21105
49 | 0.00041307 | 9.627e-05 | -0.00041301 | -9.9408e-05 | 5.7916e-08 | -3.1382e-06 | 0.00061615 | 0.00061721 | 0.00061721 | 0.99358 | -0.047776 | 0.99343 | -0.0489 | 0.2286
50 | 0.00018875 | 4.3875e-05 | -0.00018874 | -4.7302e-05 | 1.3167e-08 | -3.4271e-06 | 0.00028155 | 0.00028272 | 0.00028272 | 0.99343 | -0.0489 | 0.99336 | -0.04944 | 0.10471
51 | 0.00022426 | 5.5533e-05 | -0.00022426 | -5.6205e-05 | 3.6582e-09 | -6.7175e-07 | 0.00033568 | 0.00033591 | 0.00033591 | 0.99343 | -0.0489 | 0.99342 | -0.049019 | 0.12441

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.018079 | 0.0042835

## res_load
| p_mw | q_mvar
0 | 0.0027338 | 0.00068516
1 | 0.0011516 | 0.00028862
2 | 0.00018538 | 4.6462e-05
3 | 6.8611e-05 | 1.7196e-05
4 | 0.00024595 | 6.1641e-05
5 | 0.00015587 | 3.9064e-05
6 | 0.00018285 | 4.5827e-05
7 | 8.7993e-05 | 2.2053e-05
8 | 0.0001551 | 3.8872e-05
9 | 0.00034119 | 8.551e-05
10 | 0.00015543 | 3.8955e-05
11 | 0.00053722 | 0.00013464
12 | 0.00050911 | 0.0001276
13 | 0.00048929 | 0.00012263
14 | 0.00033106 | 8.2972e-05
15 | 0.00050294 | 0.00012605
16 | 0.0005224 | 0.00013093
17 | 0.00052589 | 0.0001318
18 | 0.00054546 | 0.0001367
19 | 0.00053204 | 0.00013334
20 | 0.00050806 | 0.00012733
21 | 0.00048782 | 0.00012226
22 | 0.00046721 | 0.00011709
23 | 0.00047077 | 0.00011799
24 | 0.00048273 | 0.00012098
25 | 0.00043314 | 0.00010856
26 | 0.00056637 | 0.00014195
27 | 0.00051682 | 0.00012953
28 | 0.00041621 | 0.00010431
29 | 0.00056543 | 0.00014171
30 | 0.00012092 | 3.0304e-05
31 | 0.00058351 | 0.00014624
32 | 0.00016823 | 4.2162e-05
33 | 6.0896e-05 | 1.5262e-05
34 | 0.00024772 | 6.2086e-05
35 | 0.00027917 | 6.9967e-05
36 | 0.00010129 | 2.5386e-05
37 | 0.00022426 | 5.6205e-05
38 | 0.00018874 | 4.7302e-05
39 | 0.00037062 | 9.2886e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1