## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1404-1_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1404-1_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1404-1_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1404-1_0_2_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1404-1_0_2_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_1404-1_0_2_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1404-1_0_2_node_126 | 0.4 | n |  | TRUE
7 | bus_LV_1404-1_0_2_node_125 | 0.4 | n |  | TRUE
8 | bus_LV_1404-1_0_2_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_1404-1_0_2_node_133 | 0.4 | n |  | TRUE
10 | bus_LV_1404-1_0_2_node_135 | 0.4 | n |  | TRUE
11 | bus_LV_1404-1_0_2_node_134 | 0.4 | n |  | TRUE
12 | bus_LV_1404-1_0_2_node_64 | 0.4 | n |  | TRUE
13 | bus_LV_1404-1_0_2_node_65 | 0.4 | n |  | TRUE
14 | bus_LV_1404-1_0_2_node_66 | 0.4 | n |  | TRUE
15 | bus_LV_1404-1_0_2_node_67 | 0.4 | n |  | TRUE
16 | bus_LV_1404-1_0_2_node_68 | 0.4 | n |  | TRUE
17 | bus_LV_1404-1_0_2_node_69 | 0.4 | n |  | TRUE
18 | bus_LV_1404-1_0_2_node_70 | 0.4 | n |  | TRUE
19 | bus_LV_1404-1_0_2_node_85 | 0.4 | n |  | TRUE
20 | bus_LV_1404-1_0_2_node_275 | 0.4 | n |  | TRUE
21 | bus_LV_1404-1_0_2_node_71 | 0.4 | n |  | TRUE
22 | bus_LV_1404-1_0_2_node_74 | 0.4 | n |  | TRUE
23 | bus_LV_1404-1_0_2_node_73 | 0.4 | n |  | TRUE
24 | bus_LV_1404-1_0_2_node_77 | 0.4 | n |  | TRUE
25 | bus_LV_1404-1_0_2_node_75 | 0.4 | n |  | TRUE
26 | bus_LV_1404-1_0_2_node_76 | 0.4 | n |  | TRUE
27 | bus_LV_1404-1_0_2_node_78 | 0.4 | n |  | TRUE
28 | bus_LV_1404-1_0_2_node_79 | 0.4 | n |  | TRUE
29 | bus_LV_1404-1_0_2_node_80 | 0.4 | n |  | TRUE
30 | bus_LV_1404-1_0_2_node_81 | 0.4 | n |  | TRUE
31 | bus_LV_1404-1_0_2_node_83 | 0.4 | n |  | TRUE
32 | bus_LV_1404-1_0_2_node_84 | 0.4 | n |  | TRUE
33 | bus_LV_1404-1_0_2_node_95 | 0.4 | n |  | TRUE
34 | bus_LV_1404-1_0_2_node_91 | 0.4 | n |  | TRUE
35 | bus_LV_1404-1_0_2_node_82 | 0.4 | n |  | TRUE
36 | bus_LV_1404-1_0_2_node_109 | 0.4 | n |  | TRUE
37 | bus_LV_1404-1_0_2_node_86 | 0.4 | n |  | TRUE
38 | bus_LV_1404-1_0_2_node_94 | 0.4 | n |  | TRUE
39 | bus_LV_1404-1_0_2_node_87 | 0.4 | n |  | TRUE
40 | bus_LV_1404-1_0_2_node_88 | 0.4 | n |  | TRUE
41 | bus_LV_1404-1_0_2_node_89 | 0.4 | n |  | TRUE
42 | bus_LV_1404-1_0_2_node_90 | 0.4 | n |  | TRUE
43 | bus_LV_1404-1_0_2_node_92 | 0.4 | n |  | TRUE
44 | bus_LV_1404-1_0_2_node_93 | 0.4 | n |  | TRUE
45 | bus_LV_1404-1_0_2_node_282 | 0.4 | n |  | TRUE
46 | bus_LV_1404-1_0_2_node_100 | 0.4 | n |  | TRUE
47 | bus_LV_1404-1_0_2_node_96 | 0.4 | n |  | TRUE
48 | bus_LV_1404-1_0_2_node_97 | 0.4 | n |  | TRUE
49 | bus_LV_1404-1_0_2_node_98 | 0.4 | n |  | TRUE
50 | bus_LV_1404-1_0_2_node_99 | 0.4 | n |  | TRUE
51 | bus_LV_1404-1_0_2_node_267 | 0.4 | n |  | TRUE
52 | bus_LV_1404-1_0_2_node_104 | 0.4 | n |  | TRUE
53 | bus_LV_1404-1_0_2_node_103 | 0.4 | n |  | TRUE
54 | bus_LV_1404-1_0_2_node_101 | 0.4 | n |  | TRUE
55 | bus_LV_1404-1_0_2_node_102 | 0.4 | n |  | TRUE
56 | bus_LV_1404-1_0_2_node_108 | 0.4 | n |  | TRUE
57 | bus_LV_1404-1_0_2_node_119 | 0.4 | n |  | TRUE
58 | bus_LV_1404-1_0_2_node_105 | 0.4 | n |  | TRUE
59 | bus_LV_1404-1_0_2_node_106 | 0.4 | n |  | TRUE
60 | bus_LV_1404-1_0_2_node_107 | 0.4 | n |  | TRUE
61 | bus_LV_1404-1_0_2_node_110 | 0.4 | n |  | TRUE
62 | bus_LV_1404-1_0_2_node_111 | 0.4 | n |  | TRUE
63 | bus_LV_1404-1_0_2_node_113 | 0.4 | n |  | TRUE
64 | bus_LV_1404-1_0_2_node_112 | 0.4 | n |  | TRUE
65 | bus_LV_1404-1_0_2_node_114 | 0.4 | n |  | TRUE
66 | bus_LV_1404-1_0_2_node_115 | 0.4 | n |  | TRUE
67 | bus_LV_1404-1_0_2_node_116 | 0.4 | n |  | TRUE
68 | bus_LV_1404-1_0_2_node_117 | 0.4 | n |  | TRUE
69 | bus_LV_1404-1_0_2_node_118 | 0.4 | n |  | TRUE
70 | bus_LV_1404-1_0_2_node_120 | 0.4 | n |  | TRUE
71 | bus_LV_1404-1_0_2_node_121 | 0.4 | n |  | TRUE
72 | bus_LV_1404-1_0_2_node_122 | 0.4 | n |  | TRUE
73 | bus_LV_1404-1_0_2_node_123 | 0.4 | n |  | TRUE
74 | bus_LV_1404-1_0_2_node_124 | 0.4 | n |  | TRUE
75 | bus_LV_1404-1_0_2_node_284 | 0.4 | n |  | TRUE
76 | bus_LV_1404-1_0_2_node_127 | 0.4 | n |  | TRUE
77 | bus_LV_1404-1_0_2_node_130 | 0.4 | n |  | TRUE
78 | bus_LV_1404-1_0_2_node_128 | 0.4 | n |  | TRUE
79 | bus_LV_1404-1_0_2_node_129 | 0.4 | n |  | TRUE
80 | bus_LV_1404-1_0_2_node_131 | 0.4 | n |  | TRUE
81 | bus_LV_1404-1_0_2_node_132 | 0.4 | n |  | TRUE
82 | bus_LV_1404-1_0_2_node_281 | 0.4 | n |  | TRUE
83 | bus_LV_1404-1_0_2_node_144 | 0.4 | n |  | TRUE
84 | bus_LV_1404-1_0_2_node_146 | 0.4 | n |  | TRUE
85 | bus_LV_1404-1_0_2_node_136 | 0.4 | n |  | TRUE
86 | bus_LV_1404-1_0_2_node_137 | 0.4 | n |  | TRUE
87 | bus_LV_1404-1_0_2_node_138 | 0.4 | n |  | TRUE
88 | bus_LV_1404-1_0_2_node_139 | 0.4 | n |  | TRUE
89 | bus_LV_1404-1_0_2_node_140 | 0.4 | n |  | TRUE
90 | bus_LV_1404-1_0_2_node_141 | 0.4 | n |  | TRUE
91 | bus_LV_1404-1_0_2_node_145 | 0.4 | n |  | TRUE
92 | bus_LV_1404-1_0_2_node_142 | 0.4 | n |  | TRUE
93 | bus_LV_1404-1_0_2_node_143 | 0.4 | n |  | TRUE
94 | bus_LV_1404-1_0_2_node_147 | 0.4 | n |  | TRUE
95 | bus_LV_1404-1_0_2_node_248 | 0.4 | n |  | TRUE
96 | bus_LV_1404-1_0_2_node_249 | 0.4 | n |  | TRUE
97 | bus_LV_1404-1_0_2_node_250 | 0.4 | n |  | TRUE
98 | bus_LV_1404-1_0_2_node_251 | 0.4 | n |  | TRUE
99 | bus_LV_1404-1_0_2_node_261 | 0.4 | n |  | TRUE
100 | bus_LV_1404-1_0_2_node_279 | 0.4 | n |  | TRUE
101 | bus_LV_1404-1_0_2_node_260 | 0.4 | n |  | TRUE
102 | bus_LV_1404-1_0_2_node_262 | 0.4 | n |  | TRUE
103 | bus_LV_1404-1_0_2_node_280 | 0.4 | n |  | TRUE
104 | bus_LV_1404-1_0_2_node_283 | 0.4 | n |  | TRUE
105 | bus_MV_0_node_112 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1404-1_0_2_load_0 | 0 | 0.0002227 | 5.5813e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1404-1_0_2_load_1 | 1 | 0.00017922 | 4.4917e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1404-1_0_2_load_4 | 3 | 7.2851e-05 | 1.8258e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1404-1_0_2_load_126 | 6 | 6.6704e-05 | 1.6717e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1404-1_0_2_load_125 | 7 | 0.00017752 | 4.4492e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1404-1_0_2_load_133 | 9 | 8.7448e-05 | 2.1917e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1404-1_0_2_load_134 | 11 | 0.00014273 | 3.5771e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1404-1_0_2_load_64 | 12 | 0.00047179 | 0.00011824 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1404-1_0_2_load_65 | 13 | 0.00019895 | 4.9862e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1404-1_0_2_load_67 | 15 | 0.00041962 | 0.00010517 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1404-1_0_2_load_68 | 16 | 0.00014547 | 3.6459e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1404-1_0_2_load_69 | 17 | 0.00016494 | 4.1337e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1404-1_0_2_load_70 | 18 | 0.00054797 | 0.00013733 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1404-1_0_2_load_275 | 20 | 0.00016289 | 4.0825e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1404-1_0_2_load_71 | 21 | 0.00024263 | 6.0808e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1404-1_0_2_load_74 | 22 | 0.0001805 | 4.5237e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1404-1_0_2_load_77 | 24 | 0.00011186 | 2.8036e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1404-1_0_2_load_75 | 25 | 0.00037833 | 9.4819e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1404-1_0_2_load_76 | 26 | 0.00027884 | 6.9883e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1404-1_0_2_load_78 | 27 | 0.00021898 | 5.4881e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1404-1_0_2_load_91 | 34 | 0.00015199 | 3.8093e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1404-1_0_2_load_82 | 35 | 0.0019899 | 0.00049872 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1404-1_0_2_load_109 | 36 | 0.00064722 | 0.00016221 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1404-1_0_2_load_86 | 37 | 9.5427e-05 | 2.3916e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1404-1_0_2_load_94 | 38 | 0.00058478 | 0.00014656 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1404-1_0_2_load_87 | 39 | 0.0001044 | 2.6164e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1404-1_0_2_load_88 | 40 | 0.00041259 | 0.00010341 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1404-1_0_2_load_89 | 41 | 0.00066436 | 0.0001665 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1404-1_0_2_load_90 | 42 | 0.00030096 | 7.5429e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1404-1_0_2_load_92 | 43 | 0.00027316 | 6.846e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1404-1_0_2_load_93 | 44 | 0.00010944 | 2.7428e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1404-1_0_2_load_282 | 45 | 0.00076626 | 0.00019204 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1404-1_0_2_load_96 | 47 | 0.00038172 | 9.5667e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1404-1_0_2_load_97 | 48 | 0.00071149 | 0.00017832 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1404-1_0_2_load_99 | 50 | 0.00027033 | 6.775e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1404-1_0_2_load_267 | 51 | 0.00030086 | 7.5403e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1404-1_0_2_load_103 | 53 | 0.00043583 | 0.00010923 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1404-1_0_2_load_101 | 54 | 0.00080294 | 0.00020123 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1404-1_0_2_load_102 | 55 | 0.00047325 | 0.00011861 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1404-1_0_2_load_119 | 57 | 0.0019178 | 0.00048065 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1404-1_0_2_load_105 | 58 | 0.0014609 | 0.00036613 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1404-1_0_2_load_106 | 59 | 0.00054417 | 0.00013638 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1404-1_0_2_load_110 | 61 | 0.00029072 | 7.286e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1404-1_0_2_load_113 | 63 | 0.0023643 | 0.00059255 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1404-1_0_2_load_112 | 64 | 0.0010466 | 0.0002623 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1404-1_0_2_load_115 | 66 | 0.0059079 | 0.0014807 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1404-1_0_2_load_116 | 67 | 0.00024637 | 6.1745e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1404-1_0_2_load_117 | 68 | 0.0013521 | 0.00033886 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1404-1_0_2_load_120 | 70 | 7.1724e-05 | 1.7976e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1404-1_0_2_load_121 | 71 | 0.0001343 | 3.3658e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1404-1_0_2_load_123 | 73 | 0.00034652 | 8.6845e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1404-1_0_2_load_127 | 76 | 0.00043266 | 0.00010844 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1404-1_0_2_load_128 | 78 | 0.00014976 | 3.7534e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1404-1_0_2_load_129 | 79 | 0.00022372 | 5.6068e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1404-1_0_2_load_131 | 80 | 0.00043048 | 0.00010789 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1404-1_0_2_load_132 | 81 | 0.00024941 | 6.2509e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1404-1_0_2_load_281 | 82 | 0.00043152 | 0.00010815 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1404-1_0_2_load_144 | 83 | 0.00026162 | 6.5569e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1404-1_0_2_load_146 | 84 | 0.0002174 | 5.4485e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1404-1_0_2_load_136 | 85 | 0.0002878 | 7.2131e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1404-1_0_2_load_137 | 86 | 0.0002484 | 6.2255e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1404-1_0_2_load_138 | 87 | 0.00022949 | 5.7516e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1404-1_0_2_load_139 | 88 | 0.00025566 | 6.4074e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1404-1_0_2_load_140 | 89 | 0.00017293 | 4.3341e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1404-1_0_2_load_145 | 91 | 0.00037266 | 9.3396e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1404-1_0_2_load_142 | 92 | 0.00052181 | 0.00013078 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1404-1_0_2_load_143 | 93 | 0.00034692 | 8.6945e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1404-1_0_2_load_147 | 94 | 0.00021099 | 5.2878e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1404-1_0_2_load_248 | 95 | 0.00020029 | 5.0197e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1404-1_0_2_load_249 | 96 | 8.6849e-05 | 2.1766e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1404-1_0_2_load_250 | 97 | 0.00030428 | 7.6259e-05 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1404-1_0_2_load_251 | 98 | 0.00014235 | 3.5676e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1404-1_0_2_load_261 | 99 | 0.00018132 | 4.5444e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1404-1_0_2_load_260 | 101 | 0.00020466 | 5.1292e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1404-1_0_2_load_262 | 102 | 0.00015169 | 3.8017e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1404-1_0_2_load_280 | 103 | 0.00018704 | 4.6876e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1404-1_0_2_load_283 | 104 | 0.00043571 | 0.0001092 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 64 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1404-1_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.035302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1404-1_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.018642 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1404-1_0_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.064514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1404-1_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.05366 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1404-1_0_2_line_4 | NAYY 4x150 SE | 4 | 8 | 0.032532 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1404-1_0_2_line_5 | NAYY 4x150 SE | 4 | 9 | 0.13896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1404-1_0_2_line_6 | NAYY 4x150 SE | 4 | 5 | 0.039961 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1404-1_0_2_line_7 | NAYY 4x150 SE | 5 | 6 | 0.0051366 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1404-1_0_2_line_8 | NAYY 4x150 SE | 5 | 7 | 0.12724 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1404-1_0_2_line_9 | NAYY 4x150 SE | 6 | 77 | 0.030614 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1404-1_0_2_line_10 | NAYY 4x150 SE | 7 | 74 | 0.011194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1404-1_0_2_line_11 | NAYY 4x150 SE | 8 | 10 | 0.00611 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1404-1_0_2_line_12 | NAYY 4x150 SE | 8 | 11 | 0.1137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1404-1_0_2_line_13 | NAYY 4x150 SE | 9 | 70 | 0.010785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1404-1_0_2_line_14 | NAYY 4x150 SE | 10 | 83 | 0.009396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1404-1_0_2_line_15 | NAYY 4x150 SE | 10 | 84 | 0.023337 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1404-1_0_2_line_16 | NAYY 4x150 SE | 12 | 13 | 0.028894 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1404-1_0_2_line_17 | NAYY 4x150 SE | 12 | 14 | 0.13287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1404-1_0_2_line_18 | NAYY 4x150 SE | 13 | 15 | 0.16253 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1404-1_0_2_line_19 | NAYY 4x150 SE | 14 | 16 | 0.088191 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1404-1_0_2_line_20 | NAYY 4x150 SE | 14 | 17 | 0.079959 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1404-1_0_2_line_21 | NAYY 4x150 SE | 15 | 18 | 0.013369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1404-1_0_2_line_22 | NAYY 4x150 SE | 16 | 19 | 0.073622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1404-1_0_2_line_23 | NAYY 4x150 SE | 17 | 20 | 0.038231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1404-1_0_2_line_24 | NAYY 4x150 SE | 19 | 37 | 0.17141 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1404-1_0_2_line_25 | NAYY 4x150 SE | 20 | 23 | 0.28055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1404-1_0_2_line_26 | NAYY 4x150 SE | 21 | 22 | 0.15379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1404-1_0_2_line_27 | NAYY 4x150 SE | 22 | 25 | 0.045853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1404-1_0_2_line_28 | NAYY 4x150 SE | 22 | 26 | 0.0021262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1404-1_0_2_line_29 | NAYY 4x150 SE | 23 | 24 | 0.26708 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1404-1_0_2_line_30 | NAYY 4x150 SE | 24 | 25 | 0.021008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1404-1_0_2_line_31 | NAYY 4x150 SE | 27 | 28 | 0.028328 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1404-1_0_2_line_32 | NAYY 4x150 SE | 27 | 29 | 0.019338 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1404-1_0_2_line_33 | NAYY 4x150 SE | 28 | 30 | 0.12686 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1404-1_0_2_line_34 | NAYY 4x150 SE | 29 | 31 | 0.015016 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1404-1_0_2_line_35 | NAYY 4x150 SE | 29 | 32 | 0.02357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
36 | LV_1404-1_0_2_line_36 | NAYY 4x150 SE | 30 | 33 | 0.007121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1404-1_0_2_line_37 | NAYY 4x150 SE | 30 | 34 | 0.10642 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1404-1_0_2_line_38 | NAYY 4x150 SE | 31 | 35 | 0.0048027 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1404-1_0_2_line_39 | NAYY 4x150 SE | 32 | 36 | 0.0069678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
40 | LV_1404-1_0_2_line_40 | NAYY 4x150 SE | 33 | 45 | 0.069594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1404-1_0_2_line_41 | NAYY 4x150 SE | 33 | 46 | 0.21835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1404-1_0_2_line_42 | NAYY 4x150 SE | 34 | 41 | 0.0054121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1404-1_0_2_line_43 | NAYY 4x150 SE | 36 | 61 | 0.13056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
44 | LV_1404-1_0_2_line_44 | NAYY 4x150 SE | 37 | 38 | 0.018068 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1404-1_0_2_line_45 | NAYY 4x150 SE | 38 | 44 | 0.021699 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1404-1_0_2_line_46 | NAYY 4x150 SE | 39 | 40 | 0.030048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1404-1_0_2_line_47 | NAYY 4x150 SE | 39 | 41 | 0.072909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1404-1_0_2_line_48 | NAYY 4x150 SE | 40 | 42 | 0.017922 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1404-1_0_2_line_49 | NAYY 4x150 SE | 42 | 43 | 0.015902 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1404-1_0_2_line_50 | NAYY 4x150 SE | 43 | 44 | 0.00061477 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1404-1_0_2_line_51 | NAYY 4x150 SE | 46 | 52 | 0.12531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1404-1_0_2_line_52 | NAYY 4x150 SE | 46 | 53 | 0.12095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1404-1_0_2_line_53 | NAYY 4x150 SE | 46 | 49 | 0.26312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1404-1_0_2_line_54 | NAYY 4x150 SE | 47 | 48 | 0.034219 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1404-1_0_2_line_55 | NAYY 4x150 SE | 47 | 49 | 0.014873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1404-1_0_2_line_56 | NAYY 4x150 SE | 49 | 50 | 0.20249 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1404-1_0_2_line_57 | NAYY 4x150 SE | 50 | 51 | 0.068979 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1404-1_0_2_line_58 | NAYY 4x150 SE | 52 | 56 | 0.043168 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1404-1_0_2_line_59 | NAYY 4x150 SE | 52 | 57 | 0.26972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1404-1_0_2_line_60 | NAYY 4x150 SE | 53 | 55 | 0.027539 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1404-1_0_2_line_61 | NAYY 4x150 SE | 54 | 55 | 0.0052104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1404-1_0_2_line_62 | NAYY 4x150 SE | 56 | 60 | 0.061565 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1404-1_0_2_line_63 | NAYY 4x150 SE | 57 | 69 | 0.010377 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1404-1_0_2_line_64 | NAYY 4x150 SE | 58 | 59 | 0.023129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1404-1_0_2_line_65 | NAYY 4x150 SE | 59 | 60 | 0.013027 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1404-1_0_2_line_66 | NAYY 4x150 SE | 61 | 62 | 0.014417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
67 | LV_1404-1_0_2_line_67 | NAYY 4x150 SE | 62 | 63 | 0.0084863 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1404-1_0_2_line_68 | NAYY 4x150 SE | 62 | 64 | 0.052303 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
69 | LV_1404-1_0_2_line_69 | NAYY 4x150 SE | 63 | 65 | 0.027631 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1404-1_0_2_line_70 | NAYY 4x150 SE | 65 | 66 | 0.045784 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1404-1_0_2_line_71 | NAYY 4x150 SE | 65 | 67 | 0.20823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1404-1_0_2_line_72 | NAYY 4x150 SE | 68 | 69 | 0.010774 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1404-1_0_2_line_73 | NAYY 4x150 SE | 69 | 70 | 0.14787 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1404-1_0_2_line_74 | NAYY 4x150 SE | 71 | 72 | 0.081326 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1404-1_0_2_line_75 | NAYY 4x150 SE | 71 | 73 | 0.040325 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1404-1_0_2_line_76 | NAYY 4x150 SE | 72 | 74 | 0.089605 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1404-1_0_2_line_77 | NAYY 4x150 SE | 73 | 75 | 0.33584 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1404-1_0_2_line_78 | NAYY 4x150 SE | 74 | 76 | 0.031441 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1404-1_0_2_line_79 | NAYY 4x150 SE | 75 | 104 | 0.006185 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1404-1_0_2_line_80 | NAYY 4x150 SE | 77 | 81 | 0.012423 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1404-1_0_2_line_81 | NAYY 4x150 SE | 77 | 78 | 0.027834 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1404-1_0_2_line_82 | NAYY 4x150 SE | 78 | 79 | 0.14617 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1404-1_0_2_line_83 | NAYY 4x150 SE | 79 | 80 | 0.010414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1404-1_0_2_line_84 | NAYY 4x150 SE | 80 | 82 | 0.11448 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1404-1_0_2_line_85 | NAYY 4x150 SE | 82 | 100 | 0.084645 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1404-1_0_2_line_86 | NAYY 4x150 SE | 83 | 93 | 0.010083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1404-1_0_2_line_87 | NAYY 4x150 SE | 85 | 86 | 0.036067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1404-1_0_2_line_88 | NAYY 4x150 SE | 85 | 87 | 0.24942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1404-1_0_2_line_89 | NAYY 4x150 SE | 86 | 88 | 0.021129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1404-1_0_2_line_90 | NAYY 4x150 SE | 87 | 89 | 0.21716 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1404-1_0_2_line_91 | NAYY 4x150 SE | 88 | 90 | 0.027243 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1404-1_0_2_line_92 | NAYY 4x150 SE | 90 | 91 | 0.022514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1404-1_0_2_line_93 | NAYY 4x150 SE | 90 | 92 | 0.010137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1404-1_0_2_line_94 | NAYY 4x150 SE | 91 | 94 | 0.023167 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1404-1_0_2_line_95 | NAYY 4x150 SE | 92 | 93 | 0.005201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1404-1_0_2_line_96 | NAYY 4x150 SE | 95 | 96 | 0.006651 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1404-1_0_2_line_97 | NAYY 4x150 SE | 95 | 97 | 0.0088271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1404-1_0_2_line_98 | NAYY 4x150 SE | 96 | 98 | 0.0072068 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1404-1_0_2_line_99 | NAYY 4x150 SE | 98 | 99 | 0.16442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1404-1_0_2_line_100 | NAYY 4x150 SE | 98 | 100 | 0.34526 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1404-1_0_2_line_101 | NAYY 4x150 SE | 99 | 102 | 0.025318 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1404-1_0_2_line_102 | NAYY 4x150 SE | 99 | 101 | 0.059056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1404-1_0_2_line_103 | NAYY 4x150 SE | 100 | 103 | 0.029092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1404-1_0_2_trafo_112 | 0.25 MVA 20/0.4 kV | 105 | 64 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20
0 | 2665040.2429 | 1194439.5268 | 2665035.7579 | 1194440.0151 | 2665024.0187 | 1194448.0478 | 2665018.1935 | 1194460.9476 | 2665016.2632 | 1194462.3947
1 | 2665058.7054 | 1194437.0406 | 2665052.7491 | 1194438.1654 | 2665040.2429 | 1194439.5268
2 | 2665058.7054 | 1194437.0406 | 2665056.5856 | 1194464.4781 | 2665066.1754 | 1194500.2079
3 | 2665058.7054 | 1194437.0406 | 2665064.3884 | 1194414.8004 | 2665064.8842 | 1194407.7572 | 2665077.8184 | 1194387.964
4 | 2665055.465 | 1194364.3294 | 2665059.5693 | 1194368.8322 | 2665077.8184 | 1194387.964
5 | 2665077.8184 | 1194387.964 | 2665089.327 | 1194369.6229 | 2665088.9904 | 1194357.8457 | 2665090.4072 | 1194343.8973 | 2665100.4255 | 1194325.262 | 2665113.2437 | 1194311.9492 | 2665123.3353 | 1194299.196 | 2665127.9783 | 1194263.8954
6 | 2665077.8184 | 1194387.964 | 2665081.9238 | 1194393.7565 | 2665089.12 | 1194401.2503 | 2665090.9038 | 1194401.203 | 2665096.433 | 1194400.8074 | 2665111.5409 | 1194399.76
7 | 2665111.5409 | 1194399.76 | 2665116.2136 | 1194401.8933
8 | 2665111.5409 | 1194399.76 | 2665117.3758 | 1194382.4911 | 2665128.2804 | 1194357.3506 | 2665137.3916 | 1194346.4434 | 2665146.8166 | 1194344.5115 | 2665167.2175 | 1194347.9912 | 2665185.2034 | 1194348.5986 | 2665204.161 | 1194346.4228
9 | 2665140.0546 | 1194419.6042 | 2665136.2644 | 1194412.859 | 2665122.0433 | 1194404.5549 | 2665116.2136 | 1194401.8933
10 | 2665215.2818 | 1194345.1465 | 2665204.161 | 1194346.4228
11 | 2665049.5933 | 1194366.0777 | 2665055.465 | 1194364.3294
12 | 2665055.465 | 1194364.3294 | 2665054.7793 | 1194357.3067 | 2665057.3922 | 1194334.9775 | 2665059.8701 | 1194314.5592 | 2665059.8196 | 1194302.3848 | 2665057.9129 | 1194289.2119 | 2665051.3662 | 1194260.5239 | 2665051.0036 | 1194252.5264 | 2665051.0706 | 1194251.8546
13 | 2665127.9783 | 1194263.8954 | 2665129.3847 | 1194253.2021
14 | 2665049.5933 | 1194366.0777 | 2665042.8084 | 1194367.7049 | 2665040.407 | 1194367.994
15 | 2665049.5933 | 1194366.0777 | 2665048.1017 | 1194364.4827 | 2665038.898 | 1194357.2896 | 2665033.2391 | 1194349.6935
16 | 2665263.8087 | 1193321.8207 | 2665265.2497 | 1193322.6809 | 2665280.1698 | 1193331.4154 | 2665288.3865 | 1193336.986 | 2665288.3865 | 1193336.986
17 | 2665149.5632 | 1193254.047 | 2665216.4686 | 1193295.4332 | 2665257.9269 | 1193318.3096 | 2665263.8087 | 1193321.8207
18 | 2665288.3865 | 1193336.986 | 2665314.237 | 1193366.6076 | 2665335.2072 | 1193392.9297 | 2665359.591 | 1193443.7368 | 2665368.1809 | 1193475.809
19 | 2665149.5632 | 1193254.047 | 2665143.3625 | 1193250.2106 | 2665070.9193 | 1193214.2004
20 | 2665149.5632 | 1193254.047 | 2665159.3945 | 1193252.064 | 2665171.6827 | 1193244.9381 | 2665187.2991 | 1193233.1679 | 2665203.4472 | 1193214.5885 | 2665207.2437 | 1193204.0348 | 2665207.3636 | 1193203.7186
21 | 2665366.4586 | 1193489.0494 | 2665368.2395 | 1193476.0279 | 2665368.1809 | 1193475.809
22 | 2665003.3517 | 1193185.0059 | 2665061.638 | 1193209.5869 | 2665070.9193 | 1193214.2004
23 | 2665230.2967 | 1193210.701 | 2665225.2724 | 1193198.2389 | 2665220.3861 | 1193194.0833 | 2665215.0982 | 1193193.9144 | 2665211.088 | 1193196.0942 | 2665208.931 | 1193199.5839 | 2665207.3636 | 1193203.7186
24 | 2665003.3517 | 1193185.0059 | 2665010.8106 | 1193268.7692 | 2665014.3057 | 1193290.1197 | 2665021.2761 | 1193311.5079 | 2665037.2509 | 1193345.946 | 2665040.2699 | 1193350.2098
25 | 2665230.2967 | 1193210.701 | 2665499.3309 | 1193131.1368
26 | 2665687.0845 | 1193401.9355 | 2665825.7257 | 1193335.3821
27 | 2665687.0845 | 1193401.9355 | 2665685.4734 | 1193397.7774 | 2665680.1808 | 1193395.2734 | 2665670.7944 | 1193393.536 | 2665665.1516 | 1193386.1364 | 2665659.107 | 1193370.583
28 | 2665687.8526 | 1193403.9182 | 2665687.0845 | 1193401.9355
29 | 2665647.0159 | 1193353.6711 | 2665499.3309 | 1193131.1368
30 | 2665659.107 | 1193370.583 | 2665657.1978 | 1193365.6705 | 2665647.0159 | 1193353.6711
31 | 2665123.7431 | 1193737.4712 | 2665135.4958 | 1193748.639 | 2665143.0003 | 1193758.1503
32 | 2665153.5698 | 1193774.2063 | 2665150.3959 | 1193767.5234 | 2665143.0003 | 1193758.1503
33 | 2665066.137 | 1193631.2381 | 2665068.7076 | 1193631.7441 | 2665074.456 | 1193633.6966 | 2665080.2307 | 1193636.0274 | 2665085.3566 | 1193639.1405 | 2665088.7835 | 1193643.6026 | 2665091.3105 | 1193650.9233 | 2665097.3697 | 1193671.9237 | 2665109.0279 | 1193704.3918 | 2665117.1716 | 1193725.7373 | 2665123.7431 | 1193737.4712
34 | 2665139.1855 | 1193778.6523 | 2665153.5698 | 1193774.2063
35 | 2665160.6966 | 1193796.5303 | 2665157.5781 | 1193782.6549 | 2665153.5698 | 1193774.2063
36 | 2665066.137 | 1193631.2381 | 2665063.7547 | 1193637.9494
37 | 2665066.137 | 1193631.2381 | 2665072.1346 | 1193599.0733 | 2665072.1643 | 1193557.1046 | 2665071.9145 | 1193525.3778
38 | 2665139.1855 | 1193778.6523 | 2665137.4992 | 1193774.1554
39 | 2665160.6966 | 1193796.5303 | 2665165.7797 | 1193801.296
40 | 2665063.7547 | 1193637.9494 | 2665040.3792 | 1193634.4489 | 2665014.7389 | 1193626.8436 | 2664996.6972 | 1193633.974
41 | 2665031.8246 | 1193827.5134 | 2665024.006 | 1193808.4951 | 2665001.342 | 1193761.3213 | 2664997.2588 | 1193751.3266 | 2664996.6024 | 1193745.8051 | 2664997.94 | 1193737.7372 | 2665000.3824 | 1193731.8047 | 2665044.7279 | 1193681.0011 | 2665063.7547 | 1193637.9494
42 | 2665071.8719 | 1193519.9659 | 2665071.9145 | 1193525.3778
43 | 2665165.7797 | 1193801.296 | 2665170.7984 | 1193806.0014 | 2665211.2931 | 1193836.5604 | 2665240.715 | 1193871.8795 | 2665258.3104 | 1193892.3319
44 | 2665050.711 | 1193364.9557 | 2665040.2699 | 1193350.2098
45 | 2665050.711 | 1193364.9557 | 2665054.5688 | 1193370.4041 | 2665061.0367 | 1193383.964
46 | 2665070.6596 | 1193447.0739 | 2665069.545 | 1193417.0464
47 | 2665070.6596 | 1193447.0739 | 2665071.4699 | 1193468.901 | 2665071.8719 | 1193519.9659
48 | 2665066.4918 | 1193399.4392 | 2665069.3832 | 1193412.6899 | 2665069.545 | 1193417.0464
49 | 2665066.4918 | 1193399.4392 | 2665064.8675 | 1193391.9953 | 2665061.3014 | 1193384.5189
50 | 2665061.3014 | 1193384.5189 | 2665061.0367 | 1193383.964
51 | 2665000.7448 | 1193947.4238 | 2665008.9783 | 1193911.4254 | 2665018.2218 | 1193872.9589 | 2665029.7229 | 1193848.3805 | 2665033.0191 | 1193840.3228 | 2665033.3485 | 1193834.5563 | 2665031.8246 | 1193827.5134
52 | 2665031.8246 | 1193827.5134 | 2665028.6585 | 1193829.2133 | 2665025.0204 | 1193834.3657 | 2665014.4716 | 1193845.6688 | 2664997.884 | 1193857.918 | 2664990.574 | 1193862.9305 | 2664971.8962 | 1193869.7539 | 2664940.5234 | 1193879.1967 | 2664928.3727 | 1193884.9687
53 | 2664908.0511 | 1193725.1987 | 2664910.6857 | 1193718.4011 | 2664918.3658 | 1193688.4224 | 2664920.9873 | 1193682.1361 | 2664925.5476 | 1193676.271 | 2664930.089 | 1193672.8627 | 2664934.7009 | 1193671.3785 | 2664938.583 | 1193671.832 | 2664947.4421 | 1193674.3741 | 2664969.0113 | 1193684.1806 | 2664978.954 | 1193690.8147 | 2664988.6456 | 1193701.6151 | 2664994.082 | 1193709.8234 | 2664998.3677 | 1193729.2368 | 2665000.3824 | 1193731.8047 | 2664997.94 | 1193737.7372 | 2664996.6024 | 1193745.8051 | 2664997.2588 | 1193751.3266 | 2665001.342 | 1193761.3213 | 2665024.006 | 1193808.4951 | 2665031.8246 | 1193827.5134
54 | 2664912.9082 | 1193739.256 | 2664915.5661 | 1193746.9485 | 2664913.424 | 1193754.7187 | 2664911.4364 | 1193767.2156 | 2664912.6353 | 1193772.4466
55 | 2664908.0511 | 1193725.1987 | 2664912.9082 | 1193739.256
56 | 2664908.0511 | 1193725.1987 | 2664901.4972 | 1193726.5507 | 2664893.911 | 1193728.9143 | 2664882.3019 | 1193733.9802 | 2664876.1551 | 1193735.0365 | 2664846.1479 | 1193731.6537 | 2664827.4493 | 1193730.5394 | 2664812.4081 | 1193732.3109 | 2664799.176 | 1193736.6479 | 2664762.7575 | 1193748.8942 | 2664743.0463 | 1193756.83 | 2664725.1629 | 1193766.3088 | 2664718.5629 | 1193771.2292 | 2664716.9754 | 1193773.5488
57 | 2664682.2178 | 1193833.1058 | 2664712.7472 | 1193779.7269 | 2664716.9754 | 1193773.5488
58 | 2665000.7448 | 1193947.4238 | 2664997.1406 | 1193959.2916 | 2664995.8859 | 1193967.4494 | 2664996.0703 | 1193975.7229 | 2664997.6085 | 1193989.8701
59 | 2665000.7448 | 1193947.4238 | 2665008.7361 | 1193949.8342 | 2665014.4715 | 1193951.5531 | 2665018.1025 | 1193952.6487 | 2665030.1848 | 1193970.6238 | 2665055.4722 | 1193999.3266 | 2665094.3435 | 1194026.3206 | 2665149.2321 | 1194073.0786 | 2665176.9671 | 1194107.1673 | 2665181.7302 | 1194125.352 | 2665188.7768 | 1194131.733
60 | 2664904.6069 | 1193898.783 | 2664919.7703 | 1193889.0551 | 2664928.3727 | 1193884.9687
61 | 2664900.2214 | 1193901.5965 | 2664904.6069 | 1193898.783
62 | 2664997.6085 | 1193989.8701 | 2664988.9218 | 1193993.2444 | 2664983.5126 | 1193998.6889 | 2664973.8098 | 1194014.226 | 2664968.1385 | 1194026.9607 | 2664965.8726 | 1194039.1099
63 | 2665196.4686 | 1194138.6982 | 2665188.7768 | 1194131.733
64 | 2664980.8664 | 1194071.6809 | 2664978.475 | 1194068.8419 | 2664973.4802 | 1194060.7052 | 2664970.1649 | 1194051.409
65 | 2664965.8726 | 1194039.1099 | 2664969.1536 | 1194048.5733 | 2664970.1649 | 1194051.409
66 | 2665268.3241 | 1193902.1872 | 2665266.5137 | 1193901.8672 | 2665258.3104 | 1193892.3319
67 | 2665268.3241 | 1193902.1872 | 2665273.8464 | 1193903.1702 | 2665276.3643 | 1193901.778
68 | 2665268.3241 | 1193902.1872 | 2665262.2976 | 1193918.7756 | 2665262.7493 | 1193933.2557 | 2665259.7317 | 1193947.8869 | 2665256.2394 | 1193951.7773
69 | 2665300.5449 | 1193888.4083 | 2665276.3643 | 1193901.778
70 | 2665300.5449 | 1193888.4083 | 2665309.8355 | 1193897.4595 | 2665326.4396 | 1193910.2593 | 2665338.0423 | 1193912.6587
71 | 2665300.5449 | 1193888.4083 | 2665302.4201 | 1193875.8103 | 2665304.2786 | 1193855.6632 | 2665310.9082 | 1193847.3752 | 2665319.9471 | 1193843.1936 | 2665333.0892 | 1193838.0451 | 2665340.9145 | 1193832.6274 | 2665347.3908 | 1193820.2464 | 2665377.7249 | 1193753.2161 | 2665397.3609 | 1193714.392
72 | 2665196.4686 | 1194138.6982 | 2665202.3836 | 1194138.5959 | 2665207.0985 | 1194137.4243
73 | 2665196.4686 | 1194138.6982 | 2665193.9531 | 1194145.7416 | 2665179.9341 | 1194156.5952 | 2665151.2277 | 1194164.8319 | 2665142.5289 | 1194174.932 | 2665136.2637 | 1194200.9013 | 2665129.3847 | 1194253.2021
74 | 2665303.2981 | 1194328.6744 | 2665301.2845 | 1194307.1954 | 2665295.5136 | 1194274.5688 | 2665296.1605 | 1194253.0077 | 2665297.3116 | 1194248.0915
75 | 2665300.3219 | 1194208.2935 | 2665301.8327 | 1194219.2942 | 2665300.437 | 1194234.7436 | 2665297.3116 | 1194248.0915
76 | 2665303.2981 | 1194328.6744 | 2665294.1216 | 1194332.2653 | 2665259.6978 | 1194340.0388 | 2665215.2818 | 1194345.1465
77 | 2665300.3219 | 1194208.2935 | 2665620.5865 | 1194107.204
78 | 2665234.8114 | 1194369.8182 | 2665225.9467 | 1194358.1036 | 2665215.2818 | 1194345.1465
79 | 2665624.8122 | 1194111.7307 | 2665620.5865 | 1194107.204
80 | 2665140.0546 | 1194419.6042 | 2665152.2577 | 1194421.9338
81 | 2665140.0546 | 1194419.6042 | 2665153.6928 | 1194443.8675
82 | 2665245.8242 | 1194551.4819 | 2665242.4167 | 1194537.4885 | 2665223.696 | 1194529.5464 | 2665212.7473 | 1194521.678 | 2665189.8241 | 1194486.7967 | 2665156.3143 | 1194448.5315 | 2665153.6928 | 1194443.8675
83 | 2665248.2881 | 1194561.6 | 2665245.8242 | 1194551.4819
84 | 2665248.2881 | 1194561.6 | 2665360.6316 | 1194583.6389
85 | 2665360.6316 | 1194583.6389 | 2665356.8846 | 1194589.7126 | 2665357.6376 | 1194595.4242 | 2665362.4199 | 1194606.8832 | 2665373.6371 | 1194627.7958 | 2665392.1759 | 1194651.6346 | 2665394.921 | 1194656.3451
86 | 2665040.407 | 1194367.994 | 2665030.3965 | 1194369.1991
87 | 2664960.7921 | 1194306.6771 | 2664960.8546 | 1194306.7567 | 2664984.0293 | 1194334.2603
88 | 2664960.7921 | 1194306.6771 | 2664948.5873 | 1194291.1255 | 2664943.1516 | 1194285.6967 | 2664936.2728 | 1194279.8297 | 2664908.5474 | 1194265.1759 | 2664901.6572 | 1194260.3428 | 2664879.2816 | 1194240.055 | 2664857.7588 | 1194217.7086 | 2664834.861 | 1194187.9097 | 2664827.2016 | 1194177.3983 | 2664822.9582 | 1194167.4243 | 2664820.9784 | 1194158.8312 | 2664819.1858 | 1194132.9744 | 2664818.0959 | 1194117.2535
89 | 2664984.0293 | 1194334.2603 | 2664997.644 | 1194350.4181
90 | 2664706.0535 | 1193938.8299 | 2664711.1299 | 1193946.129 | 2664733.4475 | 1193981.0908 | 2664752.1145 | 1194008.9868 | 2664759.5785 | 1194018.5732 | 2664768.4814 | 1194028.9979 | 2664784.2947 | 1194043.1217 | 2664805.0292 | 1194061.6348 | 2664810.3482 | 1194068.7188 | 2664814.9753 | 1194081.2763 | 2664816.3188 | 1194091.6191 | 2664818.0959 | 1194117.2535
91 | 2665015.1982 | 1194371.2514 | 2664997.644 | 1194350.4181
92 | 2665015.1982 | 1194371.2514 | 2664992.9292 | 1194374.5609
93 | 2665015.1982 | 1194371.2514 | 2665021.5494 | 1194370.2642 | 2665025.2327 | 1194369.8208
94 | 2664969.9702 | 1194377.572 | 2664975.3234 | 1194377.1773 | 2664992.9292 | 1194374.5609
95 | 2665025.2327 | 1194369.8208 | 2665030.3965 | 1194369.1991
96 | 2665743.4302 | 1194690.6108 | 2665741.5629 | 1194684.2273
97 | 2665745.9083 | 1194699.0829 | 2665743.4302 | 1194690.6108
98 | 2665741.5629 | 1194684.2273 | 2665739.5396 | 1194677.3103
99 | 2665739.5396 | 1194677.3103 | 2665838.3437 | 1194545.8938
100 | 2665394.921 | 1194656.3451 | 2665739.5396 | 1194677.3103
101 | 2665838.3437 | 1194545.8938 | 2665848.5293 | 1194549.023 | 2665863.1908 | 1194549.1844
102 | 2665794.8054 | 1194508.4575 | 2665809.5128 | 1194528.2149 | 2665826.5347 | 1194542.2659 | 2665838.3437 | 1194545.8938
103 | 2665394.921 | 1194656.3451 | 2665389.9689 | 1194656.2465 | 2665385.574 | 1194658.1551 | 2665383.2924 | 1194660.5316 | 2665381.5903 | 1194664.2708 | 2665381.2553 | 1194667.7247 | 2665382.2641 | 1194671.638 | 2665383.7268 | 1194675.8565

## bus_geodata
| x | y | coords
0 | 2665040.2429 | 1194439.5268
1 | 2665016.2632 | 1194462.3947
2 | 2665058.7054 | 1194437.0406
3 | 2665066.1754 | 1194500.2079
4 | 2665077.8184 | 1194387.964
5 | 2665111.5409 | 1194399.76
6 | 2665116.2136 | 1194401.8933
7 | 2665204.161 | 1194346.4228
8 | 2665055.465 | 1194364.3294
9 | 2665127.9783 | 1194263.8954
10 | 2665049.5933 | 1194366.0777
11 | 2665051.0706 | 1194251.8546
12 | 2665263.8087 | 1193321.8207
13 | 2665288.3865 | 1193336.986
14 | 2665149.5632 | 1193254.047
15 | 2665368.1809 | 1193475.809
16 | 2665070.9193 | 1193214.2004
17 | 2665207.3636 | 1193203.7186
18 | 2665366.4586 | 1193489.0494
19 | 2665003.3517 | 1193185.0059
20 | 2665230.2967 | 1193210.701
21 | 2665825.7257 | 1193335.3821
22 | 2665687.0845 | 1193401.9355
23 | 2665499.3309 | 1193131.1368
24 | 2665647.0159 | 1193353.6711
25 | 2665659.107 | 1193370.583
26 | 2665687.8526 | 1193403.9182
27 | 2665143.0003 | 1193758.1503
28 | 2665123.7431 | 1193737.4712
29 | 2665153.5698 | 1193774.2063
30 | 2665066.137 | 1193631.2381
31 | 2665139.1855 | 1193778.6523
32 | 2665160.6966 | 1193796.5303
33 | 2665063.7547 | 1193637.9494
34 | 2665071.9145 | 1193525.3778
35 | 2665137.4992 | 1193774.1554
36 | 2665165.7797 | 1193801.296
37 | 2665040.2699 | 1193350.2098
38 | 2665050.711 | 1193364.9557
39 | 2665070.6596 | 1193447.0739
40 | 2665069.545 | 1193417.0464
41 | 2665071.8719 | 1193519.9659
42 | 2665066.4918 | 1193399.4392
43 | 2665061.3014 | 1193384.5189
44 | 2665061.0367 | 1193383.964
45 | 2664996.6972 | 1193633.974
46 | 2665031.8246 | 1193827.5134
47 | 2664912.9082 | 1193739.256
48 | 2664912.6353 | 1193772.4466
49 | 2664908.0511 | 1193725.1987
50 | 2664716.9754 | 1193773.5488
51 | 2664682.2178 | 1193833.1058
52 | 2665000.7448 | 1193947.4238
53 | 2664928.3727 | 1193884.9687
54 | 2664900.2214 | 1193901.5965
55 | 2664904.6069 | 1193898.783
56 | 2664997.6085 | 1193989.8701
57 | 2665188.7768 | 1194131.733
58 | 2664980.8664 | 1194071.6809
59 | 2664970.1649 | 1194051.409
60 | 2664965.8726 | 1194039.1099
61 | 2665258.3104 | 1193892.3319
62 | 2665268.3241 | 1193902.1872
63 | 2665276.3643 | 1193901.778
64 | 2665256.2394 | 1193951.7773
65 | 2665300.5449 | 1193888.4083
66 | 2665338.0423 | 1193912.6587
67 | 2665397.3609 | 1193714.392
68 | 2665207.0985 | 1194137.4243
69 | 2665196.4686 | 1194138.6982
70 | 2665129.3847 | 1194253.2021
71 | 2665297.3116 | 1194248.0915
72 | 2665303.2981 | 1194328.6744
73 | 2665300.3219 | 1194208.2935
74 | 2665215.2818 | 1194345.1465
75 | 2665620.5865 | 1194107.204
76 | 2665234.8114 | 1194369.8182
77 | 2665140.0546 | 1194419.6042
78 | 2665153.6928 | 1194443.8675
79 | 2665245.8242 | 1194551.4819
80 | 2665248.2881 | 1194561.6
81 | 2665152.2577 | 1194421.9338
82 | 2665360.6316 | 1194583.6389
83 | 2665040.407 | 1194367.994
84 | 2665033.2391 | 1194349.6935
85 | 2664960.7921 | 1194306.6771
86 | 2664984.0293 | 1194334.2603
87 | 2664818.0959 | 1194117.2535
88 | 2664997.644 | 1194350.4181
89 | 2664706.0535 | 1193938.8299
90 | 2665015.1982 | 1194371.2514
91 | 2664992.9292 | 1194374.5609
92 | 2665025.2327 | 1194369.8208
93 | 2665030.3965 | 1194369.1991
94 | 2664969.9702 | 1194377.572
95 | 2665743.4302 | 1194690.6108
96 | 2665741.5629 | 1194684.2273
97 | 2665745.9083 | 1194699.0829
98 | 2665739.5396 | 1194677.3103
99 | 2665838.3437 | 1194545.8938
100 | 2665394.921 | 1194656.3451
101 | 2665794.8054 | 1194508.4575
102 | 2665863.1908 | 1194549.1844
103 | 2665383.7268 | 1194675.8565
104 | 2665624.8122 | 1194111.7307
105 | 2665256.2394 | 1193951.7773

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9726 | -0.19784 | 0.0002227 | 5.5813e-05
1 | 0.97259 | -0.19791 | 0.00017922 | 4.4917e-05
2 | 0.97261 | -0.19776 | 0 | 0
3 | 0.9726 | -0.19782 | 7.2851e-05 | 1.8258e-05
4 | 0.97264 | -0.19749 | 0 | 0
5 | 0.97238 | -0.19947 | 0 | 0
6 | 0.97236 | -0.19964 | 6.6704e-05 | 1.6717e-05
7 | 0.97209 | -0.20161 | 0.00017752 | 4.4492e-05
8 | 0.97249 | -0.19864 | 0 | 0
9 | 0.97433 | -0.18498 | 8.7448e-05 | 2.1917e-05
10 | 0.97246 | -0.19884 | 0 | 0
11 | 0.97247 | -0.19881 | 0.00014273 | 3.5771e-05
12 | 0.98514 | -0.1066 | 0.00047179 | 0.00011824
13 | 0.98509 | -0.10695 | 0.00019895 | 4.9862e-05
14 | 0.98546 | -0.10433 | 0 | 0
15 | 0.98487 | -0.10859 | 0.00041962 | 0.00010517
16 | 0.98586 | -0.10136 | 0.00014547 | 3.6459e-05
17 | 0.98528 | -0.10564 | 0.00016494 | 4.1337e-05
18 | 0.98485 | -0.10866 | 0.00054797 | 0.00013733
19 | 0.98621 | -0.098765 | 0 | 0
20 | 0.98521 | -0.10621 | 0.00016289 | 4.0825e-05
21 | 0.98413 | -0.11417 | 0.00024263 | 6.0808e-05
22 | 0.98418 | -0.11377 | 0.0001805 | 4.5237e-05
23 | 0.98472 | -0.10982 | 0 | 0
24 | 0.98426 | -0.11319 | 0.00011186 | 2.8036e-05
25 | 0.98423 | -0.11343 | 0.00037833 | 9.4819e-05
26 | 0.98418 | -0.11378 | 0.00027884 | 6.9883e-05
27 | 0.99459 | -0.038319 | 0.00021898 | 5.4881e-05
28 | 0.9936 | -0.045324 | 0 | 0
29 | 0.99526 | -0.033502 | 0 | 0
30 | 0.9892 | -0.076856 | 0 | 0
31 | 0.99522 | -0.033803 | 0 | 0
32 | 0.99571 | -0.030333 | 0 | 0
33 | 0.98902 | -0.078185 | 0 | 0
34 | 0.98828 | -0.083561 | 0.00015199 | 3.8093e-05
35 | 0.99521 | -0.033899 | 0.0019899 | 0.00049872
36 | 0.99584 | -0.029396 | 0.00064722 | 0.00016221
37 | 0.98703 | -0.092712 | 9.5427e-05 | 2.3916e-05
38 | 0.98712 | -0.092056 | 0.00058478 | 0.00014656
39 | 0.98769 | -0.087879 | 0.0001044 | 2.6164e-05
40 | 0.98747 | -0.089489 | 0.00041259 | 0.00010341
41 | 0.98823 | -0.083894 | 0.00066436 | 0.0001665
42 | 0.98735 | -0.090374 | 0.00030096 | 7.5429e-05
43 | 0.98725 | -0.09111 | 0.00027316 | 6.846e-05
44 | 0.98724 | -0.091137 | 0.00010944 | 2.7428e-05
45 | 0.98894 | -0.078732 | 0.00076626 | 0.00019204
46 | 0.98357 | -0.11741 | 0 | 0
47 | 0.98291 | -0.12222 | 0.00038172 | 9.5667e-05
48 | 0.98288 | -0.12247 | 0.00071149 | 0.00017832
49 | 0.98294 | -0.12205 | 0 | 0
50 | 0.98277 | -0.12328 | 0.00027033 | 6.775e-05
51 | 0.98274 | -0.1235 | 0.00030086 | 7.5403e-05
52 | 0.98106 | -0.13562 | 0 | 0
53 | 0.98327 | -0.11956 | 0.00043583 | 0.00010923
54 | 0.98321 | -0.11997 | 0.00080294 | 0.00020123
55 | 0.98322 | -0.11993 | 0.00047325 | 0.00011861
56 | 0.98093 | -0.13653 | 0 | 0
57 | 0.97644 | -0.16938 | 0.0019178 | 0.00048065
58 | 0.98067 | -0.13843 | 0.0014609 | 0.00036613
59 | 0.98072 | -0.13808 | 0.00054417 | 0.00013638
60 | 0.98075 | -0.13781 | 0 | 0
61 | 0.99837 | -0.011464 | 0.00029072 | 7.286e-05
62 | 0.99866 | -0.0094672 | 0 | 0
63 | 0.99855 | -0.010193 | 0.0023643 | 0.00059255
64 | 1 | 0 | -0.036851 | -0.0090116
65 | 0.99831 | -0.011903 | 0 | 0
66 | 0.99792 | -0.014614 | 0.0059079 | 0.0014807
67 | 0.99824 | -0.012438 | 0.00024637 | 6.1745e-05
68 | 0.97627 | -0.17063 | 0.0013521 | 0.00033886
69 | 0.97629 | -0.17047 | 0 | 0
70 | 0.97446 | -0.184 | 7.1724e-05 | 1.7976e-05
71 | 0.97184 | -0.2035 | 0.0001343 | 3.3658e-05
72 | 0.97195 | -0.20268 | 0 | 0
73 | 0.9718 | -0.20385 | 0.00034652 | 8.6845e-05
74 | 0.97207 | -0.20177 | 0 | 0
75 | 0.97158 | -0.20546 | 0 | 0
76 | 0.97205 | -0.20192 | 0.00043266 | 0.00010844
77 | 0.97222 | -0.20062 | 0 | 0
78 | 0.97211 | -0.20144 | 0.00014976 | 3.7534e-05
79 | 0.97157 | -0.20551 | 0.00022372 | 5.6068e-05
80 | 0.97153 | -0.20577 | 0.00043048 | 0.00010789
81 | 0.97222 | -0.20066 | 0.00024941 | 6.2509e-05
82 | 0.97122 | -0.20815 | 0.00043152 | 0.00010815
83 | 0.97242 | -0.19914 | 0.00026162 | 6.5569e-05
84 | 0.97245 | -0.19889 | 0.0002174 | 5.4485e-05
85 | 0.97223 | -0.20061 | 0.0002878 | 7.2131e-05
86 | 0.97226 | -0.20033 | 0.0002484 | 6.2255e-05
87 | 0.97208 | -0.20175 | 0.00022949 | 5.7516e-05
88 | 0.97229 | -0.20011 | 0.00025566 | 6.4074e-05
89 | 0.97202 | -0.20217 | 0.00017293 | 4.3341e-05
90 | 0.97234 | -0.19975 | 0 | 0
91 | 0.97232 | -0.19989 | 0.00037266 | 9.3396e-05
92 | 0.97236 | -0.19955 | 0.00052181 | 0.00013078
93 | 0.97238 | -0.19942 | 0.00034692 | 8.6945e-05
94 | 0.97231 | -0.19994 | 0.00021099 | 5.2878e-05
95 | 0.97038 | -0.21439 | 0.00020029 | 5.0197e-05
96 | 0.97039 | -0.21435 | 8.6849e-05 | 2.1766e-05
97 | 0.97038 | -0.21442 | 0.00030428 | 7.6259e-05
98 | 0.97039 | -0.21431 | 0.00014235 | 3.5676e-05
99 | 0.97026 | -0.21527 | 0.00018132 | 4.5444e-05
100 | 0.97104 | -0.20951 | 0 | 0
101 | 0.97024 | -0.2154 | 0.00020466 | 5.1292e-05
102 | 0.97026 | -0.21531 | 0.00015169 | 3.8017e-05
103 | 0.97103 | -0.20957 | 0.00018704 | 4.6876e-05
104 | 0.97158 | -0.20548 | 0.00043571 | 0.0001092
105 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.00017922 | 4.448e-05 | -0.00017922 | -4.4917e-05 | 1.6553e-09 | -4.3747e-07 | 0.00027405 | 0.0002742 | 0.0002742 | 0.9726 | -0.19784 | 0.97259 | -0.19791 | 0.10156
1 | -0.00040192 | -0.00010029 | 0.00040193 | 0.00010006 | 4.3956e-09 | -2.2966e-07 | 0.00061476 | 0.00061468 | 0.00061476 | 0.9726 | -0.19784 | 0.97261 | -0.19776 | 0.22769
2 | 7.2851e-05 | 1.7458e-05 | -7.2851e-05 | -1.8258e-05 | 4.9881e-10 | -8.0044e-07 | 0.00011117 | 0.00011146 | 0.00011146 | 0.97261 | -0.19776 | 0.9726 | -0.19782 | 0.04128
3 | -0.00047478 | -0.00011752 | 0.0004748 | 0.00011686 | 1.7635e-08 | -6.5918e-07 | 0.00072585 | 0.00072561 | 0.00072585 | 0.97261 | -0.19776 | 0.97264 | -0.19749 | 0.26883
4 | 0.0032695 | 0.00080955 | -0.003269 | -0.00080976 | 5.0719e-07 | -2.0863e-07 | 0.0049984 | 0.0049985 | 0.0049985 | 0.97264 | -0.19749 | 0.97249 | -0.19864 | 1.8513
5 | -0.0082871 | -0.002043 | 0.008301 | 0.0020466 | 1.391e-05 | 3.6224e-06 | 0.012666 | 0.012665 | 0.012666 | 0.97264 | -0.19749 | 0.97433 | -0.18498 | 4.6911
6 | 0.0045428 | 0.0011165 | -0.0045416 | -0.0011166 | 1.2017e-06 | -3.364e-08 | 0.006942 | 0.0069421 | 0.0069421 | 0.97264 | -0.19749 | 0.97238 | -0.19947 | 2.5712
7 | 0.003014 | 0.0007426 | -0.003014 | -0.00074263 | 6.8053e-08 | -3.7542e-08 | 0.0046078 | 0.0046078 | 0.0046078 | 0.97238 | -0.19947 | 0.97236 | -0.19964 | 1.7066
8 | 0.0015275 | 0.00037398 | -0.0015271 | -0.00037539 | 4.3276e-07 | -1.4114e-06 | 0.0023344 | 0.0023349 | 0.0023349 | 0.97238 | -0.19947 | 0.97209 | -0.20161 | 0.86479
9 | 0.0029473 | 0.00072592 | -0.0029469 | -0.00072615 | 3.8783e-07 | -2.3052e-07 | 0.0045057 | 0.0045059 | 0.0045059 | 0.97236 | -0.19964 | 0.97222 | -0.20062 | 1.6688
10 | 0.0013496 | 0.0003309 | -0.0013495 | -0.00033103 | 2.9734e-08 | -1.2733e-07 | 0.0020632 | 0.0020633 | 0.0020633 | 0.97209 | -0.20161 | 0.97207 | -0.20177 | 0.76417
11 | 0.0031263 | 0.0007754 | -0.0031262 | -0.00077544 | 8.7136e-08 | -4.2293e-08 | 0.0047806 | 0.0047806 | 0.0047806 | 0.97249 | -0.19864 | 0.97246 | -0.19884 | 1.7706
12 | 0.00014273 | 3.4362e-05 | -0.00014273 | -3.5771e-05 | 3.3761e-09 | -1.4093e-06 | 0.0002179 | 0.0002184 | 0.0002184 | 0.97249 | -0.19864 | 0.97247 | -0.19881 | 0.080887
13 | -0.0083884 | -0.0020685 | 0.0083895 | 0.0020688 | 1.1025e-06 | 2.8968e-07 | 0.012799 | 0.012799 | 0.012799 | 0.97433 | -0.18498 | 0.97446 | -0.184 | 4.7403
14 | 0.0029088 | 0.00072124 | -0.0029087 | -0.00072132 | 1.1601e-07 | -7.1951e-08 | 0.0044481 | 0.0044481 | 0.0044481 | 0.97246 | -0.19884 | 0.97242 | -0.19914 | 1.6475
15 | 0.0002174 | 5.4196e-05 | -0.0002174 | -5.4485e-05 | 1.611e-09 | -2.8891e-07 | 0.00033255 | 0.00033266 | 0.00033266 | 0.97246 | -0.19884 | 0.97245 | -0.19889 | 0.12321
16 | 0.0011668 | 0.00028986 | -0.0011668 | -0.00029021 | 5.595e-08 | -3.4635e-07 | 0.0017615 | 0.0017617 | 0.0017617 | 0.98514 | -0.1066 | 0.98509 | -0.10695 | 0.65246
17 | -0.0016386 | -0.00040811 | 0.0016391 | 0.00040661 | 5.0742e-07 | -1.4972e-06 | 0.0024741 | 0.0024735 | 0.0024741 | 0.98514 | -0.1066 | 0.98546 | -0.10433 | 0.91635
18 | 0.00096781 | 0.00024035 | -0.0009676 | -0.00024233 | 2.1662e-07 | -1.9854e-06 | 0.0014611 | 0.0014619 | 0.0014619 | 0.98509 | -0.10695 | 0.98487 | -0.10859 | 0.54143
19 | -0.0031607 | -0.00077685 | 0.0031619 | 0.0007762 | 1.2505e-06 | -6.4309e-07 | 0.0047671 | 0.0047667 | 0.0047671 | 0.98546 | -0.10433 | 0.98586 | -0.10136 | 1.7656
20 | 0.0015215 | 0.00037024 | -0.0015213 | -0.00037116 | 2.6251e-07 | -9.1757e-07 | 0.0022936 | 0.0022939 | 0.0022939 | 0.98546 | -0.10433 | 0.98528 | -0.10564 | 0.84961
21 | 0.00054798 | 0.00013717 | -0.00054797 | -0.00013733 | 5.7181e-09 | -1.6793e-07 | 0.00082787 | 0.00082793 | 0.00082793 | 0.98487 | -0.10859 | 0.98485 | -0.10866 | 0.30664
22 | -0.0033074 | -0.00081266 | 0.0033085 | 0.00081216 | 1.1421e-06 | -4.9979e-07 | 0.0049863 | 0.004986 | 0.0049863 | 0.98586 | -0.10136 | 0.98621 | -0.098765 | 1.8468
23 | 0.0013563 | 0.00032982 | -0.0013562 | -0.00033027 | 9.976e-08 | -4.4849e-07 | 0.0020449 | 0.002045 | 0.002045 | 0.98528 | -0.10564 | 0.98521 | -0.10621 | 0.75742
24 | -0.0033085 | -0.00081216 | 0.0033112 | 0.000811 | 2.6586e-06 | -1.1665e-06 | 0.004986 | 0.0049852 | 0.004986 | 0.98621 | -0.098765 | 0.98703 | -0.092712 | 1.8467
25 | 0.0011933 | 0.00028944 | -0.0011928 | -0.00029279 | 5.6697e-07 | -3.3527e-06 | 0.001799 | 0.0018002 | 0.0018002 | 0.98521 | -0.10621 | 0.98472 | -0.10982 | 0.66676
26 | -0.00024263 | -6.0808e-05 | 0.00024264 | 5.8859e-05 | 1.2891e-08 | -1.9492e-06 | 0.00036686 | 0.00036617 | 0.00036686 | 0.98413 | -0.11417 | 0.98418 | -0.11377 | 0.13587
27 | -0.00070197 | -0.00017395 | 0.00070201 | 0.00017338 | 3.2181e-08 | -5.7033e-07 | 0.0010606 | 0.0010604 | 0.0010606 | 0.98418 | -0.11377 | 0.98423 | -0.11343 | 0.39283
28 | 0.00027884 | 6.9856e-05 | -0.00027884 | -6.9883e-05 | 2.358e-10 | -2.6929e-08 | 0.00042157 | 0.00042158 | 0.00042158 | 0.98418 | -0.11377 | 0.98418 | -0.11378 | 0.15614
29 | 0.0011928 | 0.00029279 | -0.0011922 | -0.00029598 | 5.4048e-07 | -3.1882e-06 | 0.0018002 | 0.0018014 | 0.0018014 | 0.98472 | -0.10982 | 0.98426 | -0.11319 | 0.6672
30 | 0.0010804 | 0.00026795 | -0.0010803 | -0.0002682 | 3.493e-08 | -2.5355e-07 | 0.0016323 | 0.0016324 | 0.0016324 | 0.98426 | -0.11319 | 0.98423 | -0.11343 | 0.6046
31 | 0.024229 | 0.0060377 | -0.024206 | -0.0060292 | 2.3212e-05 | 8.5603e-06 | 0.036237 | 0.036237 | 0.036237 | 0.99459 | -0.038319 | 0.9936 | -0.045324 | 13.4212
32 | -0.024448 | -0.0060926 | 0.024464 | 0.0060986 | 1.6133e-05 | 5.9538e-06 | 0.036565 | 0.036565 | 0.036565 | 0.99459 | -0.038319 | 0.99526 | -0.033502 | 13.5425
33 | 0.024206 | 0.0060292 | -0.024102 | -0.0059908 | 0.00010395 | 3.8345e-05 | 0.036237 | 0.036238 | 0.036238 | 0.9936 | -0.045324 | 0.9892 | -0.076856 | 13.4214
34 | 0.00199 | 0.0004985 | -0.0019899 | -0.00049866 | 8.2942e-08 | -1.6323e-07 | 0.0029752 | 0.0029752 | 0.0029752 | 0.99526 | -0.033502 | 0.99522 | -0.033803 | 1.1019
35 | -0.026454 | -0.0065971 | 0.026465 | 0.0066009 | 1.1497e-05 | 3.809e-06 | 0.03954 | 0.03954 | 0.03954 | 0.99526 | -0.033502 | 0.99571 | -0.030333 | 7.3222
36 | 0.018082 | 0.0045032 | -0.018079 | -0.004502 | 3.2851e-06 | 1.1721e-06 | 0.02719 | 0.02719 | 0.02719 | 0.9892 | -0.076856 | 0.98902 | -0.078185 | 10.0704
37 | 0.0060197 | 0.0014876 | -0.0060142 | -0.0014869 | 5.4361e-06 | 7.2599e-07 | 0.0090477 | 0.0090482 | 0.0090482 | 0.9892 | -0.076856 | 0.98828 | -0.083561 | 3.3512
38 | 0.0019899 | 0.00049866 | -0.0019899 | -0.00049872 | 2.6529e-08 | -5.2202e-08 | 0.0029752 | 0.0029753 | 0.0029753 | 0.99522 | -0.033803 | 0.99521 | -0.033899 | 1.1019
39 | -0.026465 | -0.0066009 | 0.026469 | 0.006602 | 3.3987e-06 | 1.1259e-06 | 0.03954 | 0.039539 | 0.03954 | 0.99571 | -0.030333 | 0.99584 | -0.029396 | 7.3221
40 | 0.00076632 | 0.00019117 | -0.00076626 | -0.00019204 | 5.7712e-08 | -8.7081e-07 | 0.0011526 | 0.001153 | 0.001153 | 0.98902 | -0.078185 | 0.98894 | -0.078732 | 0.42702
41 | 0.017312 | 0.0043109 | -0.01722 | -0.0042781 | 9.2375e-05 | 3.2742e-05 | 0.026037 | 0.026038 | 0.026038 | 0.98902 | -0.078185 | 0.98357 | -0.11741 | 9.6439
42 | 0.0058622 | 0.0014488 | -0.005862 | -0.0014488 | 2.6268e-07 | 3.1685e-08 | 0.0088193 | 0.0088194 | 0.0088194 | 0.98828 | -0.083561 | 0.98823 | -0.083894 | 3.2664
43 | -0.027116 | -0.0067642 | 0.027183 | 0.0067865 | 6.6834e-05 | 2.23e-05 | 0.040507 | 0.040505 | 0.040507 | 0.99584 | -0.029396 | 0.99837 | -0.011464 | 7.5012
44 | -0.0034066 | -0.00083491 | 0.0034069 | 0.0008348 | 2.966e-07 | -1.1688e-07 | 0.0051291 | 0.005129 | 0.0051291 | 0.98703 | -0.092712 | 0.98712 | -0.092056 | 1.8997
45 | -0.0039917 | -0.00098135 | 0.0039922 | 0.00098127 | 4.8915e-07 | -8.9291e-08 | 0.0060105 | 0.0060104 | 0.0060105 | 0.98712 | -0.092056 | 0.98724 | -0.091137 | 2.2261
46 | 0.0050904 | 0.001256 | -0.0050893 | -0.0012559 | 1.1008e-06 | 3.8903e-08 | 0.0076621 | 0.0076622 | 0.0076622 | 0.98769 | -0.087879 | 0.98747 | -0.089489 | 2.8379
47 | -0.0051948 | -0.0012821 | 0.0051976 | 0.0012823 | 2.7816e-06 | 1.3621e-07 | 0.0078194 | 0.007819 | 0.0078194 | 0.98769 | -0.087879 | 0.98823 | -0.083894 | 2.8961
48 | 0.0046767 | 0.0011525 | -0.0046762 | -0.0011525 | 5.5435e-07 | -1.6029e-08 | 0.0070405 | 0.0070406 | 0.0070406 | 0.98747 | -0.089489 | 0.98735 | -0.090374 | 2.6076
49 | 0.0043752 | 0.0010771 | -0.0043748 | -0.0010772 | 4.3055e-07 | -3.7764e-08 | 0.006587 | 0.0065871 | 0.0065871 | 0.98735 | -0.090374 | 0.98725 | -0.09111 | 2.4397
50 | 0.0041016 | 0.0010087 | -0.0041016 | -0.0010087 | 1.4629e-08 | -2.2343e-09 | 0.0061753 | 0.0061754 | 0.0061754 | 0.98725 | -0.09111 | 0.98724 | -0.091137 | 2.2872
51 | 0.013842 | 0.0034406 | -0.013808 | -0.003429 | 3.4258e-05 | 1.159e-05 | 0.020931 | 0.020931 | 0.020931 | 0.98357 | -0.11741 | 0.98106 | -0.13562 | 7.7524
52 | 0.0017126 | 0.00042734 | -0.0017121 | -0.00042868 | 5.0647e-07 | -1.3397e-06 | 0.0025903 | 0.0025908 | 0.0025908 | 0.98357 | -0.11741 | 0.98327 | -0.11956 | 0.95956
53 | 0.0016656 | 0.0004102 | -0.0016645 | -0.00041313 | 1.0409e-06 | -2.937e-06 | 0.0025173 | 0.0025184 | 0.0025184 | 0.98357 | -0.11741 | 0.98294 | -0.12205 | 0.93276
54 | 0.00071152 | 0.00017789 | -0.00071149 | -0.00017832 | 2.4771e-08 | -4.2418e-07 | 0.001077 | 0.0010772 | 0.0010772 | 0.98291 | -0.12222 | 0.98288 | -0.12247 | 0.39895
55 | -0.0010932 | -0.00027356 | 0.0010933 | 0.00027338 | 2.5415e-08 | -1.7874e-07 | 0.0016549 | 0.0016548 | 0.0016549 | 0.98291 | -0.12222 | 0.98294 | -0.12205 | 0.61292
56 | 0.00057129 | 0.00013975 | -0.0005712 | -0.00014228 | 9.4344e-08 | -2.53e-06 | 0.00086364 | 0.00086454 | 0.00086454 | 0.98294 | -0.12205 | 0.98277 | -0.12328 | 0.3202
57 | 0.00030087 | 7.4532e-05 | -0.00030086 | -7.5403e-05 | 8.9265e-09 | -8.7058e-07 | 0.00045524 | 0.00045555 | 0.00045555 | 0.98277 | -0.12328 | 0.98274 | -0.1235 | 0.16872
58 | 0.0020058 | 0.00050102 | -0.0020055 | -0.00050147 | 2.4923e-07 | -4.4916e-07 | 0.0030417 | 0.0030418 | 0.0030418 | 0.98106 | -0.13562 | 0.98093 | -0.13653 | 1.1266
59 | 0.011802 | 0.002928 | -0.011748 | -0.0029106 | 5.3869e-05 | 1.7329e-05 | 0.01789 | 0.017891 | 0.017891 | 0.98106 | -0.13562 | 0.97644 | -0.16938 | 6.6263
60 | 0.0012763 | 0.00031945 | -0.0012762 | -0.00031978 | 6.4098e-08 | -3.2464e-07 | 0.0019313 | 0.0019314 | 0.0019314 | 0.98327 | -0.11956 | 0.98322 | -0.11993 | 0.71532
61 | -0.00080294 | -0.00020123 | 0.00080294 | 0.00020117 | 4.801e-09 | -6.4235e-08 | 0.0012152 | 0.0012152 | 0.0012152 | 0.98321 | -0.11997 | 0.98322 | -0.11993 | 0.45007
62 | 0.0020055 | 0.00050147 | -0.0020052 | -0.00050211 | 3.5549e-07 | -6.4031e-07 | 0.0030418 | 0.0030421 | 0.0030421 | 0.98093 | -0.13653 | 0.98075 | -0.13781 | 1.1267
63 | 0.0098302 | 0.00243 | -0.0098287 | -0.0024296 | 1.4508e-06 | 4.2821e-07 | 0.014968 | 0.014968 | 0.014968 | 0.97644 | -0.16938 | 0.97629 | -0.17047 | 5.5439
64 | -0.0014609 | -0.00036613 | 0.0014609 | 0.00036586 | 7.0911e-08 | -2.6456e-07 | 0.0022166 | 0.0022165 | 0.0022166 | 0.98067 | -0.13843 | 0.98072 | -0.13808 | 0.82098
65 | -0.0020051 | -0.00050224 | 0.0020052 | 0.00050211 | 7.5228e-08 | -1.3545e-07 | 0.0030422 | 0.0030421 | 0.0030422 | 0.98072 | -0.13808 | 0.98075 | -0.13781 | 1.1267
66 | -0.027474 | -0.0068594 | 0.027481 | 0.0068619 | 7.5386e-06 | 2.5223e-06 | 0.040939 | 0.040939 | 0.040939 | 0.99837 | -0.011464 | 0.99866 | -0.0094672 | 7.5812
67 | 0.0085231 | 0.0021329 | -0.0085223 | -0.0021327 | 8.539e-07 | 2.174e-07 | 0.012698 | 0.012699 | 0.012699 | 0.99866 | -0.0094672 | 0.99855 | -0.010193 | 4.7032
68 | -0.036004 | -0.0089948 | 0.036051 | 0.0090115 | 4.6947e-05 | 1.6686e-05 | 0.053637 | 0.053637 | 0.053637 | 0.99866 | -0.0094672 | 1 | 0 | 9.9328
69 | 0.0061579 | 0.0015401 | -0.0061565 | -0.0015399 | 1.4515e-06 | 1.9691e-07 | 0.0091753 | 0.0091754 | 0.0091754 | 0.99855 | -0.010193 | 0.99831 | -0.011903 | 3.3983
70 | 0.0059101 | 0.0014809 | -0.0059079 | -0.0014807 | 2.217e-06 | 2.5431e-07 | 0.0088091 | 0.0088093 | 0.0088093 | 0.99831 | -0.011903 | 0.99792 | -0.014614 | 3.2627
71 | 0.00024638 | 5.903e-05 | -0.00024637 | -6.1745e-05 | 1.7479e-08 | -2.7157e-06 | 0.00036631 | 0.00036725 | 0.00036725 | 0.99831 | -0.011903 | 0.99824 | -0.012438 | 0.13602
72 | -0.0013521 | -0.00033886 | 0.0013521 | 0.00033873 | 2.8551e-08 | -1.2374e-07 | 0.0020608 | 0.0020607 | 0.0020608 | 0.97627 | -0.17063 | 0.97629 | -0.17047 | 0.76325
73 | 0.0084766 | 0.0020908 | -0.0084613 | -0.0020868 | 1.5374e-05 | 4.0674e-06 | 0.012908 | 0.012908 | 0.012908 | 0.97629 | -0.17047 | 0.97446 | -0.184 | 4.7809
74 | -0.00091665 | -0.00022502 | 0.00091675 | 0.00022405 | 9.9699e-08 | -9.6947e-07 | 0.0014018 | 0.0014015 | 0.0014018 | 0.97184 | -0.2035 | 0.97195 | -0.20268 | 0.51919
75 | 0.00078235 | 0.00019136 | -0.00078232 | -0.00019184 | 3.6011e-08 | -4.8579e-07 | 0.0011962 | 0.0011964 | 0.0011964 | 0.97184 | -0.2035 | 0.9718 | -0.20385 | 0.4431
76 | -0.00091675 | -0.00022405 | 0.00091686 | 0.00022298 | 1.0979e-07 | -1.0684e-06 | 0.0014015 | 0.0014011 | 0.0014015 | 0.97195 | -0.20268 | 0.97207 | -0.20177 | 0.51906
77 | 0.0004358 | 0.000105 | -0.00043571 | -0.00010912 | 9.3103e-08 | -4.1242e-06 | 0.0006658 | 0.00066728 | 0.00066728 | 0.9718 | -0.20385 | 0.97158 | -0.20546 | 0.24714
78 | 0.00043267 | 0.00010805 | -0.00043266 | -0.00010844 | 8.6045e-09 | -3.8645e-07 | 0.00066218 | 0.00066232 | 0.00066232 | 0.97207 | -0.20177 | 0.97205 | -0.20192 | 0.2453
79 | 0.00043571 | 0.00010912 | -0.00043571 | -0.0001092 | 1.7185e-09 | -7.5935e-08 | 0.00066728 | 0.00066731 | 0.00066731 | 0.97158 | -0.20546 | 0.97158 | -0.20548 | 0.24715
80 | 0.00024942 | 6.2355e-05 | -0.00024941 | -6.2509e-05 | 1.1295e-09 | -1.5362e-07 | 0.00038168 | 0.00038174 | 0.00038174 | 0.97222 | -0.20062 | 0.97222 | -0.20066 | 0.14138
81 | 0.0026975 | 0.00066379 | -0.0026972 | -0.00066402 | 2.9542e-07 | -2.3149e-07 | 0.0041242 | 0.0041243 | 0.0041243 | 0.97222 | -0.20062 | 0.97211 | -0.20144 | 1.5275
82 | 0.0025474 | 0.00062649 | -0.002546 | -0.00062777 | 1.3841e-06 | -1.2789e-06 | 0.0038951 | 0.0038957 | 0.0038957 | 0.97211 | -0.20144 | 0.97157 | -0.20551 | 1.4429
83 | 0.0023223 | 0.0005717 | -0.0023222 | -0.0005718 | 8.2036e-08 | -9.7406e-08 | 0.0035531 | 0.0035531 | 0.0035531 | 0.97157 | -0.20551 | 0.97153 | -0.20577 | 1.316
84 | 0.0018918 | 0.00046391 | -0.0018912 | -0.0004651 | 5.9833e-07 | -1.1871e-06 | 0.0028938 | 0.0028943 | 0.0028943 | 0.97153 | -0.20577 | 0.97122 | -0.20815 | 1.072
85 | 0.0014596 | 0.00035695 | -0.0014594 | -0.00035789 | 2.6345e-07 | -9.4595e-07 | 0.0022332 | 0.0022335 | 0.0022335 | 0.97122 | -0.20815 | 0.97104 | -0.20951 | 0.82723
86 | 0.002647 | 0.00065575 | -0.0026469 | -0.00065583 | 1.0309e-07 | -8.5429e-08 | 0.0040478 | 0.0040478 | 0.0040478 | 0.97242 | -0.19914 | 0.97238 | -0.19942 | 1.4992
87 | -0.0006903 | -0.00016723 | 0.00069032 | 0.00016679 | 2.502e-08 | -4.3764e-07 | 0.0010545 | 0.0010543 | 0.0010545 | 0.97223 | -0.20061 | 0.97226 | -0.20033 | 0.39054
88 | 0.00040249 | 9.5099e-05 | -0.00040243 | -9.8169e-05 | 5.8776e-08 | -3.0699e-06 | 0.000614 | 0.00061507 | 0.00061507 | 0.97223 | -0.20061 | 0.97208 | -0.20175 | 0.2278
89 | -0.00093872 | -0.00022905 | 0.00093875 | 0.00022879 | 2.7128e-08 | -2.5161e-07 | 0.0014345 | 0.0014344 | 0.0014345 | 0.97226 | -0.20033 | 0.97229 | -0.20011 | 0.53128
90 | 0.00017294 | 4.0653e-05 | -0.00017293 | -4.3341e-05 | 9.4627e-09 | -2.6883e-06 | 0.00026379 | 0.00026474 | 0.00026474 | 0.97208 | -0.20175 | 0.97202 | -0.20217 | 0.09805
91 | -0.0011944 | -0.00029287 | 0.0011945 | 0.00029255 | 5.6655e-08 | -3.161e-07 | 0.0018256 | 0.0018255 | 0.0018256 | 0.97229 | -0.20011 | 0.97234 | -0.19975 | 0.67616
92 | 0.00058366 | 0.00014571 | -0.00058364 | -0.00014599 | 1.1204e-08 | -2.7493e-07 | 0.00089299 | 0.00089309 | 0.00089309 | 0.97234 | -0.19975 | 0.97232 | -0.19989 | 0.33078
93 | -0.0017781 | -0.00043827 | 0.0017782 | 0.00043816 | 4.6748e-08 | -1.0776e-07 | 0.0027185 | 0.0027185 | 0.0027185 | 0.97234 | -0.19975 | 0.97236 | -0.19955 | 1.0069
94 | 0.00021099 | 5.2592e-05 | -0.00021099 | -5.2878e-05 | 1.5067e-09 | -2.8676e-07 | 0.00032279 | 0.00032289 | 0.00032289 | 0.97232 | -0.19989 | 0.97231 | -0.19994 | 0.11959
95 | -0.0023 | -0.00056894 | 0.0023 | 0.00056889 | 4.0143e-08 | -4.9076e-08 | 0.003517 | 0.003517 | 0.003517 | 0.97236 | -0.19955 | 0.97238 | -0.19942 | 1.3026
96 | -0.00050457 | -0.00012635 | 0.00050457 | 0.00012627 | 2.4842e-09 | -8.1209e-08 | 0.00077369 | 0.00077366 | 0.00077369 | 0.97038 | -0.21439 | 0.97039 | -0.21435 | 0.28655
97 | 0.00030428 | 7.6151e-05 | -0.00030428 | -7.6259e-05 | 1.199e-09 | -1.0858e-07 | 0.00046655 | 0.00046659 | 0.00046659 | 0.97038 | -0.21439 | 0.97038 | -0.21442 | 0.17281
98 | -0.00059142 | -0.00014803 | 0.00059142 | 0.00014795 | 3.698e-09 | -8.761e-08 | 0.00090683 | 0.0009068 | 0.00090683 | 0.97039 | -0.21435 | 0.97039 | -0.21431 | 0.33586
99 | 0.00053774 | 0.00013171 | -0.00053768 | -0.00013371 | 6.9635e-08 | -2.0041e-06 | 0.00082349 | 0.00082422 | 0.00082422 | 0.97039 | -0.21431 | 0.97026 | -0.21527 | 0.30527
100 | -0.0012715 | -0.00031533 | 0.0012723 | 0.00031138 | 8.1736e-07 | -3.9537e-06 | 0.0019486 | 0.001947 | 0.0019486 | 0.97039 | -0.21431 | 0.97104 | -0.20951 | 0.72169
101 | 0.00015169 | 3.7705e-05 | -0.00015169 | -3.8017e-05 | 8.546e-10 | -3.1236e-07 | 0.00023253 | 0.00023264 | 0.00023264 | 0.97026 | -0.21527 | 0.97026 | -0.21531 | 0.086162
102 | 0.00020466 | 5.0564e-05 | -0.00020466 | -5.1292e-05 | 3.6273e-09 | -7.2797e-07 | 0.00031361 | 0.00031387 | 0.00031387 | 0.97026 | -0.21527 | 0.97024 | -0.2154 | 0.11625
103 | 0.00018704 | 4.6517e-05 | -0.00018704 | -4.6876e-05 | 1.4906e-09 | -3.593e-07 | 0.00028649 | 0.00028662 | 0.00028662 | 0.97104 | -0.20951 | 0.97103 | -0.20957 | 0.10615

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.037898 | 0.0092739

## res_load
| p_mw | q_mvar
0 | 0.0002227 | 5.5813e-05
1 | 0.00017922 | 4.4917e-05
2 | 7.2851e-05 | 1.8258e-05
3 | 6.6704e-05 | 1.6717e-05
4 | 0.00017752 | 4.4492e-05
5 | 8.7448e-05 | 2.1917e-05
6 | 0.00014273 | 3.5771e-05
7 | 0.00047179 | 0.00011824
8 | 0.00019895 | 4.9862e-05
9 | 0.00041962 | 0.00010517
10 | 0.00014547 | 3.6459e-05
11 | 0.00016494 | 4.1337e-05
12 | 0.00054797 | 0.00013733
13 | 0.00016289 | 4.0825e-05
14 | 0.00024263 | 6.0808e-05
15 | 0.0001805 | 4.5237e-05
16 | 0.00011186 | 2.8036e-05
17 | 0.00037833 | 9.4819e-05
18 | 0.00027884 | 6.9883e-05
19 | 0.00021898 | 5.4881e-05
20 | 0.00015199 | 3.8093e-05
21 | 0.0019899 | 0.00049872
22 | 0.00064722 | 0.00016221
23 | 9.5427e-05 | 2.3916e-05
24 | 0.00058478 | 0.00014656
25 | 0.0001044 | 2.6164e-05
26 | 0.00041259 | 0.00010341
27 | 0.00066436 | 0.0001665
28 | 0.00030096 | 7.5429e-05
29 | 0.00027316 | 6.846e-05
30 | 0.00010944 | 2.7428e-05
31 | 0.00076626 | 0.00019204
32 | 0.00038172 | 9.5667e-05
33 | 0.00071149 | 0.00017832
34 | 0.00027033 | 6.775e-05
35 | 0.00030086 | 7.5403e-05
36 | 0.00043583 | 0.00010923
37 | 0.00080294 | 0.00020123
38 | 0.00047325 | 0.00011861
39 | 0.0019178 | 0.00048065
40 | 0.0014609 | 0.00036613
41 | 0.00054417 | 0.00013638
42 | 0.00029072 | 7.286e-05
43 | 0.0023643 | 0.00059255
44 | 0.0010466 | 0.0002623
45 | 0.0059079 | 0.0014807
46 | 0.00024637 | 6.1745e-05
47 | 0.0013521 | 0.00033886
48 | 7.1724e-05 | 1.7976e-05
49 | 0.0001343 | 3.3658e-05
50 | 0.00034652 | 8.6845e-05
51 | 0.00043266 | 0.00010844
52 | 0.00014976 | 3.7534e-05
53 | 0.00022372 | 5.6068e-05
54 | 0.00043048 | 0.00010789
55 | 0.00024941 | 6.2509e-05
56 | 0.00043152 | 0.00010815
57 | 0.00026162 | 6.5569e-05
58 | 0.0002174 | 5.4485e-05
59 | 0.0002878 | 7.2131e-05
60 | 0.0002484 | 6.2255e-05
61 | 0.00022949 | 5.7516e-05
62 | 0.00025566 | 6.4074e-05
63 | 0.00017293 | 4.3341e-05
64 | 0.00037266 | 9.3396e-05
65 | 0.00052181 | 0.00013078
66 | 0.00034692 | 8.6945e-05
67 | 0.00021099 | 5.2878e-05
68 | 0.00020029 | 5.0197e-05
69 | 8.6849e-05 | 2.1766e-05
70 | 0.00030428 | 7.6259e-05
71 | 0.00014235 | 3.5676e-05
72 | 0.00018132 | 4.5444e-05
73 | 0.00020466 | 5.1292e-05
74 | 0.00015169 | 3.8017e-05
75 | 0.00018704 | 4.6876e-05
76 | 0.00043571 | 0.0001092

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1