## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1404-21_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1404-21_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1404-21_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1404-21_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1404-21_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1404-21_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1404-21_0_5_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1404-21_0_5_node_19 | 0.4 | n |  | TRUE
8 | bus_LV_1404-21_0_5_node_31 | 0.4 | n |  | TRUE
9 | bus_LV_1404-21_0_5_node_32 | 0.4 | n |  | TRUE
10 | bus_LV_1404-21_0_5_node_30 | 0.4 | n |  | TRUE
11 | bus_LV_1404-21_0_5_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_1404-21_0_5_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1404-21_0_5_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_1404-21_0_5_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_1404-21_0_5_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_1404-21_0_5_node_35 | 0.4 | n |  | TRUE
17 | bus_LV_1404-21_0_5_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_1404-21_0_5_node_34 | 0.4 | n |  | TRUE
19 | bus_LV_1404-21_0_5_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_1404-21_0_5_node_33 | 0.4 | n |  | TRUE
21 | bus_LV_1404-21_0_5_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_1404-21_0_5_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_1404-21_0_5_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_1404-21_0_5_node_26 | 0.4 | n |  | TRUE
25 | bus_LV_1404-21_0_5_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_1404-21_0_5_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_1404-21_0_5_node_25 | 0.4 | n |  | TRUE
28 | bus_LV_1404-21_0_5_node_23 | 0.4 | n |  | TRUE
29 | bus_LV_1404-21_0_5_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_1404-21_0_5_node_22 | 0.4 | n |  | TRUE
31 | bus_LV_1404-21_0_5_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_1404-21_0_5_node_27 | 0.4 | n |  | TRUE
33 | bus_LV_1404-21_0_5_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_1404-21_0_5_node_29 | 0.4 | n |  | TRUE
35 | bus_MV_140_0_node_12 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1404-21_0_5_load_0 | 0 | 0.00093668 | 0.00023475 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1404-21_0_5_load_1 | 1 | 0.00065262 | 0.00016356 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1404-21_0_5_load_4 | 4 | 0.011536 | 0.0028911 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1404-21_0_5_load_6 | 6 | 0.0011749 | 0.00029446 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1404-21_0_5_load_19 | 7 | 0.00099262 | 0.00024877 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1404-21_0_5_load_31 | 8 | 0.0038966 | 0.00097659 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1404-21_0_5_load_32 | 9 | 0.010038 | 0.0025158 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1404-21_0_5_load_30 | 10 | 0.00080131 | 0.00020083 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1404-21_0_5_load_7 | 12 | 0.0055298 | 0.0013859 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1404-21_0_5_load_8 | 13 | 0.014152 | 0.0035468 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1404-21_0_5_load_9 | 14 | 0.0062751 | 0.0015727 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1404-21_0_5_load_35 | 16 | 0.016248 | 0.0040722 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1404-21_0_5_load_11 | 17 | 0.0067593 | 0.0016941 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1404-21_0_5_load_13 | 19 | 0.024229 | 0.0060723 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1404-21_0_5_load_33 | 20 | 0.00062019 | 0.00015544 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1404-21_0_5_load_16 | 23 | 0.0096332 | 0.0024143 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1404-21_0_5_load_26 | 24 | 0.0008391 | 0.0002103 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1404-21_0_5_load_17 | 25 | 0.0041851 | 0.0010489 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1404-21_0_5_load_18 | 26 | 0.0082512 | 0.0020679 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1404-21_0_5_load_23 | 28 | 0.00097336 | 0.00024395 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1404-21_0_5_load_21 | 29 | 0.0076685 | 0.0019219 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1404-21_0_5_load_24 | 31 | 0.0062135 | 0.0015573 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1404-21_0_5_load_27 | 32 | 0.0073321 | 0.0018376 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1404-21_0_5_load_28 | 33 | 0.0089844 | 0.0022517 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1404-21_0_5_load_29 | 34 | 0.070088 | 0.017566 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 13 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1404-21_0_5_line_0 | NAYY 4x150 SE | 0 | 1 | 0.025555 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1404-21_0_5_line_1 | NAYY 4x150 SE | 0 | 2 | 0.023916 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1404-21_0_5_line_2 | NAYY 4x150 SE | 1 | 3 | 0.045285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1404-21_0_5_line_3 | NAYY 4x150 SE | 2 | 4 | 0.039124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
4 | LV_1404-21_0_5_line_4 | NAYY 4x150 SE | 2 | 5 | 0.01613 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
5 | LV_1404-21_0_5_line_5 | NAYY 4x150 SE | 3 | 6 | 0.084656 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1404-21_0_5_line_6 | NAYY 4x150 SE | 3 | 7 | 0.18369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1404-21_0_5_line_7 | NAYY 4x150 SE | 4 | 8 | 0.0084021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1404-21_0_5_line_8 | NAYY 4x150 SE | 5 | 9 | 0.079288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
9 | LV_1404-21_0_5_line_9 | NAYY 4x150 SE | 8 | 10 | 0.0052898 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1404-21_0_5_line_10 | NAYY 4x150 SE | 9 | 11 | 0.066563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
11 | LV_1404-21_0_5_line_11 | NAYY 4x150 SE | 10 | 33 | 0.0047199 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1404-21_0_5_line_12 | NAYY 4x150 SE | 11 | 15 | 0.081021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
13 | LV_1404-21_0_5_line_13 | NAYY 4x150 SE | 12 | 13 | 0.030468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1404-21_0_5_line_14 | NAYY 4x150 SE | 12 | 14 | 0.026815 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1404-21_0_5_line_15 | NAYY 4x150 SE | 13 | 15 | 0.094616 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
16 | LV_1404-21_0_5_line_16 | NAYY 4x150 SE | 13 | 16 | 0.99442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1404-21_0_5_line_17 | NAYY 4x150 SE | 14 | 17 | 0.0083308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1404-21_0_5_line_18 | NAYY 4x150 SE | 16 | 18 | 0.53656 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1404-21_0_5_line_19 | NAYY 4x150 SE | 17 | 19 | 0.026682 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1404-21_0_5_line_20 | NAYY 4x150 SE | 18 | 20 | 0.0071435 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1404-21_0_5_line_21 | NAYY 4x150 SE | 19 | 21 | 0.066137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1404-21_0_5_line_22 | NAYY 4x150 SE | 21 | 22 | 0.14312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1404-21_0_5_line_23 | NAYY 4x150 SE | 21 | 23 | 0.07037 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1404-21_0_5_line_24 | NAYY 4x150 SE | 22 | 24 | 0.15129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1404-21_0_5_line_25 | NAYY 4x150 SE | 23 | 25 | 0.16732 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1404-21_0_5_line_26 | NAYY 4x150 SE | 25 | 26 | 0.013012 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1404-21_0_5_line_27 | NAYY 4x150 SE | 26 | 27 | 0.015878 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1404-21_0_5_line_28 | NAYY 4x150 SE | 27 | 28 | 0.017459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1404-21_0_5_line_29 | NAYY 4x150 SE | 28 | 30 | 0.0087993 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1404-21_0_5_line_30 | NAYY 4x150 SE | 29 | 30 | 0.048977 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1404-21_0_5_line_31 | NAYY 4x150 SE | 30 | 31 | 0.04095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1404-21_0_5_line_32 | NAYY 4x150 SE | 32 | 33 | 0.027205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1404-21_0_5_line_33 | NAYY 4x150 SE | 32 | 34 | 0.015612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1404-21_0_5_trafo_8 | 0.25 MVA 20/0.4 kV | 35 | 13 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2664156.5182 | 1192010.0487 | 2664154.5754 | 1192014.3111 | 2664148.0688 | 1192025.3145 | 2664143.559 | 1192032.0281
1 | 2664163.0312 | 1191987.186 | 2664161.7171 | 1191995.977 | 2664158.9475 | 1192004.7191 | 2664156.5182 | 1192010.0487
2 | 2664117.9634 | 1192069.3843 | 2664133.7363 | 1192046.6511 | 2664143.559 | 1192032.0281
3 | 2664163.0312 | 1191987.186 | 2664177.0695 | 1191989.0264 | 2664197.2709 | 1192003.6964
4 | 2664163.5241 | 1191971.0819 | 2664163.5978 | 1191979.8433 | 2664163.0312 | 1191987.186
5 | 2664117.9634 | 1192069.3843 | 2664120.8231 | 1192072.1498 | 2664121.9465 | 1192075.4527 | 2664121.6441 | 1192078.7736 | 2664113.9633 | 1192095.4899 | 2664097.125 | 1192124.4709 | 2664089.1427 | 1192140.8839 | 2664087.8716 | 1192144.3473
6 | 2664117.9634 | 1192069.3843 | 2663946.3531 | 1192003.8722
7 | 2664197.2709 | 1192003.6964 | 2664204.0694 | 1192008.6334
8 | 2664163.5241 | 1191971.0819 | 2664217.065 | 1191970.4111 | 2664223.3001 | 1191968.3768 | 2664227.9765 | 1191965.2585 | 2664237.7972 | 1191955.9029
9 | 2664208.3497 | 1192011.7417 | 2664204.0694 | 1192008.6334
10 | 2664277.7271 | 1191904.3904 | 2664263.4358 | 1191915.4434 | 2664247.6289 | 1191933.4509 | 2664244.9531 | 1191938.4028 | 2664237.7972 | 1191955.9029
11 | 2664213.0521 | 1192012.1476 | 2664208.3497 | 1192011.7417 | 2664208.3497 | 1192011.7417
12 | 2664277.7271 | 1191904.3904 | 2664281.7352 | 1191908.1245 | 2664285.7726 | 1191909.8466 | 2664293.9291 | 1191912.0688 | 2664355.4607 | 1191924.1147
13 | 2664450.4184 | 1191999.5245 | 2664447.6134 | 1191990.9783 | 2664443.4154 | 1191984.3626 | 2664434.896 | 1191974.7986 | 2664434.2909 | 1191974.2301
14 | 2664450.4184 | 1191999.5245 | 2664450.4184 | 1191999.5245 | 2664453.902 | 1192018.6732 | 2664455.1741 | 1192025.9142
15 | 2664355.4607 | 1191924.1147 | 2664369.6282 | 1191928.136 | 2664388.6599 | 1191937.8019 | 2664415.0992 | 1191956.197 | 2664434.2909 | 1191974.2301
16 | 2664434.2909 | 1191974.2301 | 2665242.5673 | 1191394.9527
17 | 2664456.6157 | 1192034.1193 | 2664455.1741 | 1192025.9142
18 | 2665003.8303 | 1190914.4317 | 2665242.5673 | 1191394.9527
19 | 2664456.6157 | 1192034.1193 | 2664457.5869 | 1192039.6473 | 2664461.216 | 1192051.66 | 2664464.757 | 1192059.4095
20 | 2665003.8303 | 1190914.4317 | 2664997.8101 | 1190910.5863
21 | 2664492.1904 | 1192119.5887 | 2664469.6396 | 1192070.0948 | 2664464.757 | 1192059.4095
22 | 2664555.8287 | 1192247.7493 | 2664523.3576 | 1192187.9533 | 2664492.1904 | 1192119.5887
23 | 2664492.1904 | 1192119.5887 | 2664445.3547 | 1192140.5188 | 2664434.8761 | 1192145.1309 | 2664429.0822 | 1192150.0825 | 2664429.0822 | 1192150.0825
24 | 2664555.8287 | 1192247.7493 | 2664550.2518 | 1192252.3807 | 2664544.8674 | 1192258.9487 | 2664465.2795 | 1192368.6705
25 | 2664293.3189 | 1192194.513 | 2664297.0564 | 1192193.5662 | 2664308.3588 | 1192194.5659 | 2664368.801 | 1192208.4014 | 2664376.5022 | 1192209.6738 | 2664383.6122 | 1192208.5051 | 2664390.2971 | 1192205.0417 | 2664394.494 | 1192201.8294 | 2664402.8296 | 1192190.9127 | 2664418.9978 | 1192164.8159 | 2664424.6909 | 1192156.4723 | 2664429.0822 | 1192150.0825
26 | 2664280.9706 | 1192198.563 | 2664288.8465 | 1192195.6459 | 2664293.3189 | 1192194.513
27 | 2664270.1331 | 1192209.642 | 2664273.0033 | 1192204.3142 | 2664280.9706 | 1192198.563
28 | 2664270.1331 | 1192209.642 | 2664252.7177 | 1192208.4141
29 | 2664243.9238 | 1192208.2154 | 2664250.6014 | 1192208.2649 | 2664252.7177 | 1192208.4141
30 | 2664243.9238 | 1192208.2154 | 2664238.4699 | 1192184.3763 | 2664229.0489 | 1192186.3542 | 2664218.0027 | 1192193.4398 | 2664216.2365 | 1192193.5875
31 | 2664243.9238 | 1192208.2154 | 2664238.4699 | 1192184.3763 | 2664229.0489 | 1192186.3542 | 2664223.2674 | 1192190.0628
32 | 2664240.1559 | 1192014.4873 | 2664213.0521 | 1192012.1476
33 | 2664255.7098 | 1192015.83 | 2664240.1559 | 1192014.4873

## bus_geodata
| x | y | coords
0 | 2664156.5182 | 1192010.0487
1 | 2664143.559 | 1192032.0281
2 | 2664163.0312 | 1191987.186
3 | 2664117.9634 | 1192069.3843
4 | 2664197.2709 | 1192003.6964
5 | 2664163.5241 | 1191971.0819
6 | 2664087.8716 | 1192144.3473
7 | 2663946.3531 | 1192003.8722
8 | 2664204.0694 | 1192008.6334
9 | 2664237.7972 | 1191955.9029
10 | 2664208.3497 | 1192011.7417
11 | 2664277.7271 | 1191904.3904
12 | 2664450.4184 | 1191999.5245
13 | 2664434.2909 | 1191974.2301
14 | 2664455.1741 | 1192025.9142
15 | 2664355.4607 | 1191924.1147
16 | 2665242.5673 | 1191394.9527
17 | 2664456.6157 | 1192034.1193
18 | 2665003.8302 | 1190914.4317
19 | 2664464.757 | 1192059.4095
20 | 2664997.8101 | 1190910.5863
21 | 2664492.1904 | 1192119.5887
22 | 2664555.8287 | 1192247.7493
23 | 2664429.0822 | 1192150.0825
24 | 2664465.2795 | 1192368.6705
25 | 2664293.3189 | 1192194.513
26 | 2664280.9706 | 1192198.563
27 | 2664270.1331 | 1192209.642
28 | 2664252.7177 | 1192208.4141
29 | 2664216.2365 | 1192193.5875
30 | 2664243.9238 | 1192208.2154
31 | 2664223.2674 | 1192190.0627
32 | 2664240.1559 | 1192014.4873
33 | 2664213.0521 | 1192012.1476
34 | 2664255.7098 | 1192015.83
35 | 2664355.4607 | 1191924.1147

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98073 | -0.13404 | 0.00093668 | 0.00023475
1 | 0.98062 | -0.13479 | 0.00065262 | 0.00016356
2 | 0.98086 | -0.1331 | 0 | 0
3 | 0.98048 | -0.13583 | 0 | 0
4 | 0.97792 | -0.15399 | 0.011536 | 0.0028911
5 | 0.98212 | -0.1242 | 0 | 0
6 | 0.98034 | -0.13686 | 0.0011749 | 0.00029446
7 | 0.98022 | -0.13773 | 0.00099262 | 0.00024877
8 | 0.97679 | -0.16199 | 0.0038966 | 0.00097659
9 | 0.98624 | -0.095212 | 0.010038 | 0.0025158
10 | 0.97612 | -0.16682 | 0.00080131 | 0.00020083
11 | 0.99002 | -0.068787 | 0 | 0
12 | 0.99645 | -0.024607 | 0.0055298 | 0.0013859
13 | 1 | 0 | -0.21929 | -0.055329
14 | 0.99353 | -0.044909 | 0.0062751 | 0.0015727
15 | 0.99462 | -0.036888 | 0 | 0
16 | 0.97549 | -0.17261 | 0.016248 | 0.0040722
17 | 0.9927 | -0.050711 | 0.0067593 | 0.0016941
18 | 0.97501 | -0.17624 | 0 | 0
19 | 0.9903 | -0.067523 | 0.024229 | 0.0060723
20 | 0.975 | -0.17629 | 0.00062019 | 0.00015544
21 | 0.98666 | -0.093079 | 0 | 0
22 | 0.98649 | -0.094342 | 0 | 0
23 | 0.98287 | -0.11984 | 0.0096332 | 0.0024143
24 | 0.9863 | -0.095655 | 0.0008391 | 0.0002103
25 | 0.9762 | -0.16738 | 0.0041851 | 0.0010489
26 | 0.97576 | -0.17053 | 0.0082512 | 0.0020679
27 | 0.97541 | -0.17301 | 0 | 0
28 | 0.97503 | -0.17573 | 0.00097336 | 0.00024395
29 | 0.9743 | -0.18096 | 0.0076685 | 0.0019219
30 | 0.97485 | -0.17702 | 0 | 0
31 | 0.97448 | -0.17969 | 0.0062135 | 0.0015573
32 | 0.97243 | -0.19325 | 0.0073321 | 0.0018376
33 | 0.97552 | -0.17109 | 0.0089844 | 0.0022517
34 | 0.97082 | -0.20482 | 0.070088 | 0.017566
35 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0028212 | 0.00070291 | -0.0028209 | -0.00070312 | 2.9198e-07 | -2.1014e-07 | 0.0042789 | 0.0042791 | 0.0042791 | 0.98073 | -0.13404 | 0.98062 | -0.13479 | 1.5848
1 | -0.0037578 | -0.00093767 | 0.0037583 | 0.00093755 | 4.8488e-07 | -1.1533e-07 | 0.0057001 | 0.0057 | 0.0057001 | 0.98073 | -0.13404 | 0.98086 | -0.1331 | 2.1112
2 | 0.0021682 | 0.00053956 | -0.0021679 | -0.00054001 | 3.0565e-07 | -4.5367e-07 | 0.0032888 | 0.003289 | 0.003289 | 0.98062 | -0.13479 | 0.98048 | -0.13583 | 1.2181
3 | 0.1035 | 0.026054 | -0.1032 | -0.02594 | 0.00030112 | 0.00011483 | 0.15706 | 0.15706 | 0.15706 | 0.98086 | -0.1331 | 0.97792 | -0.15399 | 29.0853
4 | -0.10726 | -0.026992 | 0.10739 | 0.027043 | 0.00013332 | 5.0868e-05 | 0.16276 | 0.16276 | 0.16276 | 0.98086 | -0.1331 | 0.98212 | -0.1242 | 30.1408
5 | 0.0011751 | 0.00029345 | -0.0011749 | -0.00029446 | 1.6796e-07 | -1.0029e-06 | 0.0017829 | 0.0017833 | 0.0017833 | 0.98048 | -0.13583 | 0.98034 | -0.13686 | 0.66049
6 | 0.00099288 | 0.00024656 | -0.00099262 | -0.00024877 | 2.6012e-07 | -2.2161e-06 | 0.001506 | 0.0015068 | 0.0015068 | 0.98048 | -0.13583 | 0.98022 | -0.13773 | 0.55809
7 | 0.091666 | 0.023049 | -0.091564 | -0.023009 | 0.00010204 | 3.9141e-05 | 0.13951 | 0.13951 | 0.13951 | 0.97792 | -0.15399 | 0.97679 | -0.16199 | 51.6696
8 | -0.10739 | -0.027043 | 0.10783 | 0.027208 | 0.00043688 | 0.00016501 | 0.16276 | 0.16276 | 0.16276 | 0.98212 | -0.1242 | 0.98624 | -0.095212 | 20.0939
9 | 0.087668 | 0.022033 | -0.087609 | -0.02201 | 5.8892e-05 | 2.2585e-05 | 0.13357 | 0.13357 | 0.13357 | 0.97679 | -0.16199 | 0.97612 | -0.16682 | 49.4711
10 | -0.11787 | -0.029724 | 0.11831 | 0.02989 | 0.0004382 | 0.00016598 | 0.1779 | 0.1779 | 0.1779 | 0.98624 | -0.095212 | 0.99002 | -0.068787 | 21.9636
11 | 0.086807 | 0.021809 | -0.086756 | -0.02179 | 5.159e-05 | 1.9783e-05 | 0.13235 | 0.13235 | 0.13235 | 0.97612 | -0.16682 | 0.97552 | -0.17109 | 49.0187
12 | -0.11831 | -0.02989 | 0.11884 | 0.030092 | 0.00053337 | 0.000202 | 0.1779 | 0.1779 | 0.1779 | 0.99002 | -0.068787 | 0.99462 | -0.036888 | 21.9635
13 | -0.081462 | -0.020527 | 0.081743 | 0.020635 | 0.00028153 | 0.00010788 | 0.12169 | 0.12169 | 0.12169 | 0.99645 | -0.024607 | 1 | 0 | 45.0696
14 | 0.075932 | 0.019141 | -0.075717 | -0.019059 | 0.00021529 | 8.2454e-05 | 0.11343 | 0.11343 | 0.11343 | 0.99645 | -0.024607 | 0.99353 | -0.044909 | 42.0112
15 | 0.11946 | 0.030328 | -0.11884 | -0.030092 | 0.00062286 | 0.00023586 | 0.1779 | 0.1779 | 0.1779 | 1 | 0 | 0.99462 | -0.036888 | 21.9633
16 | 0.01728 | 0.0043663 | -0.016869 | -0.004221 | 0.00041072 | 0.00014524 | 0.025725 | 0.025729 | 0.025729 | 1 | 0 | 0.97549 | -0.17261 | 9.5294
17 | 0.069442 | 0.017486 | -0.069385 | -0.017465 | 5.6261e-05 | 2.1531e-05 | 0.10403 | 0.10403 | 0.10403 | 0.99353 | -0.044909 | 0.9927 | -0.050711 | 38.5304
18 | 0.0006205 | 0.00014877 | -0.0006202 | -0.00015535 | 2.9918e-07 | -6.5801e-06 | 0.00094413 | 0.00094649 | 0.00094649 | 0.97549 | -0.17261 | 0.97501 | -0.17624 | 0.35055
19 | 0.062626 | 0.015771 | -0.062479 | -0.015715 | 0.0001468 | 5.6118e-05 | 0.0939 | 0.0939 | 0.0939 | 0.9927 | -0.050711 | 0.9903 | -0.067523 | 34.7779
20 | 0.0006202 | 0.00015535 | -0.00062019 | -0.00015544 | 3.9934e-09 | -8.7555e-08 | 0.00094649 | 0.00094652 | 0.00094652 | 0.97501 | -0.17624 | 0.975 | -0.17629 | 0.35056
21 | 0.03825 | 0.0096422 | -0.038114 | -0.0095906 | 0.00013642 | 5.1622e-05 | 0.057494 | 0.057495 | 0.057495 | 0.9903 | -0.067523 | 0.98666 | -0.093079 | 21.2943
22 | 0.0008394 | 0.00020665 | -0.00083925 | -0.00020843 | 1.4289e-07 | -1.7726e-06 | 0.0012646 | 0.0012653 | 0.0012653 | 0.98666 | -0.093079 | 0.98649 | -0.094342 | 0.46861
23 | 0.037275 | 0.0093839 | -0.037136 | -0.0093314 | 0.00013884 | 5.2504e-05 | 0.05623 | 0.05623 | 0.05623 | 0.98666 | -0.093079 | 0.98287 | -0.11984 | 20.826
24 | 0.00083925 | 0.00020843 | -0.0008391 | -0.0002103 | 1.5121e-07 | -1.873e-06 | 0.0012653 | 0.0012659 | 0.0012659 | 0.98649 | -0.094342 | 0.9863 | -0.095655 | 0.46887
25 | 0.027503 | 0.0069171 | -0.027321 | -0.0068496 | 0.00018109 | 6.7543e-05 | 0.041646 | 0.041647 | 0.041647 | 0.98287 | -0.11984 | 0.9762 | -0.16738 | 15.4248
26 | 0.023136 | 0.0058007 | -0.023126 | -0.005797 | 1.0099e-05 | 3.7217e-06 | 0.035268 | 0.035268 | 0.035268 | 0.9762 | -0.16738 | 0.97576 | -0.17053 | 13.0621
27 | 0.014875 | 0.003729 | -0.01487 | -0.0037273 | 5.0985e-06 | 1.7627e-06 | 0.022685 | 0.022685 | 0.022685 | 0.97576 | -0.17053 | 0.97541 | -0.17301 | 8.4017
28 | 0.01487 | 0.0037273 | -0.014864 | -0.0037253 | 5.6061e-06 | 1.9384e-06 | 0.022685 | 0.022685 | 0.022685 | 0.97541 | -0.17301 | 0.97503 | -0.17573 | 8.4018
29 | 0.013891 | 0.0034814 | -0.013889 | -0.0034805 | 2.4676e-06 | 8.3936e-07 | 0.021199 | 0.021199 | 0.021199 | 0.97503 | -0.17573 | 0.97485 | -0.17702 | 7.8516
30 | -0.0076685 | -0.0019219 | 0.0076727 | 0.0019229 | 4.192e-06 | 1.002e-06 | 0.011712 | 0.011712 | 0.011712 | 0.9743 | -0.18096 | 0.97485 | -0.17702 | 4.3377
31 | 0.0062158 | 0.0015576 | -0.0062135 | -0.0015573 | 2.3002e-06 | 3.7435e-07 | 0.0094878 | 0.0094879 | 0.0094879 | 0.97485 | -0.17702 | 0.97448 | -0.17969 | 3.514
32 | -0.077532 | -0.019446 | 0.077771 | 0.019538 | 0.00023896 | 9.1571e-05 | 0.11865 | 0.11865 | 0.11865 | 0.97243 | -0.19325 | 0.97552 | -0.17109 | 43.943
33 | 0.0702 | 0.017609 | -0.070088 | -0.017566 | 0.00011242 | 4.3047e-05 | 0.10743 | 0.10743 | 0.10743 | 0.97243 | -0.19325 | 0.97082 | -0.20482 | 39.7876

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.23344 | 0.058876

## res_load
| p_mw | q_mvar
0 | 0.00093668 | 0.00023475
1 | 0.00065262 | 0.00016356
2 | 0.011536 | 0.0028911
3 | 0.0011749 | 0.00029446
4 | 0.00099262 | 0.00024877
5 | 0.0038966 | 0.00097659
6 | 0.010038 | 0.0025158
7 | 0.00080131 | 0.00020083
8 | 0.0055298 | 0.0013859
9 | 0.014152 | 0.0035468
10 | 0.0062751 | 0.0015727
11 | 0.016248 | 0.0040722
12 | 0.0067593 | 0.0016941
13 | 0.024229 | 0.0060723
14 | 0.00062019 | 0.00015544
15 | 0.0096332 | 0.0024143
16 | 0.0008391 | 0.0002103
17 | 0.0041851 | 0.0010489
18 | 0.0082512 | 0.0020679
19 | 0.00097336 | 0.00024395
20 | 0.0076685 | 0.0019219
21 | 0.0062135 | 0.0015573
22 | 0.0073321 | 0.0018376
23 | 0.0089844 | 0.0022517
24 | 0.070088 | 0.017566

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1