## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1404-29_1_3_node_50 | 0.4 | n |  | TRUE
1 | bus_LV_1404-29_1_3_node_51 | 0.4 | n |  | TRUE
2 | bus_LV_1404-29_1_3_node_52 | 0.4 | n |  | TRUE
3 | bus_LV_1404-29_1_3_node_61 | 0.4 | n |  | TRUE
4 | bus_LV_1404-29_1_3_node_58 | 0.4 | n |  | TRUE
5 | bus_LV_1404-29_1_3_node_53 | 0.4 | n |  | TRUE
6 | bus_LV_1404-29_1_3_node_54 | 0.4 | n |  | TRUE
7 | bus_LV_1404-29_1_3_node_55 | 0.4 | n |  | TRUE
8 | bus_LV_1404-29_1_3_node_56 | 0.4 | n |  | TRUE
9 | bus_LV_1404-29_1_3_node_57 | 0.4 | n |  | TRUE
10 | bus_LV_1404-29_1_3_node_59 | 0.4 | n |  | TRUE
11 | bus_LV_1404-29_1_3_node_60 | 0.4 | n |  | TRUE
12 | bus_LV_1404-29_1_3_node_62 | 0.4 | n |  | TRUE
13 | bus_LV_1404-29_1_3_node_64 | 0.4 | n |  | TRUE
14 | bus_LV_1404-29_1_3_node_81 | 0.4 | n |  | TRUE
15 | bus_LV_1404-29_1_3_node_63 | 0.4 | n |  | TRUE
16 | bus_LV_1404-29_1_3_node_65 | 0.4 | n |  | TRUE
17 | bus_LV_1404-29_1_3_node_66 | 0.4 | n |  | TRUE
18 | bus_LV_1404-29_1_3_node_67 | 0.4 | n |  | TRUE
19 | bus_LV_1404-29_1_3_node_92 | 0.4 | n |  | TRUE
20 | bus_LV_1404-29_1_3_node_99 | 0.4 | n |  | TRUE
21 | bus_LV_1404-29_1_3_node_83 | 0.4 | n |  | TRUE
22 | bus_LV_1404-29_1_3_node_84 | 0.4 | n |  | TRUE
23 | bus_LV_1404-29_1_3_node_98 | 0.4 | n |  | TRUE
24 | bus_LV_1404-29_1_3_node_85 | 0.4 | n |  | TRUE
25 | bus_LV_1404-29_1_3_node_106 | 0.4 | n |  | TRUE
26 | bus_LV_1404-29_1_3_node_96 | 0.4 | n |  | TRUE
27 | bus_LV_1404-29_1_3_node_86 | 0.4 | n |  | TRUE
28 | bus_LV_1404-29_1_3_node_87 | 0.4 | n |  | TRUE
29 | bus_LV_1404-29_1_3_node_88 | 0.4 | n |  | TRUE
30 | bus_LV_1404-29_1_3_node_89 | 0.4 | n |  | TRUE
31 | bus_LV_1404-29_1_3_node_91 | 0.4 | n |  | TRUE
32 | bus_LV_1404-29_1_3_node_90 | 0.4 | n |  | TRUE
33 | bus_LV_1404-29_1_3_node_103 | 0.4 | n |  | TRUE
34 | bus_LV_1404-29_1_3_node_94 | 0.4 | n |  | TRUE
35 | bus_LV_1404-29_1_3_node_93 | 0.4 | n |  | TRUE
36 | bus_LV_1404-29_1_3_node_95 | 0.4 | n |  | TRUE
37 | bus_LV_1404-29_1_3_node_97 | 0.4 | n |  | TRUE
38 | bus_LV_1404-29_1_3_node_100 | 0.4 | n |  | TRUE
39 | bus_LV_1404-29_1_3_node_101 | 0.4 | n |  | TRUE
40 | bus_LV_1404-29_1_3_node_102 | 0.4 | n |  | TRUE
41 | bus_LV_1404-29_1_3_node_104 | 0.4 | n |  | TRUE
42 | bus_LV_1404-29_1_3_node_105 | 0.4 | n |  | TRUE
43 | bus_MV_140_0_node_23 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1404-29_1_3_load_58 | 4 | 0.00021156 | 5.3022e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1404-29_1_3_load_53 | 5 | 0.00021886 | 5.4852e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1404-29_1_3_load_54 | 6 | 0.00052654 | 0.00013196 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1404-29_1_3_load_55 | 7 | 0.00031009 | 7.7715e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1404-29_1_3_load_56 | 8 | 0.00015119 | 3.7893e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1404-29_1_3_load_59 | 10 | 0.00016436 | 4.1194e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1404-29_1_3_load_60 | 11 | 0.00015546 | 3.8962e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1404-29_1_3_load_62 | 12 | 0.00011713 | 2.9355e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1404-29_1_3_load_64 | 13 | 0.00044205 | 0.00011079 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1404-29_1_3_load_81 | 14 | 0.0002392 | 5.995e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1404-29_1_3_load_63 | 15 | 0.00035755 | 8.961e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1404-29_1_3_load_66 | 17 | 0.00012623 | 3.1637e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1404-29_1_3_load_67 | 18 | 0.00018899 | 4.7366e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1404-29_1_3_load_99 | 20 | 0.00010593 | 2.6548e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1404-29_1_3_load_83 | 21 | 0.0010255 | 0.00025702 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1404-29_1_3_load_85 | 24 | 0.00085797 | 0.00021503 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1404-29_1_3_load_106 | 25 | 0.0015151 | 0.00037973 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1404-29_1_3_load_96 | 26 | 0.00049332 | 0.00012364 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1404-29_1_3_load_86 | 27 | 0.0089497 | 0.002243 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1404-29_1_3_load_87 | 28 | 0.012937 | 0.0032422 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1404-29_1_3_load_88 | 29 | 0.01641 | 0.0041127 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1404-29_1_3_load_89 | 30 | 0.01218 | 0.0030526 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1404-29_1_3_load_103 | 33 | 0.0060429 | 0.0015145 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1404-29_1_3_load_93 | 35 | 0.001423 | 0.00035664 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1404-29_1_3_load_95 | 36 | 0.0028639 | 0.00071777 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1404-29_1_3_load_97 | 37 | 0.00044859 | 0.00011243 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1404-29_1_3_load_100 | 38 | 0.0080153 | 0.0020088 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1404-29_1_3_load_101 | 39 | 0.0054331 | 0.0013617 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1404-29_1_3_load_102 | 40 | 0.030974 | 0.0077627 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1404-29_1_3_load_104 | 41 | 0.0005273 | 0.00013215 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1404-29_1_3_load_105 | 42 | 0.00057422 | 0.00014391 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 40 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1404-29_1_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.044883 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1404-29_1_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.06802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1404-29_1_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.011369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1404-29_1_3_line_3 | NAYY 4x150 SE | 1 | 4 | 0.042957 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1404-29_1_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.010364 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1404-29_1_3_line_5 | NAYY 4x150 SE | 3 | 14 | 0.072544 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1404-29_1_3_line_6 | NAYY 4x150 SE | 4 | 8 | 0.0057198 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1404-29_1_3_line_7 | NAYY 4x150 SE | 5 | 6 | 0.071541 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1404-29_1_3_line_8 | NAYY 4x150 SE | 7 | 8 | 0.043834 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1404-29_1_3_line_9 | NAYY 4x150 SE | 7 | 9 | 0.17403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1404-29_1_3_line_10 | NAYY 4x150 SE | 9 | 10 | 0.087393 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1404-29_1_3_line_11 | NAYY 4x150 SE | 9 | 11 | 0.039876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1404-29_1_3_line_12 | NAYY 4x150 SE | 10 | 12 | 0.0018218 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1404-29_1_3_line_13 | NAYY 4x150 SE | 11 | 13 | 0.027118 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1404-29_1_3_line_14 | NAYY 4x150 SE | 12 | 15 | 0.016531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1404-29_1_3_line_15 | NAYY 4x150 SE | 13 | 16 | 0.0038563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1404-29_1_3_line_16 | NAYY 4x150 SE | 16 | 17 | 0.00429 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1404-29_1_3_line_17 | NAYY 4x150 SE | 16 | 18 | 0.25707 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1404-29_1_3_line_18 | NAYY 4x150 SE | 18 | 19 | 0.25197 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1404-29_1_3_line_19 | NAYY 4x150 SE | 18 | 20 | 0.22602 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1404-29_1_3_line_20 | NAYY 4x150 SE | 19 | 32 | 0.16887 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1404-29_1_3_line_21 | NAYY 4x150 SE | 21 | 22 | 0.053177 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1404-29_1_3_line_22 | NAYY 4x150 SE | 22 | 23 | 0.092083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1404-29_1_3_line_23 | NAYY 4x150 SE | 23 | 26 | 0.13492 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1404-29_1_3_line_24 | NAYY 4x150 SE | 23 | 37 | 0.37416 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1404-29_1_3_line_25 | NAYY 4x150 SE | 24 | 25 | 0.080206 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
26 | LV_1404-29_1_3_line_26 | NAYY 4x150 SE | 24 | 26 | 0.11399 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
27 | LV_1404-29_1_3_line_27 | NAYY 4x150 SE | 25 | 42 | 0.013704 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
28 | LV_1404-29_1_3_line_28 | NAYY 4x150 SE | 26 | 31 | 0.22109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
29 | LV_1404-29_1_3_line_29 | NAYY 4x150 SE | 27 | 28 | 0.0062763 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1404-29_1_3_line_30 | NAYY 4x150 SE | 27 | 29 | 0.085817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1404-29_1_3_line_31 | NAYY 4x150 SE | 28 | 30 | 0.15449 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
32 | LV_1404-29_1_3_line_32 | NAYY 4x150 SE | 30 | 31 | 0.018882 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
33 | LV_1404-29_1_3_line_33 | NAYY 4x150 SE | 31 | 34 | 0.031262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1404-29_1_3_line_34 | NAYY 4x150 SE | 32 | 33 | 0.19518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1404-29_1_3_line_35 | NAYY 4x150 SE | 33 | 39 | 0.008977 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1404-29_1_3_line_36 | NAYY 4x150 SE | 34 | 35 | 0.041009 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1404-29_1_3_line_37 | NAYY 4x150 SE | 35 | 36 | 0.04405 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1404-29_1_3_line_38 | NAYY 4x150 SE | 38 | 39 | 0.017485 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1404-29_1_3_line_39 | NAYY 4x150 SE | 38 | 40 | 0.19509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1404-29_1_3_line_40 | NAYY 4x150 SE | 40 | 41 | 0.020012 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
41 | LV_1404-29_1_3_line_41 | NAYY 4x150 SE | 41 | 42 | 0.0050428 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1404-29_1_3_trafo_102 | 0.25 MVA 20/0.4 kV | 43 | 40 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25
0 | 2664465.1286 | 1193416.8092 | 2664475.8897 | 1193418.3149 | 2664500.0662 | 1193442.3561
1 | 2664516.3139 | 1193508.2697 | 2664512.2552 | 1193490.9714 | 2664509.4411 | 1193472.7527 | 2664505.4468 | 1193458.6569 | 2664500.0662 | 1193442.3561
2 | 2664465.1286 | 1193416.8092 | 2664465.2383 | 1193415.1205 | 2664458.5379 | 1193408.1221
3 | 2664465.1286 | 1193416.8092 | 2664458.2981 | 1193420.4711 | 2664456.1853 | 1193426.9744 | 2664458.8927 | 1193441.6788 | 2664459.9876 | 1193455.0518
4 | 2664516.3139 | 1193508.2697 | 2664526.6312 | 1193507.2833
5 | 2664458.5379 | 1193408.1221 | 2664453.877 | 1193402.1128 | 2664450.9272 | 1193394.3432 | 2664444.299 | 1193372.1477 | 2664442.9515 | 1193364.929 | 2664440.6825 | 1193344.1925 | 2664439.699 | 1193339.0244
6 | 2664459.9876 | 1193455.0518 | 2664460.4543 | 1193460.7525
7 | 2664564.4194 | 1193551.636 | 2664560.7341 | 1193552.0076 | 2664557.9246 | 1193547.4969 | 2664560.4633 | 1193538.9637 | 2664561.3875 | 1193529.6015 | 2664554.5428 | 1193519.7442 | 2664539.9544 | 1193507.7687 | 2664527.2854 | 1193507.2207 | 2664526.6312 | 1193507.2833
8 | 2664462.3608 | 1193504.479 | 2664462.8665 | 1193490.2166 | 2664460.4543 | 1193460.7525
9 | 2664466.8642 | 1193677.269 | 2664469.0671 | 1193673.7017 | 2664459.341 | 1193589.6367 | 2664462.3608 | 1193504.479
10 | 2664466.8642 | 1193677.269 | 2664465.3205 | 1193679.776 | 2664416.0118 | 1193702.8809 | 2664410.2009 | 1193710.9675 | 2664412.1248 | 1193721.9946 | 2664417.6598 | 1193728.8918
11 | 2664466.8642 | 1193677.269 | 2664473.4107 | 1193716.6037
12 | 2664417.6598 | 1193728.8918 | 2664418.8 | 1193730.3126
13 | 2664473.4107 | 1193716.6037 | 2664477.8627 | 1193743.3534
14 | 2664418.8 | 1193730.3126 | 2664423.0145 | 1193735.5642 | 2664420.0559 | 1193744.9045
15 | 2664478.4958 | 1193747.1573 | 2664477.8627 | 1193743.3534
16 | 2664478.4958 | 1193747.1573 | 2664481.6116 | 1193750.1149
17 | 2664478.4958 | 1193747.1573 | 2664477.7636 | 1193776.9002 | 2664491.1742 | 1193860.6047 | 2664496.6639 | 1193919.754 | 2664496.4119 | 1193981.2873 | 2664497.8215 | 1194002.8458
18 | 2664483.4836 | 1194251.5839 | 2664485.8799 | 1194230.7753 | 2664494.5594 | 1194210.3347 | 2664496.9567 | 1194196.508 | 2664495.3722 | 1194184.4283 | 2664498.4979 | 1194159.5919 | 2664497.2125 | 1194145.9256 | 2664494.4948 | 1194102.5376 | 2664494.8552 | 1194061.3396 | 2664493.4936 | 1194043.4366 | 2664494.6191 | 1194026.6945 | 2664498.5185 | 1194013.5066 | 2664497.8215 | 1194002.8458
19 | 2664497.8215 | 1194002.8458 | 2664719.6331 | 1193959.4498
20 | 2664358.5136 | 1194144.2981 | 2664367.9067 | 1194157.3735 | 2664390.1335 | 1194181.0486 | 2664403.6123 | 1194189.7877 | 2664435.464 | 1194204.9727 | 2664452.4063 | 1194214.772 | 2664469.7705 | 1194227.1441 | 2664479.034 | 1194239.4733 | 2664483.4836 | 1194251.5839
21 | 2663931.6844 | 1193574.8576 | 2663961.9232 | 1193574.5138 | 2663983.7262 | 1193567.3935
22 | 2663870.0643 | 1193643.284 | 2663931.6844 | 1193574.8576
23 | 2663870.0643 | 1193643.284 | 2663877.413 | 1193656.7036 | 2663887.1428 | 1193680.5325 | 2663897.8291 | 1193714.6887 | 2663914.7359 | 1193770.2621
24 | 2663870.0643 | 1193643.284 | 2663863.6261 | 1193644.5272 | 2663858.5558 | 1193641.1378 | 2663852.5601 | 1193635.1925 | 2663842.1384 | 1193626.1872 | 2663831.0521 | 1193618.7535 | 2663822.6627 | 1193613.5722 | 2663814.4102 | 1193609.8375 | 2663808.0113 | 1193611.6704 | 2663804.2661 | 1193619.1015 | 2663802.9094 | 1193626.2467 | 2663806.0297 | 1193633.1062 | 2663815.4693 | 1193639.8664 | 2663840.8311 | 1193656.5577 | 2663844.4358 | 1193664.4452 | 2663847.5523 | 1193675.9295 | 2663862.4814 | 1193726.7518 | 2663864.865 | 1193737.6391 | 2663867.615 | 1193756.3238 | 2663869.1855 | 1193774.8403 | 2663869.081 | 1193798.1861 | 2663867.4112 | 1193816.8125 | 2663867.4657 | 1193838.8371 | 2663865.2038 | 1193844.3939 | 2663858.4737 | 1193853.7165 | 2663834.8081 | 1193874.5651
25 | 2664078.7882 | 1193814.5708 | 2664058.9329 | 1193793.6013 | 2664027.4271 | 1193753.0806
26 | 2663914.7359 | 1193770.2621 | 2664027.4271 | 1193753.0806
27 | 2664078.7882 | 1193814.5708 | 2664088.2101 | 1193824.5215
28 | 2663923.5943 | 1193982.3979 | 2663936.7671 | 1193950.709 | 2663943.1867 | 1193934.0678 | 2663946.6535 | 1193918.4624 | 2663948.4001 | 1193904.7953 | 2663947.6071 | 1193887.0098 | 2663944.1517 | 1193868.7511 | 2663923.842 | 1193800.1942 | 2663914.7359 | 1193770.2621
29 | 2664059.658 | 1194093.9327 | 2664053.9965 | 1194091.2236
30 | 2664059.658 | 1194093.9327 | 2664080.6591 | 1194103.9819 | 2664119.5776 | 1194121.2199 | 2664139.3624 | 1194123.937
31 | 2664053.9965 | 1194091.2236 | 2664031.5116 | 1194080.4643 | 2663993.8834 | 1194058.6825 | 2663986.4763 | 1194053.6448 | 2663970.5007 | 1194035.2966 | 2663938.6943 | 1194004.9835 | 2663935.1111 | 1194000.8205 | 2663933.7854 | 1193997.7208
32 | 2663923.5943 | 1193982.3979 | 2663928.5219 | 1193986.275 | 2663930.0477 | 1193988.9818 | 2663933.7854 | 1193997.7208
33 | 2663923.5943 | 1193982.3979 | 2663920.0502 | 1193993.8334 | 2663918.9123 | 1194003.3267 | 2663919.22 | 1194013.0468
34 | 2664358.5136 | 1194144.2981 | 2664288.9357 | 1193961.9437
35 | 2664288.9357 | 1193961.9437 | 2664284.2713 | 1193954.2736
36 | 2663919.22 | 1194013.0468 | 2663908.4062 | 1194012.2864 | 2663904.1307 | 1194008.7165 | 2663902.3514 | 1194003.3499 | 2663901.3952 | 1193995.1238 | 2663899.7835 | 1193984.5834
37 | 2663896.7405 | 1193940.7312 | 2663897.2422 | 1193967.9636 | 2663899.7835 | 1193984.5834
38 | 2664270.8319 | 1193943.7963 | 2664281.7015 | 1193950.0479 | 2664284.2713 | 1193954.2736
39 | 2664270.8319 | 1193943.7963 | 2664249.1998 | 1193931.3547 | 2664219.621 | 1193906.5894 | 2664175.4681 | 1193867.8042 | 2664109.9596 | 1193838.9742 | 2664108.9109 | 1193838.3553
40 | 2664108.9109 | 1193838.3553 | 2664091.6773 | 1193828.1832
41 | 2664091.6773 | 1193828.1832 | 2664091.6773 | 1193828.1832 | 2664088.2101 | 1193824.5215

## bus_geodata
| x | y | coords
0 | 2664500.0662 | 1193442.3561
1 | 2664465.1286 | 1193416.8092
2 | 2664516.3139 | 1193508.2697
3 | 2664458.5379 | 1193408.1221
4 | 2664459.9876 | 1193455.0518
5 | 2664526.6312 | 1193507.2833
6 | 2664564.4194 | 1193551.636
7 | 2664462.3608 | 1193504.479
8 | 2664460.4543 | 1193460.7525
9 | 2664466.8642 | 1193677.269
10 | 2664417.6598 | 1193728.8918
11 | 2664473.4107 | 1193716.6037
12 | 2664418.8 | 1193730.3126
13 | 2664477.8627 | 1193743.3534
14 | 2664439.699 | 1193339.0244
15 | 2664420.0559 | 1193744.9045
16 | 2664478.4958 | 1193747.1573
17 | 2664481.6116 | 1193750.1149
18 | 2664497.8215 | 1194002.8458
19 | 2664483.4836 | 1194251.5839
20 | 2664719.6331 | 1193959.4498
21 | 2663983.7262 | 1193567.3935
22 | 2663931.6844 | 1193574.8576
23 | 2663870.0643 | 1193643.284
24 | 2664027.4271 | 1193753.0806
25 | 2664078.7882 | 1193814.5708
26 | 2663914.7359 | 1193770.2621
27 | 2664059.658 | 1194093.9327
28 | 2664053.9965 | 1194091.2236
29 | 2664139.3624 | 1194123.937
30 | 2663933.7854 | 1193997.7208
31 | 2663923.5943 | 1193982.3979
32 | 2664358.5136 | 1194144.2981
33 | 2664288.9357 | 1193961.9437
34 | 2663919.22 | 1194013.0468
35 | 2663899.7835 | 1193984.5834
36 | 2663896.7405 | 1193940.7312
37 | 2663834.8081 | 1193874.5651
38 | 2664270.8319 | 1193943.7963
39 | 2664284.2713 | 1193954.2736
40 | 2664108.9109 | 1193838.3552
41 | 2664091.6773 | 1193828.1832
42 | 2664088.2101 | 1193824.5215
43 | 2664288.9357 | 1193961.9437

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9882 | -0.084614 | 0 | 0
1 | 0.98825 | -0.084265 | 0 | 0
2 | 0.98813 | -0.08514 | 0 | 0
3 | 0.98825 | -0.084293 | 0 | 0
4 | 0.98831 | -0.08382 | 0.00021156 | 5.3022e-05
5 | 0.98812 | -0.08522 | 0.00021886 | 5.4852e-05
6 | 0.98806 | -0.085607 | 0.00052654 | 0.00013196
7 | 0.98841 | -0.08313 | 0.00031009 | 7.7715e-05
8 | 0.98832 | -0.083748 | 0.00015119 | 3.7893e-05
9 | 0.98882 | -0.080107 | 0 | 0
10 | 0.98874 | -0.080682 | 0.00016436 | 4.1194e-05
11 | 0.98895 | -0.079146 | 0.00015546 | 3.8962e-05
12 | 0.98874 | -0.080691 | 0.00011713 | 2.9355e-05
13 | 0.98905 | -0.078449 | 0.00044205 | 0.00011079
14 | 0.98822 | -0.084473 | 0.0002392 | 5.995e-05
15 | 0.98873 | -0.080751 | 0.00035755 | 8.961e-05
16 | 0.98907 | -0.078332 | 0 | 0
17 | 0.98906 | -0.078338 | 0.00012623 | 3.1637e-05
18 | 0.99018 | -0.070206 | 0.00018899 | 4.7366e-05
19 | 0.99139 | -0.061386 | 0 | 0
20 | 0.99015 | -0.070475 | 0.00010593 | 2.6548e-05
21 | 0.98973 | -0.071376 | 0.0010255 | 0.00025702
22 | 0.98981 | -0.070819 | 0 | 0
23 | 0.98994 | -0.069848 | 0 | 0
24 | 0.99495 | -0.034894 | 0.00085797 | 0.00021503
25 | 0.99831 | -0.011614 | 0.0015151 | 0.00037973
26 | 0.99023 | -0.067746 | 0.00049332 | 0.00012364
27 | 0.97615 | -0.16747 | 0.0089497 | 0.002243
28 | 0.97638 | -0.1658 | 0.012937 | 0.0032422
29 | 0.97409 | -0.18225 | 0.01641 | 0.0041127
30 | 0.9807 | -0.13495 | 0.01218 | 0.0030526
31 | 0.9814 | -0.13 | 0 | 0
32 | 0.99219 | -0.055452 | 0 | 0
33 | 0.99312 | -0.04857 | 0.0060429 | 0.0015145
34 | 0.9812 | -0.13139 | 0 | 0
35 | 0.98095 | -0.13322 | 0.001423 | 0.00035664
36 | 0.98076 | -0.13453 | 0.0028639 | 0.00071777
37 | 0.9897 | -0.071627 | 0.00044859 | 0.00011243
38 | 0.99361 | -0.045058 | 0.0080153 | 0.0020088
39 | 0.99324 | -0.047704 | 0.0054331 | 0.0013617
40 | 1 | 0 | -0.085254 | -0.021306
41 | 0.99912 | -0.0060375 | 0.0005273 | 0.00013215
42 | 0.9989 | -0.0075472 | 0.00057422 | 0.00014391
43 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00074549 | -0.00018493 | 0.00074553 | 0.00018437 | 3.5243e-08 | -5.6149e-07 | 0.0011219 | 0.0011217 | 0.0011219 | 0.9882 | -0.084614 | 0.98825 | -0.084265 | 0.41551
1 | 0.00074549 | 0.00018493 | -0.00074544 | -0.00018578 | 5.3435e-08 | -8.5083e-07 | 0.0011219 | 0.0011222 | 0.0011222 | 0.9882 | -0.084614 | 0.98813 | -0.08514 | 0.41562
2 | 0.00023921 | 5.8877e-05 | -0.00023921 | -5.9022e-05 | 9.1852e-10 | -1.4531e-07 | 0.0003598 | 0.00035985 | 0.00035985 | 0.98825 | -0.084265 | 0.98825 | -0.084293 | 0.13328
3 | -0.00098473 | -0.00024324 | 0.00098479 | 0.00024272 | 5.8823e-08 | -5.2781e-07 | 0.0014815 | 0.0014813 | 0.0014815 | 0.98825 | -0.084265 | 0.98831 | -0.08382 | 0.54869
4 | 0.00074544 | 0.00018578 | -0.00074543 | -0.00018591 | 8.1445e-09 | -1.2963e-07 | 0.0011222 | 0.0011222 | 0.0011222 | 0.98813 | -0.08514 | 0.98812 | -0.08522 | 0.41564
5 | 0.00023921 | 5.9022e-05 | -0.0002392 | -5.995e-05 | 5.8671e-09 | -9.2721e-07 | 0.00035985 | 0.00036018 | 0.00036018 | 0.98825 | -0.084293 | 0.98822 | -0.084473 | 0.1334
6 | -0.0011964 | -0.00029574 | 0.0011964 | 0.00029567 | 1.1561e-08 | -6.885e-08 | 0.0017998 | 0.0017998 | 0.0017998 | 0.98831 | -0.08382 | 0.98832 | -0.083748 | 0.66659
7 | 0.00052657 | 0.00013106 | -0.00052654 | -0.00013196 | 2.8059e-08 | -9.0556e-07 | 0.00079264 | 0.00079296 | 0.00079296 | 0.98812 | -0.08522 | 0.98806 | -0.085607 | 0.29369
8 | 0.0013477 | 0.00033304 | -0.0013476 | -0.00033356 | 1.1242e-07 | -5.1853e-07 | 0.0020272 | 0.0020274 | 0.0020274 | 0.98841 | -0.08313 | 0.98832 | -0.083748 | 0.75089
9 | -0.0016578 | -0.00041076 | 0.0016584 | 0.00040879 | 6.7527e-07 | -1.9717e-06 | 0.002494 | 0.0024933 | 0.002494 | 0.98841 | -0.08313 | 0.98882 | -0.080107 | 0.92372
10 | 0.0006391 | 0.00015882 | -0.00063905 | -0.00015993 | 5.0411e-08 | -1.1016e-06 | 0.00096126 | 0.00096166 | 0.00096166 | 0.98882 | -0.080107 | 0.98874 | -0.080682 | 0.35617
11 | -0.0022975 | -0.00056761 | 0.0022978 | 0.00056721 | 2.9692e-07 | -3.9738e-07 | 0.0034545 | 0.0034543 | 0.0034545 | 0.98882 | -0.080107 | 0.98895 | -0.079146 | 1.2795
12 | 0.00047468 | 0.00011873 | -0.00047468 | -0.00011876 | 5.7994e-10 | -2.3142e-08 | 0.0007143 | 0.0007143 | 0.0007143 | 0.98874 | -0.080682 | 0.98874 | -0.080691 | 0.26456
13 | -0.0024533 | -0.00060618 | 0.0024535 | 0.00060592 | 2.3018e-07 | -2.5945e-07 | 0.0036882 | 0.0036881 | 0.0036882 | 0.98895 | -0.079146 | 0.98905 | -0.078449 | 1.366
14 | 0.00035755 | 8.94e-05 | -0.00035755 | -8.961e-05 | 2.9865e-09 | -2.1087e-07 | 0.00053803 | 0.0005381 | 0.0005381 | 0.98874 | -0.080691 | 0.98873 | -0.080751 | 0.1993
15 | -0.0028956 | -0.0007167 | 0.0028956 | 0.00071667 | 4.56e-08 | -3.1952e-08 | 0.0043532 | 0.0043532 | 0.0043532 | 0.98905 | -0.078449 | 0.98907 | -0.078332 | 1.6123
16 | 0.00012623 | 3.1582e-05 | -0.00012623 | -3.1637e-05 | 9.6549e-11 | -5.502e-08 | 0.0001899 | 0.00018992 | 0.00018992 | 0.98907 | -0.078332 | 0.98906 | -0.078338 | 0.070339
17 | -0.0030218 | -0.00074826 | 0.0030252 | 0.00074623 | 3.3099e-06 | -2.0299e-06 | 0.0045431 | 0.0045419 | 0.0045431 | 0.98907 | -0.078332 | 0.99018 | -0.070206 | 1.6826
18 | -0.0033201 | -0.00081723 | 0.003324 | 0.00081549 | 3.9049e-06 | -1.7432e-06 | 0.0049841 | 0.004983 | 0.0049841 | 0.99018 | -0.070206 | 0.99139 | -0.061386 | 1.846
19 | 0.00010593 | 2.3642e-05 | -0.00010593 | -2.6548e-05 | 3.5515e-09 | -2.9058e-06 | 0.00015821 | 0.00015919 | 0.00015919 | 0.99018 | -0.070206 | 0.99015 | -0.070475 | 0.058959
20 | -0.003324 | -0.00081549 | 0.0033266 | 0.00081432 | 2.6161e-06 | -1.1731e-06 | 0.004983 | 0.0049822 | 0.004983 | 0.99139 | -0.061386 | 0.99219 | -0.055452 | 1.8455
21 | -0.0010255 | -0.00025702 | 0.0010256 | 0.00025637 | 7.8871e-08 | -6.5311e-07 | 0.0015418 | 0.0015416 | 0.0015418 | 0.98973 | -0.071376 | 0.98981 | -0.070819 | 0.57105
22 | -0.0010256 | -0.00025637 | 0.0010257 | 0.00025524 | 1.3652e-07 | -1.1312e-06 | 0.0015416 | 0.0015412 | 0.0015416 | 0.98981 | -0.070819 | 0.98994 | -0.069848 | 0.57096
23 | -0.0014744 | -0.0003629 | 0.0014749 | 0.00036132 | 4.1254e-07 | -1.5764e-06 | 0.0022139 | 0.0022133 | 0.0022139 | 0.98994 | -0.069848 | 0.99023 | -0.067746 | 0.81998
24 | 0.0004487 | 0.00010766 | -0.00044859 | -0.00011243 | 1.0594e-07 | -4.7686e-06 | 0.00067279 | 0.00067446 | 0.00067446 | 0.98994 | -0.069848 | 0.9897 | -0.071627 | 0.2498
25 | -0.058576 | -0.014789 | 0.058768 | 0.014861 | 0.00019222 | 7.1839e-05 | 0.087643 | 0.087642 | 0.087643 | 0.99495 | -0.034894 | 0.99831 | -0.011614 | 16.2302
26 | 0.057718 | 0.014574 | -0.057453 | -0.014475 | 0.00026526 | 9.9074e-05 | 0.08636 | 0.086361 | 0.086361 | 0.99495 | -0.034894 | 0.99023 | -0.067746 | 15.9928
27 | -0.060283 | -0.01524 | 0.060318 | 0.015253 | 3.4555e-05 | 1.2932e-05 | 0.089901 | 0.0899 | 0.089901 | 0.99831 | -0.011614 | 0.9989 | -0.0075472 | 16.6483
28 | 0.055485 | 0.01399 | -0.055005 | -0.013811 | 0.00047989 | 0.00017893 | 0.083406 | 0.083408 | 0.083408 | 0.99023 | -0.067746 | 0.9814 | -0.13 | 15.446
29 | -0.025393 | -0.0063676 | 0.025399 | 0.0063697 | 5.8686e-06 | 2.1787e-06 | 0.03871 | 0.03871 | 0.03871 | 0.97615 | -0.16747 | 0.97638 | -0.1658 | 14.337
30 | 0.016443 | 0.0041246 | -0.01641 | -0.0041127 | 3.365e-05 | 1.1872e-05 | 0.025067 | 0.025068 | 0.025068 | 0.97615 | -0.16747 | 0.97409 | -0.18225 | 9.2843
31 | -0.038336 | -0.009612 | 0.0385 | 0.0096714 | 0.00016454 | 5.9401e-05 | 0.058426 | 0.058424 | 0.058426 | 0.97638 | -0.1658 | 0.9807 | -0.13495 | 10.8196
32 | -0.05068 | -0.012724 | 0.050715 | 0.012737 | 3.4843e-05 | 1.2924e-05 | 0.076905 | 0.076905 | 0.076905 | 0.9807 | -0.13495 | 0.9814 | -0.13 | 14.2417
33 | 0.0042893 | 0.0010739 | -0.0042885 | -0.0010739 | 8.2502e-07 | -7.7625e-08 | 0.0065032 | 0.0065033 | 0.0065033 | 0.9814 | -0.13 | 0.9812 | -0.13139 | 2.4086
34 | -0.0033266 | -0.00081432 | 0.0033296 | 0.00081296 | 3.0226e-06 | -1.3606e-06 | 0.0049822 | 0.0049813 | 0.0049822 | 0.99219 | -0.055452 | 0.99312 | -0.04857 | 1.8453
35 | -0.0093725 | -0.0023275 | 0.0093736 | 0.0023278 | 1.1035e-06 | 3.0825e-07 | 0.014036 | 0.014035 | 0.014036 | 0.99312 | -0.04857 | 0.99324 | -0.047704 | 5.1983
36 | 0.0042885 | 0.0010739 | -0.0042874 | -0.001074 | 1.0823e-06 | -1.0157e-07 | 0.0065033 | 0.0065035 | 0.0065035 | 0.9812 | -0.13139 | 0.98095 | -0.13322 | 2.4087
37 | 0.0028644 | 0.00071741 | -0.0028639 | -0.00071777 | 5.1894e-07 | -3.564e-07 | 0.0043449 | 0.0043451 | 0.0043451 | 0.98095 | -0.13322 | 0.98076 | -0.13453 | 1.6093
38 | 0.014812 | 0.0036913 | -0.014807 | -0.0036894 | 5.365e-06 | 1.8371e-06 | 0.022175 | 0.022175 | 0.022175 | 0.99361 | -0.045058 | 0.99324 | -0.047704 | 8.213
39 | -0.022827 | -0.0057001 | 0.02297 | 0.0057522 | 0.00014221 | 5.2151e-05 | 0.034179 | 0.034178 | 0.034179 | 0.99361 | -0.045058 | 1 | 0 | 12.6587
40 | 0.061485 | 0.015554 | -0.061432 | -0.015534 | 5.232e-05 | 1.9599e-05 | 0.091541 | 0.091541 | 0.091541 | 1 | 0 | 0.99912 | -0.0060375 | 16.9521
41 | 0.060905 | 0.015402 | -0.060892 | -0.015397 | 1.2959e-05 | 4.8522e-06 | 0.090756 | 0.090756 | 0.090756 | 0.99912 | -0.0060375 | 0.9989 | -0.0075472 | 16.8066

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.11623 | 0.029069

## res_load
| p_mw | q_mvar
0 | 0.00021156 | 5.3022e-05
1 | 0.00021886 | 5.4852e-05
2 | 0.00052654 | 0.00013196
3 | 0.00031009 | 7.7715e-05
4 | 0.00015119 | 3.7893e-05
5 | 0.00016436 | 4.1194e-05
6 | 0.00015546 | 3.8962e-05
7 | 0.00011713 | 2.9355e-05
8 | 0.00044205 | 0.00011079
9 | 0.0002392 | 5.995e-05
10 | 0.00035755 | 8.961e-05
11 | 0.00012623 | 3.1637e-05
12 | 0.00018899 | 4.7366e-05
13 | 0.00010593 | 2.6548e-05
14 | 0.0010255 | 0.00025702
15 | 0.00085797 | 0.00021503
16 | 0.0015151 | 0.00037973
17 | 0.00049332 | 0.00012364
18 | 0.0089497 | 0.002243
19 | 0.012937 | 0.0032422
20 | 0.01641 | 0.0041127
21 | 0.01218 | 0.0030526
22 | 0.0060429 | 0.0015145
23 | 0.001423 | 0.00035664
24 | 0.0028639 | 0.00071777
25 | 0.00044859 | 0.00011243
26 | 0.0080153 | 0.0020088
27 | 0.0054331 | 0.0013617
28 | 0.030974 | 0.0077627
29 | 0.0005273 | 0.00013215
30 | 0.00057422 | 0.00014391

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1