## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1404-2_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1404-2_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1404-2_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1404-2_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1404-2_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1404-2_0_3_node_14 | 0.4 | n |  | TRUE
6 | bus_LV_1404-2_0_3_node_8 | 0.4 | n |  | TRUE
7 | bus_LV_1404-2_0_3_node_15 | 0.4 | n |  | TRUE
8 | bus_LV_1404-2_0_3_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_1404-2_0_3_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_1404-2_0_3_node_19 | 0.4 | n |  | TRUE
11 | bus_LV_1404-2_0_3_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_1404-2_0_3_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_1404-2_0_3_node_12 | 0.4 | n |  | TRUE
14 | bus_LV_1404-2_0_3_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_1404-2_0_3_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_1404-2_0_3_node_20 | 0.4 | n |  | TRUE
17 | bus_LV_1404-2_0_3_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_1404-2_0_3_node_21 | 0.4 | n |  | TRUE
19 | bus_LV_1404-2_0_3_node_32 | 0.4 | n |  | TRUE
20 | bus_LV_1404-2_0_3_node_27 | 0.4 | n |  | TRUE
21 | bus_LV_1404-2_0_3_node_22 | 0.4 | n |  | TRUE
22 | bus_LV_1404-2_0_3_node_28 | 0.4 | n |  | TRUE
23 | bus_LV_1404-2_0_3_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_1404-2_0_3_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_1404-2_0_3_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_1404-2_0_3_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_1404-2_0_3_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_1404-2_0_3_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_1404-2_0_3_node_26 | 0.4 | n |  | TRUE
30 | bus_LV_1404-2_0_3_node_29 | 0.4 | n |  | TRUE
31 | bus_LV_1404-2_0_3_node_30 | 0.4 | n |  | TRUE
32 | bus_LV_1404-2_0_3_node_31 | 0.4 | n |  | TRUE
33 | bus_MV_141_0_node_117 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1404-2_0_3_load_0 | 0 | 0.02225 | 0.0055764 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1404-2_0_3_load_1 | 1 | 0.012415 | 0.0031116 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1404-2_0_3_load_2 | 2 | 0.012351 | 0.0030954 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1404-2_0_3_load_4 | 4 | 0.0054677 | 0.0013703 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1404-2_0_3_load_14 | 5 | 0.0072797 | 0.0018245 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1404-2_0_3_load_15 | 7 | 0.0022678 | 0.00056837 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1404-2_0_3_load_9 | 8 | 0.0030332 | 0.00076018 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1404-2_0_3_load_7 | 9 | 0.018081 | 0.0045314 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1404-2_0_3_load_5 | 11 | 0.019174 | 0.0048055 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1404-2_0_3_load_6 | 12 | 0.017137 | 0.0042948 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1404-2_0_3_load_12 | 13 | 0.0029347 | 0.0007355 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1404-2_0_3_load_10 | 14 | 0.018035 | 0.00452 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1404-2_0_3_load_11 | 15 | 0.0030328 | 0.00076008 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1404-2_0_3_load_13 | 17 | 0.0029351 | 0.00073559 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1404-2_0_3_load_21 | 18 | 0.0056887 | 0.0014257 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1404-2_0_3_load_32 | 19 | 0.0084924 | 0.0021284 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1404-2_0_3_load_27 | 20 | 0.0037887 | 0.00094953 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1404-2_0_3_load_22 | 21 | 0.0027245 | 0.00068283 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1404-2_0_3_load_28 | 22 | 0.004081 | 0.0010228 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1404-2_0_3_load_18 | 23 | 0.0033387 | 0.00083676 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1404-2_0_3_load_16 | 24 | 0.0026945 | 0.0006753 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1404-2_0_3_load_17 | 25 | 0.0026351 | 0.00066042 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1404-2_0_3_load_23 | 26 | 0.0025384 | 0.00063618 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1404-2_0_3_load_24 | 27 | 0.0030201 | 0.00075692 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1404-2_0_3_load_25 | 28 | 0.0030143 | 0.00075547 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1404-2_0_3_load_26 | 29 | 0.022821 | 0.0057194 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1404-2_0_3_load_29 | 30 | 0.0041168 | 0.0010318 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1404-2_0_3_load_31 | 32 | 0.0018968 | 0.00047537 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 5 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1404-2_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.026051 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1404-2_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0076921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1404-2_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.033131 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1404-2_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.035924 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1404-2_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.008813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
5 | LV_1404-2_0_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.002104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
6 | LV_1404-2_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.0051194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1404-2_0_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.027885 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1404-2_0_3_line_8 | NAYY 4x150 SE | 6 | 9 | 0.011324 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1404-2_0_3_line_9 | NAYY 4x150 SE | 7 | 10 | 0.016294 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1404-2_0_3_line_10 | NAYY 4x150 SE | 8 | 13 | 0.011019 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1404-2_0_3_line_11 | NAYY 4x150 SE | 9 | 11 | 0.021985 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1404-2_0_3_line_12 | NAYY 4x150 SE | 10 | 22 | 0.013438 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1404-2_0_3_line_13 | NAYY 4x150 SE | 10 | 23 | 0.015501 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1404-2_0_3_line_14 | NAYY 4x150 SE | 11 | 12 | 0.0338 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1404-2_0_3_line_15 | NAYY 4x150 SE | 13 | 14 | 0.0018283 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1404-2_0_3_line_16 | NAYY 4x150 SE | 14 | 15 | 0.022671 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1404-2_0_3_line_17 | NAYY 4x150 SE | 14 | 16 | 0.035831 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1404-2_0_3_line_18 | NAYY 4x150 SE | 15 | 17 | 0.011248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1404-2_0_3_line_19 | NAYY 4x150 SE | 16 | 18 | 0.033802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1404-2_0_3_line_20 | NAYY 4x150 SE | 18 | 21 | 0.023395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1404-2_0_3_line_21 | NAYY 4x150 SE | 19 | 20 | 0.012804 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1404-2_0_3_line_22 | NAYY 4x150 SE | 20 | 29 | 0.0023531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1404-2_0_3_line_23 | NAYY 4x150 SE | 21 | 26 | 0.0090469 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1404-2_0_3_line_24 | NAYY 4x150 SE | 21 | 25 | 0.036559 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1404-2_0_3_line_25 | NAYY 4x150 SE | 22 | 30 | 0.0050126 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1404-2_0_3_line_26 | NAYY 4x150 SE | 24 | 25 | 0.017076 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1404-2_0_3_line_27 | NAYY 4x150 SE | 26 | 27 | 0.0038014 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1404-2_0_3_line_28 | NAYY 4x150 SE | 27 | 28 | 0.0046355 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1404-2_0_3_line_29 | NAYY 4x150 SE | 28 | 29 | 0.021124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1404-2_0_3_line_30 | NAYY 4x150 SE | 30 | 31 | 0.011563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1404-2_0_3_line_31 | NAYY 4x150 SE | 31 | 32 | 0.013274 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1404-2_0_3_trafo_14 | 0.25 MVA 20/0.4 kV | 33 | 5 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2662625.3595 | 1194427.8976 | 2662601.2463 | 1194418.0391
1 | 2662625.3595 | 1194427.8976 | 2662632.4795 | 1194430.8086
2 | 2662570.5798 | 1194405.5013 | 2662601.2463 | 1194418.0391
3 | 2662665.9221 | 1194433.0038 | 2662657.8193 | 1194437.5772 | 2662648.3575 | 1194437.3002 | 2662632.4795 | 1194430.8086
4 | 2662573.3573 | 1194397.1366 | 2662570.5798 | 1194405.5013
5 | 2662568.5669 | 1194404.8688 | 2662570.5798 | 1194405.5013
6 | 2662665.9221 | 1194433.0038 | 2662665.9221 | 1194433.0038 | 2662667.6179 | 1194428.1734
7 | 2662568.5669 | 1194404.8688 | 2662543.0984 | 1194393.5138
8 | 2662568.5669 | 1194404.8688 | 2662566.9852 | 1194410.3777 | 2662567.9869 | 1194415.8802 | 2662567.9869 | 1194415.8802
9 | 2662673.0152 | 1194412.7997 | 2662667.6179 | 1194428.1734
10 | 2662533.0344 | 1194389.0268 | 2662543.0984 | 1194393.5138
11 | 2662581.8966 | 1194432.4807 | 2662576.296 | 1194428.0075 | 2662571.7755 | 1194423.0463 | 2662567.9869 | 1194415.8802
12 | 2662673.0152 | 1194412.7997 | 2662682.8187 | 1194415.3705 | 2662686.0948 | 1194415.7879
13 | 2662673.0152 | 1194412.7997 | 2662664.4616 | 1194409.4748 | 2662658.6076 | 1194407.0815
14 | 2662581.8966 | 1194432.4807 | 2662585.4782 | 1194435.3411 | 2662595.2507 | 1194442.3363 | 2662611.0878 | 1194449.0423
15 | 2662533.0344 | 1194389.0268 | 2662531.3646 | 1194388.2822
16 | 2662510.6583 | 1194379.0504 | 2662531.3646 | 1194388.2822
17 | 2662531.3646 | 1194388.2822 | 2662540.8826 | 1194353.7385
18 | 2662510.6583 | 1194379.0504 | 2662504.1684 | 1194376.1569 | 2662500.4137 | 1194374.408
19 | 2662540.8826 | 1194353.7385 | 2662548.4285 | 1194347.0357 | 2662551.9418 | 1194345.5605 | 2662555.0936 | 1194345.1376 | 2662559.1045 | 1194346.358 | 2662569.0544 | 1194350.987 | 2662570.414 | 1194351.7352
20 | 2662591.5782 | 1194352.7124 | 2662591.5782 | 1194352.7124 | 2662587.9014 | 1194355.9758 | 2662580.7734 | 1194356.2348 | 2662575.4797 | 1194354.5229 | 2662570.414 | 1194351.7352
21 | 2662559.2124 | 1194325.1135 | 2662571.5917 | 1194328.3854
22 | 2662573.8667 | 1194328.9867 | 2662571.5917 | 1194328.3854
23 | 2662591.5782 | 1194352.7124 | 2662595.4579 | 1194346.8051 | 2662595.4786 | 1194344.8258
24 | 2662609.1428 | 1194384.7753 | 2662591.5782 | 1194352.7124
25 | 2662686.0948 | 1194415.7879 | 2662689.1886 | 1194416.1821 | 2662691.0779 | 1194416.3118
26 | 2662609.1428 | 1194384.7753 | 2662624.6872 | 1194391.843
27 | 2662595.4786 | 1194344.8258 | 2662595.5184 | 1194341.0246 | 2662595.5184 | 1194341.0246
28 | 2662592.9065 | 1194337.195 | 2662592.9065 | 1194337.195 | 2662595.5184 | 1194341.0246
29 | 2662592.9065 | 1194337.195 | 2662587.7977 | 1194333.8396 | 2662586.1912 | 1194332.2441 | 2662573.8667 | 1194328.9867
30 | 2662702.6275 | 1194416.5454 | 2662696.263 | 1194416.6676 | 2662691.0779 | 1194416.3118
31 | 2662702.6275 | 1194416.5454 | 2662706.8598 | 1194416.2673 | 2662710.9969 | 1194415.6214 | 2662715.6778 | 1194414.3696

## bus_geodata
| x | y | coords
0 | 2662625.3595 | 1194427.8976
1 | 2662601.2463 | 1194418.0391
2 | 2662632.4795 | 1194430.8086
3 | 2662570.5798 | 1194405.5013
4 | 2662665.9221 | 1194433.0038
5 | 2662573.3573 | 1194397.1366
6 | 2662568.5669 | 1194404.8688
7 | 2662667.6179 | 1194428.1734
8 | 2662543.0984 | 1194393.5138
9 | 2662567.9869 | 1194415.8802
10 | 2662673.0152 | 1194412.7997
11 | 2662581.8966 | 1194432.4807
12 | 2662611.0878 | 1194449.0423
13 | 2662533.0344 | 1194389.0268
14 | 2662531.3646 | 1194388.2822
15 | 2662510.6583 | 1194379.0504
16 | 2662540.8826 | 1194353.7385
17 | 2662500.4137 | 1194374.408
18 | 2662570.414 | 1194351.7352
19 | 2662559.2124 | 1194325.1135
20 | 2662571.5917 | 1194328.3854
21 | 2662591.5782 | 1194352.7124
22 | 2662686.0948 | 1194415.7879
23 | 2662658.6076 | 1194407.0815
24 | 2662624.6872 | 1194391.843
25 | 2662609.1428 | 1194384.7753
26 | 2662595.4786 | 1194344.8258
27 | 2662595.5184 | 1194341.0246
28 | 2662592.9065 | 1194337.195
29 | 2662573.8667 | 1194328.9867
30 | 2662691.0779 | 1194416.3118
31 | 2662702.6275 | 1194416.5454
32 | 2662715.6778 | 1194414.3696
33 | 2662570.5798 | 1194405.5013

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99379 | -0.043482 | 0.02225 | 0.0055764
1 | 0.99587 | -0.028827 | 0.012415 | 0.0031116
2 | 0.99342 | -0.046089 | 0.012351 | 0.0030954
3 | 0.99911 | -0.0061629 | 0 | 0
4 | 0.99232 | -0.053792 | 0.0054677 | 0.0013703
5 | 1 | 0 | -0.21238 | -0.053236
6 | 0.9989 | -0.0076548 | 0 | 0
7 | 0.99221 | -0.054607 | 0.0022678 | 0.00056837
8 | 0.99538 | -0.032122 | 0.0030332 | 0.00076018
9 | 0.99802 | -0.013822 | 0.018081 | 0.0045314
10 | 0.99189 | -0.056827 | 0 | 0
11 | 0.99688 | -0.021831 | 0.019174 | 0.0048055
12 | 0.99605 | -0.027654 | 0.017137 | 0.0042948
13 | 0.99404 | -0.0415 | 0.0029347 | 0.0007355
14 | 0.99383 | -0.043004 | 0.018035 | 0.00452
15 | 0.99363 | -0.044372 | 0.0030328 | 0.00076008
16 | 0.99085 | -0.063862 | 0 | 0
17 | 0.99359 | -0.044706 | 0.0029351 | 0.00073559
18 | 0.98804 | -0.083652 | 0.0056887 | 0.0014257
19 | 0.98396 | -0.11258 | 0.0084924 | 0.0021284
20 | 0.98412 | -0.11146 | 0.0037887 | 0.00094953
21 | 0.98629 | -0.096049 | 0.0027245 | 0.00068283
22 | 0.9917 | -0.058204 | 0.004081 | 0.0010228
23 | 0.99182 | -0.057353 | 0.0033387 | 0.00083676
24 | 0.98594 | -0.098522 | 0.0026945 | 0.0006753
25 | 0.98601 | -0.09805 | 0.0026351 | 0.00066042
26 | 0.98572 | -0.10011 | 0.0025384 | 0.00063618
27 | 0.98549 | -0.10171 | 0.0030201 | 0.00075692
28 | 0.98524 | -0.10353 | 0.0030143 | 0.00075547
29 | 0.98416 | -0.11116 | 0.022821 | 0.0057194
30 | 0.99166 | -0.05851 | 0.0041168 | 0.0010318
31 | 0.99162 | -0.058733 | 0 | 0
32 | 0.99159 | -0.058989 | 0.0018968 | 0.00047537
33 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.055813 | -0.013992 | 0.055926 | 0.014036 | 0.00011353 | 4.3328e-05 | 0.083571 | 0.083571 | 0.083571 | 0.99379 | -0.043482 | 0.99587 | -0.028827 | 30.9522
1 | 0.033563 | 0.0084158 | -0.033551 | -0.0084112 | 1.2123e-05 | 4.5629e-06 | 0.050255 | 0.050256 | 0.050256 | 0.99379 | -0.043482 | 0.99342 | -0.046089 | 18.6132
2 | -0.068342 | -0.017147 | 0.068557 | 0.01723 | 0.0002156 | 8.2491e-05 | 0.10212 | 0.10212 | 0.10212 | 0.99587 | -0.028827 | 0.99911 | -0.0061629 | 37.8229
3 | 0.0212 | 0.0053158 | -0.021177 | -0.0053076 | 2.2605e-05 | 8.2298e-06 | 0.031756 | 0.031756 | 0.031756 | 0.99342 | -0.046089 | 0.99232 | -0.053792 | 11.7614
4 | -0.2114 | -0.053167 | 0.21158 | 0.053236 | 0.00018178 | 6.957e-05 | 0.31491 | 0.31491 | 0.31491 | 0.99911 | -0.0061629 | 1 | 0 | 38.8776
5 | 0.14284 | 0.035937 | -0.14281 | -0.035926 | 2.9723e-05 | 1.1377e-05 | 0.21279 | 0.21279 | 0.21279 | 0.99911 | -0.0061629 | 0.9989 | -0.0076548 | 39.405
6 | 0.01571 | 0.0039373 | -0.015708 | -0.0039367 | 1.7727e-06 | 6.1569e-07 | 0.023557 | 0.023557 | 0.023557 | 0.99232 | -0.053792 | 0.99221 | -0.054607 | 8.7248
7 | 0.088319 | 0.022256 | -0.088018 | -0.022141 | 0.00030139 | 0.00011555 | 0.13161 | 0.13161 | 0.13161 | 0.9989 | -0.0076548 | 0.99538 | -0.032122 | 48.7438
8 | 0.054492 | 0.01367 | -0.054446 | -0.013652 | 4.6568e-05 | 1.7763e-05 | 0.081179 | 0.081179 | 0.081179 | 0.9989 | -0.0076548 | 0.99802 | -0.013822 | 30.0663
9 | 0.01344 | 0.0033683 | -0.013436 | -0.0033669 | 4.1306e-06 | 1.3783e-06 | 0.020156 | 0.020156 | 0.020156 | 0.99221 | -0.054607 | 0.99189 | -0.056827 | 7.4652
10 | 0.084985 | 0.02138 | -0.084874 | -0.021338 | 0.00011103 | 4.2561e-05 | 0.12707 | 0.12707 | 0.12707 | 0.99538 | -0.032122 | 0.99404 | -0.0415 | 47.0644
11 | 0.036365 | 0.0091205 | -0.036325 | -0.0091052 | 4.0333e-05 | 1.5226e-05 | 0.054221 | 0.054222 | 0.054222 | 0.99802 | -0.013822 | 0.99688 | -0.021831 | 20.0821
12 | 0.010097 | 0.0025303 | -0.010095 | -0.0025297 | 1.9238e-06 | 5.6651e-07 | 0.015147 | 0.015147 | 0.015147 | 0.99189 | -0.056827 | 0.9917 | -0.058204 | 5.61
13 | 0.003339 | 0.00083665 | -0.0033387 | -0.00083676 | 2.4269e-07 | -1.0672e-07 | 0.005009 | 0.005009 | 0.005009 | 0.99189 | -0.056827 | 0.99182 | -0.057353 | 1.8552
14 | 0.01715 | 0.0042997 | -0.017137 | -0.0042948 | 1.3823e-05 | 4.8763e-06 | 0.025601 | 0.025601 | 0.025601 | 0.99688 | -0.021831 | 0.99605 | -0.027654 | 9.4818
15 | 0.081939 | 0.020602 | -0.081922 | -0.020596 | 1.7171e-05 | 6.5805e-06 | 0.12268 | 0.12268 | 0.12268 | 0.99404 | -0.0415 | 0.99383 | -0.043004 | 45.4374
16 | 0.0059691 | 0.0014957 | -0.005968 | -0.0014956 | 1.13e-06 | 1.4089e-07 | 0.0089372 | 0.0089373 | 0.0089373 | 0.99383 | -0.043004 | 0.99363 | -0.044372 | 3.3101
17 | 0.057918 | 0.01458 | -0.057749 | -0.014516 | 0.00016822 | 6.4238e-05 | 0.08674 | 0.086741 | 0.086741 | 0.99383 | -0.043004 | 0.99085 | -0.063862 | 32.1261
18 | 0.0029352 | 0.0007355 | -0.0029351 | -0.00073559 | 1.3561e-07 | -9.3526e-08 | 0.0043955 | 0.0043956 | 0.0043956 | 0.99363 | -0.044372 | 0.99359 | -0.044706 | 1.628
19 | 0.057749 | 0.014516 | -0.057591 | -0.014455 | 0.0001587 | 6.0603e-05 | 0.086741 | 0.086741 | 0.086741 | 0.99085 | -0.063862 | 0.98804 | -0.083652 | 32.1262
20 | 0.051902 | 0.013029 | -0.051813 | -0.012995 | 8.9211e-05 | 3.4013e-05 | 0.078173 | 0.078174 | 0.078174 | 0.98804 | -0.083652 | 0.98629 | -0.096049 | 28.9532
21 | -0.0084924 | -0.0021284 | 0.0084937 | 0.0021287 | 1.3178e-06 | 3.4419e-07 | 0.012843 | 0.012843 | 0.012843 | 0.98396 | -0.11258 | 0.98412 | -0.11146 | 4.7566
22 | -0.012282 | -0.0030783 | 0.012283 | 0.0030784 | 5.0642e-07 | 1.6488e-07 | 0.018571 | 0.018571 | 0.018571 | 0.98412 | -0.11146 | 0.98416 | -0.11116 | 6.8783
23 | 0.043757 | 0.010977 | -0.043732 | -0.010968 | 2.4606e-05 | 9.3483e-06 | 0.06602 | 0.06602 | 0.06602 | 0.98629 | -0.096049 | 0.98572 | -0.10011 | 24.4519
24 | 0.0053312 | 0.0013357 | -0.0053297 | -0.0013356 | 1.4758e-06 | 1.0119e-07 | 0.0080431 | 0.0080432 | 0.0080432 | 0.98629 | -0.096049 | 0.98601 | -0.09805 | 2.979
25 | 0.006014 | 0.0015069 | -0.0060137 | -0.0015069 | 2.5469e-07 | 3.3287e-08 | 0.0090237 | 0.0090237 | 0.0090237 | 0.9917 | -0.058204 | 0.99166 | -0.05851 | 3.3421
26 | -0.0026945 | -0.0006753 | 0.0026947 | 0.00067515 | 1.7621e-07 | -1.5001e-07 | 0.0040666 | 0.0040665 | 0.0040666 | 0.98594 | -0.098522 | 0.98601 | -0.09805 | 1.5062
27 | 0.041194 | 0.010331 | -0.041185 | -0.010328 | 9.1737e-06 | 3.4799e-06 | 0.062188 | 0.062188 | 0.062188 | 0.98572 | -0.10011 | 0.98549 | -0.10171 | 23.0327
28 | 0.038165 | 0.009571 | -0.038155 | -0.0095673 | 9.6061e-06 | 3.6356e-06 | 0.057628 | 0.057628 | 0.057628 | 0.98549 | -0.10171 | 0.98524 | -0.10353 | 21.3437
29 | 0.035141 | 0.0088119 | -0.035104 | -0.0087979 | 3.7132e-05 | 1.4013e-05 | 0.053075 | 0.053076 | 0.053076 | 0.98524 | -0.10353 | 0.98416 | -0.11116 | 19.6576
30 | 0.0018969 | 0.0004751 | -0.0018968 | -0.00047523 | 5.8453e-08 | -1.2669e-07 | 0.0028462 | 0.0028463 | 0.0028463 | 0.99166 | -0.05851 | 0.99162 | -0.058733 | 1.0542
31 | 0.0018968 | 0.00047523 | -0.0018968 | -0.00047537 | 6.7106e-08 | -1.4542e-07 | 0.0028463 | 0.0028464 | 0.0028464 | 0.99162 | -0.058733 | 0.99159 | -0.058989 | 1.0542

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.21966 | 0.055061

## res_load
| p_mw | q_mvar
0 | 0.02225 | 0.0055764
1 | 0.012415 | 0.0031116
2 | 0.012351 | 0.0030954
3 | 0.0054677 | 0.0013703
4 | 0.0072797 | 0.0018245
5 | 0.0022678 | 0.00056837
6 | 0.0030332 | 0.00076018
7 | 0.018081 | 0.0045314
8 | 0.019174 | 0.0048055
9 | 0.017137 | 0.0042948
10 | 0.0029347 | 0.0007355
11 | 0.018035 | 0.00452
12 | 0.0030328 | 0.00076008
13 | 0.0029351 | 0.00073559
14 | 0.0056887 | 0.0014257
15 | 0.0084924 | 0.0021284
16 | 0.0037887 | 0.00094953
17 | 0.0027245 | 0.00068283
18 | 0.004081 | 0.0010228
19 | 0.0033387 | 0.00083676
20 | 0.0026945 | 0.0006753
21 | 0.0026351 | 0.00066042
22 | 0.0025384 | 0.00063618
23 | 0.0030201 | 0.00075692
24 | 0.0030143 | 0.00075547
25 | 0.022821 | 0.0057194
26 | 0.0041168 | 0.0010318
27 | 0.0018968 | 0.00047537

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1