## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1404-36_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1404-36_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1404-36_0_4_node_4 | 0.4 | n |  | TRUE
3 | bus_LV_1404-36_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1404-36_0_4_node_27 | 0.4 | n |  | TRUE
5 | bus_LV_1404-36_0_4_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_1404-36_0_4_node_30 | 0.4 | n |  | TRUE
7 | bus_LV_1404-36_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1404-36_0_4_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_1404-36_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_1404-36_0_4_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_1404-36_0_4_node_28 | 0.4 | n |  | TRUE
12 | bus_LV_1404-36_0_4_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_1404-36_0_4_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_1404-36_0_4_node_15 | 0.4 | n |  | TRUE
15 | bus_LV_1404-36_0_4_node_16 | 0.4 | n |  | TRUE
16 | bus_LV_1404-36_0_4_node_23 | 0.4 | n |  | TRUE
17 | bus_LV_1404-36_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_1404-36_0_4_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_1404-36_0_4_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_1404-36_0_4_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_1404-36_0_4_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_1404-36_0_4_node_41 | 0.4 | n |  | TRUE
23 | bus_LV_1404-36_0_4_node_38 | 0.4 | n |  | TRUE
24 | bus_LV_1404-36_0_4_node_37 | 0.4 | n |  | TRUE
25 | bus_LV_1404-36_0_4_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_1404-36_0_4_node_36 | 0.4 | n |  | TRUE
27 | bus_LV_1404-36_0_4_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_1404-36_0_4_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_1404-36_0_4_node_22 | 0.4 | n |  | TRUE
30 | bus_LV_1404-36_0_4_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_1404-36_0_4_node_25 | 0.4 | n |  | TRUE
32 | bus_LV_1404-36_0_4_node_26 | 0.4 | n |  | TRUE
33 | bus_LV_1404-36_0_4_node_29 | 0.4 | n |  | TRUE
34 | bus_LV_1404-36_0_4_node_40 | 0.4 | n |  | TRUE
35 | bus_LV_1404-36_0_4_node_33 | 0.4 | n |  | TRUE
36 | bus_LV_1404-36_0_4_node_34 | 0.4 | n |  | TRUE
37 | bus_LV_1404-36_0_4_node_35 | 0.4 | n |  | TRUE
38 | bus_LV_1404-36_0_4_node_39 | 0.4 | n |  | TRUE
39 | bus_MV_140_0_node_35 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1404-36_0_4_load_0 | 0 | 0.0098853 | 0.0024775 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1404-36_0_4_load_27 | 4 | 0.0070273 | 0.0017612 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1404-36_0_4_load_30 | 6 | 0.0076162 | 0.0019088 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1404-36_0_4_load_8 | 8 | 0.020425 | 0.0051189 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1404-36_0_4_load_7 | 9 | 0.025021 | 0.0062709 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1404-36_0_4_load_9 | 10 | 0.0095928 | 0.0024042 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1404-36_0_4_load_23 | 16 | 0.0080974 | 0.0020294 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1404-36_0_4_load_12 | 17 | 0.00335 | 0.0008396 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1404-36_0_4_load_18 | 21 | 0.0029821 | 0.00074739 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1404-36_0_4_load_41 | 22 | 0.006967 | 0.0017461 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1404-36_0_4_load_38 | 23 | 0.013968 | 0.0035008 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1404-36_0_4_load_37 | 24 | 0.0076852 | 0.0019261 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1404-36_0_4_load_21 | 25 | 0.0095558 | 0.0023949 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1404-36_0_4_load_19 | 27 | 0.0092831 | 0.0023266 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1404-36_0_4_load_20 | 28 | 0.0056251 | 0.0014098 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1404-36_0_4_load_22 | 29 | 0.0048604 | 0.0012181 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1404-36_0_4_load_24 | 30 | 0.0031378 | 0.0007864 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1404-36_0_4_load_25 | 31 | 0.003878 | 0.00097192 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1404-36_0_4_load_26 | 32 | 0.0034223 | 0.00085771 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1404-36_0_4_load_40 | 34 | 0.0025126 | 0.00062971 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1404-36_0_4_load_33 | 35 | 0.0052556 | 0.0013172 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1404-36_0_4_load_34 | 36 | 0.0024959 | 0.00062554 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1404-36_0_4_load_39 | 38 | 0.0066214 | 0.0016595 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 29 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1404-36_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.017664 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1404-36_0_4_line_1 | NAYY 4x150 SE | 1 | 2 | 0.025514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1404-36_0_4_line_2 | NAYY 4x150 SE | 2 | 5 | 0.064385 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1404-36_0_4_line_3 | NAYY 4x150 SE | 2 | 6 | 0.04926 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1404-36_0_4_line_4 | NAYY 4x150 SE | 2 | 3 | 0.092416 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1404-36_0_4_line_5 | NAYY 4x150 SE | 3 | 4 | 0.19854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1404-36_0_4_line_6 | NAYY 4x150 SE | 4 | 11 | 0.014647 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1404-36_0_4_line_7 | NAYY 4x150 SE | 5 | 10 | 0.0021365 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1404-36_0_4_line_8 | NAYY 4x150 SE | 5 | 9 | 0.024318 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1404-36_0_4_line_9 | NAYY 4x150 SE | 7 | 8 | 0.018786 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
10 | LV_1404-36_0_4_line_10 | NAYY 4x150 SE | 7 | 9 | 0.0061748 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
11 | LV_1404-36_0_4_line_11 | NAYY 4x150 SE | 8 | 12 | 0.016997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
12 | LV_1404-36_0_4_line_12 | NAYY 4x150 SE | 11 | 33 | 0.011122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1404-36_0_4_line_13 | NAYY 4x150 SE | 12 | 13 | 0.032083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
14 | LV_1404-36_0_4_line_14 | NAYY 4x150 SE | 13 | 14 | 0.20403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
15 | LV_1404-36_0_4_line_15 | NAYY 4x150 SE | 14 | 15 | 0.12965 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
16 | LV_1404-36_0_4_line_16 | NAYY 4x150 SE | 14 | 16 | 0.074135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
17 | LV_1404-36_0_4_line_17 | NAYY 4x150 SE | 15 | 22 | 0.1403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1404-36_0_4_line_18 | NAYY 4x150 SE | 15 | 18 | 0.12249 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1404-36_0_4_line_19 | NAYY 4x150 SE | 16 | 25 | 0.031089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
20 | LV_1404-36_0_4_line_20 | NAYY 4x150 SE | 17 | 18 | 0.0147 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1404-36_0_4_line_21 | NAYY 4x150 SE | 17 | 19 | 0.034497 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1404-36_0_4_line_22 | NAYY 4x150 SE | 19 | 20 | 0.025907 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1404-36_0_4_line_23 | NAYY 4x150 SE | 19 | 21 | 0.003118 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1404-36_0_4_line_24 | NAYY 4x150 SE | 20 | 23 | 0.018141 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1404-36_0_4_line_25 | NAYY 4x150 SE | 20 | 24 | 0.01294 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1404-36_0_4_line_26 | NAYY 4x150 SE | 24 | 26 | 0.018802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1404-36_0_4_line_27 | NAYY 4x150 SE | 25 | 27 | 0.0029841 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
28 | LV_1404-36_0_4_line_28 | NAYY 4x150 SE | 26 | 38 | 0.016329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1404-36_0_4_line_29 | NAYY 4x150 SE | 26 | 37 | 0.027822 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1404-36_0_4_line_30 | NAYY 4x150 SE | 27 | 28 | 0.025414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
31 | LV_1404-36_0_4_line_31 | NAYY 4x150 SE | 28 | 29 | 0.012708 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
32 | LV_1404-36_0_4_line_32 | NAYY 4x150 SE | 29 | 30 | 0.018083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1404-36_0_4_line_33 | NAYY 4x150 SE | 30 | 31 | 0.0090438 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1404-36_0_4_line_34 | NAYY 4x150 SE | 31 | 32 | 0.015088 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1404-36_0_4_line_35 | NAYY 4x150 SE | 33 | 34 | 0.018458 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1404-36_0_4_line_36 | NAYY 4x150 SE | 35 | 36 | 0.00051346 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1404-36_0_4_line_37 | NAYY 4x150 SE | 36 | 37 | 0.021995 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1404-36_0_4_trafo_22 | 0.25 MVA 20/0.4 kV | 39 | 29 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2663695.9515 | 1194478.2603 | 2663707.612 | 1194491.529
1 | 2663682.4125 | 1194492.3244 | 2663679.1632 | 1194486.8755 | 2663694.5053 | 1194480.246 | 2663695.9515 | 1194478.2603
2 | 2663682.4125 | 1194492.3244 | 2663691.7584 | 1194509.2004 | 2663713.1529 | 1194548.8958
3 | 2663682.4125 | 1194492.3244 | 2663669.7876 | 1194499.9946 | 2663667.073 | 1194505.1576 | 2663666.6272 | 1194511.2453 | 2663668.5739 | 1194526.6639 | 2663671.1795 | 1194533.1713
4 | 2663655.505 | 1194404.9315 | 2663663.6683 | 1194446.2981 | 2663663.7616 | 1194446.8438 | 2663665.4165 | 1194456.0335 | 2663666.2581 | 1194460.7341 | 2663669.4781 | 1194469.6513 | 2663679.1632 | 1194486.8755 | 2663682.4125 | 1194492.3244
5 | 2663655.505 | 1194404.9315 | 2663659.9669 | 1194404.5677 | 2663665.6973 | 1194401.7381 | 2663674.4727 | 1194394.9052 | 2663699.7165 | 1194370.1706 | 2663718.8474 | 1194344.8483 | 2663721.9727 | 1194343.3363 | 2663752.7393 | 1194335.2926 | 2663774.8833 | 1194329.0248 | 2663796.6347 | 1194320.9853 | 2663821.8426 | 1194308.8049
6 | 2663835.1395 | 1194302.663 | 2663823.8284 | 1194307.8454 | 2663821.8426 | 1194308.8049
7 | 2663713.1529 | 1194548.8958 | 2663714.2025 | 1194550.7567
8 | 2663713.1529 | 1194548.8958 | 2663734.2784 | 1194536.8499
9 | 2663739.6424 | 1194533.7913 | 2663749.6187 | 1194549.7094
10 | 2663739.6424 | 1194533.7913 | 2663734.2784 | 1194536.8499
11 | 2663758.6446 | 1194564.1114 | 2663749.6187 | 1194549.7094
12 | 2663835.1395 | 1194302.663 | 2663845.2714 | 1194298.0128
13 | 2663758.6446 | 1194564.1114 | 2663730.8036 | 1194580.1909
14 | 2663730.8036 | 1194580.1909 | 2663747.9318 | 1194611.1581 | 2663750.0631 | 1194615.6723 | 2663754.8317 | 1194625.1287 | 2663761.1397 | 1194641.0051 | 2663776.2269 | 1194669.6827 | 2663829.7695 | 1194632.3095 | 2663845.432 | 1194620.6253 | 2663857.6844 | 1194606.4588
15 | 2663857.6844 | 1194606.4588 | 2663872.1676 | 1194587.4801 | 2663910.8986 | 1194552.1396 | 2663915.2141 | 1194548.3501 | 2663945.5175 | 1194520.124 | 2663949.953 | 1194515.8134
16 | 2663857.6844 | 1194606.4588 | 2663814.9399 | 1194545.8868
17 | 2663914.9455 | 1194380.9494 | 2663915.5952 | 1194392.8856 | 2663943.8976 | 1194506.9879 | 2663946.586 | 1194512.1308 | 2663949.953 | 1194515.8134
18 | 2663870.0008 | 1194496.3815 | 2663910.8986 | 1194552.1396 | 2663915.2141 | 1194548.3501 | 2663945.5175 | 1194520.124 | 2663949.953 | 1194515.8134
19 | 2663814.9399 | 1194545.8868 | 2663797.0146 | 1194520.4855
20 | 2663870.0008 | 1194496.3815 | 2663861.3545 | 1194484.493
21 | 2663841.0638 | 1194456.5939 | 2663861.3545 | 1194484.493
22 | 2663841.0638 | 1194456.5939 | 2663828.2776 | 1194452.922 | 2663820.8195 | 1194442.7032
23 | 2663839.2237 | 1194454.0728 | 2663841.0638 | 1194456.5939
24 | 2663820.8195 | 1194442.7032 | 2663805.3471 | 1194452.2438
25 | 2663820.8195 | 1194442.7032 | 2663813.1891 | 1194432.2518
26 | 2663802.1026 | 1194417.0664 | 2663813.1891 | 1194432.2518
27 | 2663795.2941 | 1194518.0474 | 2663797.0146 | 1194520.4855
28 | 2663802.1026 | 1194417.0664 | 2663788.2545 | 1194425.7794
29 | 2663786.252 | 1194394.173 | 2663802.1026 | 1194417.0664
30 | 2663795.2941 | 1194518.0474 | 2663780.6409 | 1194497.2828
31 | 2663773.3138 | 1194486.8997 | 2663780.6409 | 1194497.2828
32 | 2663762.8875 | 1194472.1249 | 2663773.3138 | 1194486.8997
33 | 2663762.8875 | 1194472.1249 | 2663757.6731 | 1194464.7357
34 | 2663757.6731 | 1194464.7357 | 2663748.9735 | 1194452.4078
35 | 2663845.2714 | 1194298.0128 | 2663856.3541 | 1194312.7952
36 | 2663804.3451 | 1194380.7845 | 2663803.9324 | 1194381.0899
37 | 2663786.252 | 1194394.173 | 2663803.9324 | 1194381.0899

## bus_geodata
| x | y | coords
0 | 2663707.612 | 1194491.529
1 | 2663695.9515 | 1194478.2603
2 | 2663682.4125 | 1194492.3244
3 | 2663655.505 | 1194404.9315
4 | 2663821.8426 | 1194308.8049
5 | 2663713.1529 | 1194548.8958
6 | 2663671.1795 | 1194533.1713
7 | 2663739.6424 | 1194533.7913
8 | 2663749.6187 | 1194549.7094
9 | 2663734.2784 | 1194536.8499
10 | 2663714.2025 | 1194550.7567
11 | 2663835.1395 | 1194302.663
12 | 2663758.6446 | 1194564.1114
13 | 2663730.8036 | 1194580.1909
14 | 2663857.6844 | 1194606.4588
15 | 2663949.953 | 1194515.8134
16 | 2663814.9399 | 1194545.8868
17 | 2663861.3545 | 1194484.493
18 | 2663870.0008 | 1194496.3815
19 | 2663841.0638 | 1194456.5939
20 | 2663820.8195 | 1194442.7032
21 | 2663839.2237 | 1194454.0728
22 | 2663914.9455 | 1194380.9494
23 | 2663805.3471 | 1194452.2438
24 | 2663813.1891 | 1194432.2518
25 | 2663797.0146 | 1194520.4855
26 | 2663802.1026 | 1194417.0664
27 | 2663795.2941 | 1194518.0474
28 | 2663780.6409 | 1194497.2828
29 | 2663773.3138 | 1194486.8997
30 | 2663762.8875 | 1194472.1249
31 | 2663757.6731 | 1194464.7357
32 | 2663748.9735 | 1194452.4078
33 | 2663845.2714 | 1194298.0128
34 | 2663856.3541 | 1194312.7952
35 | 2663804.3451 | 1194380.7845
36 | 2663803.9324 | 1194381.0899
37 | 2663786.252 | 1194394.173
38 | 2663788.2545 | 1194425.7794
39 | 2663726.4696 | 1194420.5181

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97455 | -0.1788 | 0.0098853 | 0.0024775
1 | 0.97481 | -0.17697 | 0 | 0
2 | 0.97518 | -0.17432 | 0 | 0
3 | 0.97388 | -0.18361 | 0 | 0
4 | 0.9711 | -0.20363 | 0.0070273 | 0.0017612
5 | 0.97773 | -0.15607 | 0 | 0
6 | 0.97463 | -0.17826 | 0.0076162 | 0.0019088
7 | 0.97931 | -0.14478 | 0 | 0
8 | 0.97987 | -0.14076 | 0.020425 | 0.0051189
9 | 0.97903 | -0.14677 | 0.025021 | 0.0062709
10 | 0.9777 | -0.15628 | 0.0095928 | 0.0024042
11 | 0.97105 | -0.20402 | 0 | 0
12 | 0.98055 | -0.13593 | 0 | 0
13 | 0.98183 | -0.12682 | 0 | 0
14 | 0.98997 | -0.069437 | 0 | 0
15 | 0.98529 | -0.10219 | 0 | 0
16 | 0.99471 | -0.036475 | 0.0080974 | 0.0020294
17 | 0.97678 | -0.16248 | 0.00335 | 0.0008396
18 | 0.9777 | -0.15597 | 0 | 0
19 | 0.97481 | -0.17659 | 0 | 0
20 | 0.97344 | -0.18641 | 0 | 0
21 | 0.9748 | -0.17669 | 0.0029821 | 0.00074739
22 | 0.98388 | -0.11226 | 0.006967 | 0.0017461
23 | 0.97307 | -0.18908 | 0.013968 | 0.0035008
24 | 0.97303 | -0.18942 | 0.0076852 | 0.0019261
25 | 0.99682 | -0.0219 | 0.0095558 | 0.0023949
26 | 0.97263 | -0.19227 | 0 | 0
27 | 0.99704 | -0.020409 | 0.0092831 | 0.0023266
28 | 0.99899 | -0.006949 | 0.0056251 | 0.0014098
29 | 1 | 0 | -0.17841 | -0.04491
30 | 0.99973 | -0.0018849 | 0.0031378 | 0.0007864
31 | 0.99964 | -0.0025444 | 0.003878 | 0.00097192
32 | 0.99956 | -0.0030603 | 0.0034223 | 0.00085771
33 | 0.97101 | -0.20431 | 0 | 0
34 | 0.97094 | -0.2048 | 0.0025126 | 0.00062971
35 | 0.97206 | -0.19638 | 0.0052556 | 0.0013172
36 | 0.97206 | -0.19635 | 0.0024959 | 0.00062554
37 | 0.97231 | -0.19455 | 0 | 0
38 | 0.97247 | -0.19342 | 0.0066214 | 0.0016595
39 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0098853 | -0.0024775 | 0.0098878 | 0.0024782 | 2.5111e-06 | 7.4564e-07 | 0.015094 | 0.015093 | 0.015094 | 0.97455 | -0.1788 | 0.97481 | -0.17697 | 5.5902
1 | -0.0098878 | -0.0024782 | 0.0098914 | 0.0024793 | 3.6269e-06 | 1.0768e-06 | 0.015093 | 0.015093 | 0.015093 | 0.97481 | -0.17697 | 0.97518 | -0.17432 | 5.5902
2 | -0.027091 | -0.0067909 | 0.027159 | 0.0068165 | 6.8654e-05 | 2.56e-05 | 0.041338 | 0.041338 | 0.041338 | 0.97518 | -0.17432 | 0.97773 | -0.15607 | 15.3104
3 | 0.0076203 | 0.0019098 | -0.0076162 | -0.0019088 | 4.1561e-06 | 9.8427e-07 | 0.011628 | 0.011628 | 0.011628 | 0.97518 | -0.17432 | 0.97463 | -0.17826 | 4.3067
4 | 0.0095791 | 0.0024018 | -0.0095667 | -0.0023982 | 1.2321e-05 | 3.5876e-06 | 0.014617 | 0.014617 | 0.014617 | 0.97518 | -0.17432 | 0.97388 | -0.18361 | 5.4139
5 | 0.0095667 | 0.0023982 | -0.0095403 | -0.0023905 | 2.6473e-05 | 7.7185e-06 | 0.014617 | 0.014618 | 0.014618 | 0.97388 | -0.18361 | 0.9711 | -0.20363 | 5.4142
6 | 0.002513 | 0.00062932 | -0.0025128 | -0.00062945 | 1.3551e-07 | -1.2909e-07 | 0.0038505 | 0.0038505 | 0.0038505 | 0.9711 | -0.20363 | 0.97105 | -0.20402 | 1.4261
7 | 0.0095931 | 0.0024043 | -0.0095928 | -0.0024042 | 2.8418e-07 | 8.2507e-08 | 0.0146 | 0.0146 | 0.0146 | 0.97773 | -0.15607 | 0.9777 | -0.15628 | 5.4074
8 | -0.036753 | -0.0092208 | 0.0368 | 0.0092387 | 4.7482e-05 | 1.7957e-05 | 0.055938 | 0.055938 | 0.055938 | 0.97773 | -0.15607 | 0.97903 | -0.14677 | 20.7177
9 | -0.061838 | -0.015516 | 0.061873 | 0.015529 | 3.4502e-05 | 1.2561e-05 | 0.093967 | 0.093967 | 0.093967 | 0.97931 | -0.14478 | 0.97987 | -0.14076 | 11.6009
10 | 0.061838 | 0.015516 | -0.061821 | -0.01551 | 1.7011e-05 | 6.3873e-06 | 0.093967 | 0.093967 | 0.093967 | 0.97931 | -0.14478 | 0.97903 | -0.14677 | 17.4013
11 | -0.082298 | -0.020648 | 0.082353 | 0.020668 | 5.5224e-05 | 2.0597e-05 | 0.12498 | 0.12498 | 0.12498 | 0.97987 | -0.14076 | 0.98055 | -0.13593 | 15.4301
12 | 0.0025128 | 0.00062945 | -0.0025127 | -0.00062955 | 1.029e-07 | -9.8004e-08 | 0.0038505 | 0.0038506 | 0.0038506 | 0.97105 | -0.20402 | 0.97101 | -0.20431 | 1.4261
13 | -0.082353 | -0.020668 | 0.082457 | 0.020707 | 0.00010424 | 3.8877e-05 | 0.12498 | 0.12498 | 0.12498 | 0.98055 | -0.13593 | 0.98183 | -0.12682 | 15.43
14 | -0.082457 | -0.020707 | 0.08312 | 0.020954 | 0.00066289 | 0.00024715 | 0.12498 | 0.12498 | 0.12498 | 0.98183 | -0.12682 | 0.98997 | -0.069437 | 15.43
15 | 0.050075 | 0.012641 | -0.049846 | -0.012556 | 0.00022935 | 8.4895e-05 | 0.0753 | 0.075301 | 0.075301 | 0.98997 | -0.069437 | 0.98529 | -0.10219 | 13.9446
16 | -0.13319 | -0.033595 | 0.13381 | 0.03383 | 0.00061853 | 0.00023502 | 0.20028 | 0.20028 | 0.20028 | 0.98997 | -0.069437 | 0.99471 | -0.036475 | 24.7259
17 | 0.0069767 | 0.001748 | -0.006967 | -0.0017461 | 9.7196e-06 | 1.9539e-06 | 0.010536 | 0.010537 | 0.010537 | 0.98529 | -0.10219 | 0.98388 | -0.11226 | 3.9025
18 | 0.042869 | 0.010808 | -0.042548 | -0.010687 | 0.0003206 | 0.00012176 | 0.064765 | 0.064765 | 0.064765 | 0.98529 | -0.10219 | 0.9777 | -0.15597 | 23.9871
19 | -0.14191 | -0.03586 | 0.1422 | 0.035971 | 0.00029171 | 0.00011098 | 0.21239 | 0.21239 | 0.21239 | 0.99471 | -0.036475 | 0.99682 | -0.0219 | 26.2212
20 | -0.04251 | -0.010672 | 0.042548 | 0.010687 | 3.8476e-05 | 1.4614e-05 | 0.064765 | 0.064765 | 0.064765 | 0.97678 | -0.16248 | 0.9777 | -0.15597 | 23.9871
21 | 0.03916 | 0.0098324 | -0.039083 | -0.0098033 | 7.6624e-05 | 2.904e-05 | 0.059662 | 0.059662 | 0.059662 | 0.97678 | -0.16248 | 0.97481 | -0.17659 | 22.097
22 | 0.036101 | 0.009056 | -0.036052 | -0.0090374 | 4.9097e-05 | 1.8561e-05 | 0.05511 | 0.05511 | 0.05511 | 0.97481 | -0.17659 | 0.97344 | -0.18641 | 20.4111
23 | 0.0029822 | 0.00074737 | -0.0029821 | -0.00074739 | 4.0318e-08 | -2.3364e-08 | 0.0045522 | 0.0045522 | 0.0045522 | 0.97481 | -0.17659 | 0.9748 | -0.17669 | 1.686
24 | 0.013973 | 0.0035025 | -0.013968 | -0.0035008 | 5.1648e-06 | 1.761e-06 | 0.02136 | 0.02136 | 0.02136 | 0.97344 | -0.18641 | 0.97307 | -0.18908 | 7.9111
25 | 0.022078 | 0.0055349 | -0.022069 | -0.0055315 | 9.1977e-06 | 3.3768e-06 | 0.03375 | 0.03375 | 0.03375 | 0.97344 | -0.18641 | 0.97303 | -0.18942 | 12.5
26 | 0.014384 | 0.0036054 | -0.014378 | -0.0036034 | 5.677e-06 | 1.95e-06 | 0.021997 | 0.021997 | 0.021997 | 0.97303 | -0.18942 | 0.97263 | -0.19227 | 8.1471
27 | -0.15176 | -0.038366 | 0.15179 | 0.038378 | 3.1886e-05 | 1.2147e-05 | 0.22666 | 0.22666 | 0.22666 | 0.99682 | -0.0219 | 0.99704 | -0.020409 | 27.9822
28 | 0.0066224 | 0.0016597 | -0.0066214 | -0.0016595 | 1.0459e-06 | 1.9965e-07 | 0.010132 | 0.010132 | 0.010132 | 0.97263 | -0.19227 | 0.97247 | -0.19342 | 3.7524
29 | 0.0077559 | 0.0019438 | -0.0077535 | -0.0019432 | 2.4443e-06 | 5.9495e-07 | 0.011866 | 0.011866 | 0.011866 | 0.97263 | -0.19227 | 0.97231 | -0.19455 | 4.3947
30 | -0.16107 | -0.040704 | 0.16138 | 0.040821 | 0.00030578 | 0.00011661 | 0.24051 | 0.24051 | 0.24051 | 0.99704 | -0.020409 | 0.99899 | -0.006949 | 29.6926
31 | -0.167 | -0.042231 | 0.16717 | 0.042293 | 0.00016374 | 6.2477e-05 | 0.24889 | 0.24889 | 0.24889 | 0.99899 | -0.006949 | 1 | 0 | 30.727
32 | 0.010442 | 0.0026169 | -0.010439 | -0.0026161 | 2.7241e-06 | 8.1055e-07 | 0.015537 | 0.015538 | 0.015538 | 1 | 0 | 0.99973 | -0.0018849 | 5.7546
33 | 0.0073012 | 0.0018297 | -0.0073006 | -0.0018295 | 6.6646e-07 | 1.3776e-07 | 0.010867 | 0.010867 | 0.010867 | 0.99973 | -0.0018849 | 0.99964 | -0.0025444 | 4.0249
34 | 0.0034226 | 0.00085761 | -0.0034223 | -0.00085771 | 2.4437e-07 | -1.038e-07 | 0.0050946 | 0.0050947 | 0.0050947 | 0.99964 | -0.0025444 | 0.99956 | -0.0030603 | 1.8869
35 | 0.0025127 | 0.00062955 | -0.0025126 | -0.00062971 | 1.7078e-07 | -1.6262e-07 | 0.0038506 | 0.0038507 | 0.0038507 | 0.97101 | -0.20431 | 0.97094 | -0.2048 | 1.4262
36 | -0.0052556 | -0.0013172 | 0.0052556 | 0.0013172 | 2.0738e-08 | 1.611e-09 | 0.0080452 | 0.0080452 | 0.0080452 | 0.97206 | -0.19638 | 0.97206 | -0.19635 | 2.9797
37 | -0.0077515 | -0.0019427 | 0.0077535 | 0.0019432 | 1.9324e-06 | 4.7051e-07 | 0.011866 | 0.011866 | 0.011866 | 0.97206 | -0.19635 | 0.97231 | -0.19455 | 4.3948

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.18327 | 0.046128

## res_load
| p_mw | q_mvar
0 | 0.0098853 | 0.0024775
1 | 0.0070273 | 0.0017612
2 | 0.0076162 | 0.0019088
3 | 0.020425 | 0.0051189
4 | 0.025021 | 0.0062709
5 | 0.0095928 | 0.0024042
6 | 0.0080974 | 0.0020294
7 | 0.00335 | 0.0008396
8 | 0.0029821 | 0.00074739
9 | 0.006967 | 0.0017461
10 | 0.013968 | 0.0035008
11 | 0.0076852 | 0.0019261
12 | 0.0095558 | 0.0023949
13 | 0.0092831 | 0.0023266
14 | 0.0056251 | 0.0014098
15 | 0.0048604 | 0.0012181
16 | 0.0031378 | 0.0007864
17 | 0.003878 | 0.00097192
18 | 0.0034223 | 0.00085771
19 | 0.0025126 | 0.00062971
20 | 0.0052556 | 0.0013172
21 | 0.0024959 | 0.00062554
22 | 0.0066214 | 0.0016595

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1