## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1404-44_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1404-44_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1404-44_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1404-44_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1404-44_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1404-44_0_3_node_30 | 0.4 | n |  | TRUE
6 | bus_LV_1404-44_0_3_node_25 | 0.4 | n |  | TRUE
7 | bus_LV_1404-44_0_3_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1404-44_0_3_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1404-44_0_3_node_31 | 0.4 | n |  | TRUE
10 | bus_LV_1404-44_0_3_node_23 | 0.4 | n |  | TRUE
11 | bus_LV_1404-44_0_3_node_26 | 0.4 | n |  | TRUE
12 | bus_LV_1404-44_0_3_node_29 | 0.4 | n |  | TRUE
13 | bus_LV_1404-44_0_3_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_1404-44_0_3_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_1404-44_0_3_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_1404-44_0_3_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_1404-44_0_3_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_1404-44_0_3_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_1404-44_0_3_node_22 | 0.4 | n |  | TRUE
20 | bus_LV_1404-44_0_3_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_1404-44_0_3_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_1404-44_0_3_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_1404-44_0_3_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_1404-44_0_3_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_1404-44_0_3_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_1404-44_0_3_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_1404-44_0_3_node_27 | 0.4 | n |  | TRUE
28 | bus_LV_1404-44_0_3_node_28 | 0.4 | n |  | TRUE
29 | bus_MV_140_0_node_44 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1404-44_0_3_load_0 | 0 | 0.00096758 | 0.0002425 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1404-44_0_3_load_3 | 3 | 0.0035254 | 0.00088354 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1404-44_0_3_load_30 | 5 | 0.0041228 | 0.0010333 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1404-44_0_3_load_25 | 6 | 0.0023969 | 0.00060072 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1404-44_0_3_load_31 | 9 | 0.07358 | 0.018441 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1404-44_0_3_load_23 | 10 | 0.011161 | 0.0027972 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1404-44_0_3_load_26 | 11 | 0.003351 | 0.00083983 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1404-44_0_3_load_29 | 12 | 0.05275 | 0.01322 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1404-44_0_3_load_11 | 13 | 0.0065781 | 0.0016486 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1404-44_0_3_load_7 | 14 | 0.0087151 | 0.0021842 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1404-44_0_3_load_8 | 15 | 0.005336 | 0.0013373 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1404-44_0_3_load_12 | 17 | 0.024993 | 0.0062637 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1404-44_0_3_load_13 | 18 | 0.01284 | 0.0032181 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1404-44_0_3_load_14 | 21 | 0.001747 | 0.00043783 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1404-44_0_3_load_15 | 22 | 0.0017444 | 0.00043719 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1404-44_0_3_load_19 | 24 | 0.0050411 | 0.0012634 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1404-44_0_3_load_20 | 25 | 0.0026382 | 0.0006612 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1404-44_0_3_load_21 | 26 | 0.0064588 | 0.0016187 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1404-44_0_3_load_28 | 28 | 0.0055223 | 0.001384 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 28 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1404-44_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.088563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1404-44_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0072299 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1404-44_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.062769 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1404-44_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.052671 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1404-44_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.019336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1404-44_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.024563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1404-44_0_3_line_6 | NAYY 4x150 SE | 6 | 11 | 0.018598 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1404-44_0_3_line_7 | NAYY 4x150 SE | 7 | 8 | 0.079094 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_1404-44_0_3_line_8 | NAYY 4x150 SE | 7 | 9 | 0.10896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
9 | LV_1404-44_0_3_line_9 | NAYY 4x150 SE | 8 | 10 | 0.0059949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1404-44_0_3_line_10 | NAYY 4x150 SE | 9 | 12 | 0.010925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
11 | LV_1404-44_0_3_line_11 | NAYY 4x150 SE | 10 | 13 | 0.0063305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1404-44_0_3_line_12 | NAYY 4x150 SE | 11 | 27 | 0.018632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1404-44_0_3_line_13 | NAYY 4x150 SE | 12 | 27 | 0.01871 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
14 | LV_1404-44_0_3_line_14 | NAYY 4x150 SE | 13 | 16 | 0.019242 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1404-44_0_3_line_15 | NAYY 4x150 SE | 14 | 15 | 0.019774 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1404-44_0_3_line_16 | NAYY 4x150 SE | 14 | 16 | 0.024395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1404-44_0_3_line_17 | NAYY 4x150 SE | 16 | 17 | 0.025535 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1404-44_0_3_line_18 | NAYY 4x150 SE | 16 | 18 | 0.026512 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1404-44_0_3_line_19 | NAYY 4x150 SE | 17 | 19 | 0.040426 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1404-44_0_3_line_20 | NAYY 4x150 SE | 19 | 20 | 0.042966 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1404-44_0_3_line_21 | NAYY 4x150 SE | 20 | 24 | 0.018142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1404-44_0_3_line_22 | NAYY 4x150 SE | 20 | 23 | 0.00468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1404-44_0_3_line_23 | NAYY 4x150 SE | 21 | 22 | 0.0042955 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1404-44_0_3_line_24 | NAYY 4x150 SE | 21 | 23 | 0.025112 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1404-44_0_3_line_25 | NAYY 4x150 SE | 24 | 25 | 0.012865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1404-44_0_3_line_26 | NAYY 4x150 SE | 25 | 26 | 0.0064495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1404-44_0_3_line_27 | NAYY 4x150 SE | 27 | 28 | 0.022694 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1404-44_0_3_trafo_28 | 0.25 MVA 20/0.4 kV | 29 | 28 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2663475.2492 | 1194882.2401 | 2663487.8235 | 1194872.7791 | 2663499.5068 | 1194862.5638 | 2663521.3365 | 1194841.1941 | 2663540.3671 | 1194823.6636 | 2663540.8717 | 1194822.9368
1 | 2663544.9947 | 1194816.9978 | 2663540.8717 | 1194822.9368
2 | 2663475.2492 | 1194882.2401 | 2663510.4068 | 1194934.2385
3 | 2663544.9947 | 1194816.9978 | 2663549.7452 | 1194808.8101 | 2663565.2533 | 1194812.2768 | 2663571.9864 | 1194812.5597 | 2663575.8352 | 1194812.5005 | 2663576.9965 | 1194816.5152 | 2663579.7905 | 1194819.6245 | 2663583.6598 | 1194821.211 | 2663587.8381 | 1194820.9774
4 | 2663521.2373 | 1194950.2568 | 2663510.4068 | 1194934.2385
5 | 2663587.8381 | 1194820.9774 | 2663589.9549 | 1194828.2931 | 2663590.4801 | 1194832.6457 | 2663590.0172 | 1194836.7654 | 2663588.1785 | 1194844.9795
6 | 2663588.1785 | 1194844.9795 | 2663584.9052 | 1194859.6022 | 2663584.8668 | 1194863.215
7 | 2663670.843 | 1194861.1057 | 2663695.3384 | 1194852.0834 | 2663697.5899 | 1194859.6117 | 2663715.7732 | 1194900.9183
8 | 2663670.843 | 1194861.1057 | 2663658.7819 | 1194837.3524 | 2663655.8681 | 1194838.3442 | 2663650.6638 | 1194825.4369 | 2663619.1707 | 1194838.9877 | 2663617.4466 | 1194849.9202 | 2663613.5465 | 1194851.2239 | 2663619.0158 | 1194863.5782 | 2663616.9055 | 1194864.607
9 | 2663715.7732 | 1194900.9183 | 2663716.9961 | 1194906.7872
10 | 2663607.0851 | 1194869.3947 | 2663616.9055 | 1194864.607
11 | 2663718.2874 | 1194912.9846 | 2663716.9961 | 1194906.7872
12 | 2663594.2673 | 1194879.2243 | 2663587.0449 | 1194868.3523 | 2663584.8668 | 1194863.215
13 | 2663594.2673 | 1194879.2243 | 2663607.8769 | 1194872.754 | 2663606.8752 | 1194869.497 | 2663607.0851 | 1194869.3947
14 | 2663725.6762 | 1194929.7962 | 2663722.9418 | 1194928.2551 | 2663720.5142 | 1194923.671 | 2663718.2874 | 1194912.9846
15 | 2663732.9473 | 1194952.1833 | 2663744.2593 | 1194968.4018
16 | 2663725.6762 | 1194929.7962 | 2663726.6764 | 1194943.1925 | 2663732.9473 | 1194952.1833
17 | 2663725.6762 | 1194929.7962 | 2663723.6472 | 1194940.0028 | 2663718.234 | 1194946.0154 | 2663712.6312 | 1194950.2752
18 | 2663725.6762 | 1194929.7962 | 2663731.56 | 1194931.8268 | 2663737.0517 | 1194932.0409 | 2663742.6177 | 1194930.2881 | 2663750.7311 | 1194926.4954
19 | 2663683.398 | 1194978.0077 | 2663698.3169 | 1194961.6236 | 2663710.6056 | 1194951.8153 | 2663712.6312 | 1194950.2752
20 | 2663683.398 | 1194978.0077 | 2663668.6333 | 1194994.2267 | 2663656.2221 | 1195011.2602
21 | 2663656.2221 | 1195011.2602 | 2663646.7716 | 1195005.0005 | 2663641.8644 | 1195000.2836
22 | 2663653.4616 | 1195015.0442 | 2663656.2221 | 1195011.2602
23 | 2663624.3708 | 1195019.3483 | 2663628.62 | 1195018.7196
24 | 2663653.4616 | 1195015.0442 | 2663628.62 | 1195018.7196
25 | 2663641.8644 | 1195000.2836 | 2663634.1753 | 1194992.8927 | 2663632.6607 | 1194991.2979
26 | 2663632.6277 | 1194985.0828 | 2663632.0497 | 1194986.4108 | 2663631.9334 | 1194988.0327 | 2663632.0684 | 1194989.6685 | 2663632.6607 | 1194991.2979
27 | 2663594.2673 | 1194879.2243 | 2663606.8341 | 1194898.1211

## bus_geodata
| x | y | coords
0 | 2663540.8717 | 1194822.9368
1 | 2663475.2492 | 1194882.2401
2 | 2663544.9947 | 1194816.9978
3 | 2663510.4068 | 1194934.2385
4 | 2663587.8381 | 1194820.9774
5 | 2663521.2373 | 1194950.2568
6 | 2663588.1785 | 1194844.9795
7 | 2663670.843 | 1194861.1057
8 | 2663715.7732 | 1194900.9184
9 | 2663616.9055 | 1194864.607
10 | 2663716.9961 | 1194906.7872
11 | 2663584.8668 | 1194863.215
12 | 2663607.0851 | 1194869.3947
13 | 2663718.2874 | 1194912.9846
14 | 2663732.9473 | 1194952.1833
15 | 2663744.2593 | 1194968.4018
16 | 2663725.6762 | 1194929.7962
17 | 2663712.6312 | 1194950.2752
18 | 2663750.7311 | 1194926.4954
19 | 2663683.398 | 1194978.0077
20 | 2663656.2221 | 1195011.2602
21 | 2663628.62 | 1195018.7196
22 | 2663624.3708 | 1195019.3483
23 | 2663653.4616 | 1195015.0442
24 | 2663641.8644 | 1195000.2836
25 | 2663632.6607 | 1194991.2979
26 | 2663632.6277 | 1194985.0828
27 | 2663594.2673 | 1194879.2243
28 | 2663606.8341 | 1194898.1211
29 | 2663606.8341 | 1194898.1211

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99579 | -0.029346 | 0.00096758 | 0.0002425
1 | 0.99482 | -0.036181 | 0 | 0
2 | 0.99588 | -0.028718 | 0 | 0
3 | 0.99413 | -0.041029 | 0.0035254 | 0.00088354
4 | 0.99653 | -0.024144 | 0 | 0
5 | 0.99402 | -0.041834 | 0.0041228 | 0.0010333
6 | 0.99684 | -0.022012 | 0.0023969 | 0.00060072
7 | 0.98782 | -0.084864 | 0 | 0
8 | 0.98279 | -0.12035 | 0 | 0
9 | 0.99475 | -0.036556 | 0.07358 | 0.018441
10 | 0.98203 | -0.12576 | 0.011161 | 0.0027972
11 | 0.99713 | -0.019951 | 0.003351 | 0.00083983
12 | 0.99559 | -0.030651 | 0.05275 | 0.01322
13 | 0.98133 | -0.13075 | 0.0065781 | 0.0016486
14 | 0.97888 | -0.14822 | 0.0087151 | 0.0021842
15 | 0.97873 | -0.14931 | 0.005336 | 0.0013373
16 | 0.97938 | -0.14465 | 0 | 0
17 | 0.97779 | -0.15599 | 0.024993 | 0.0062637
18 | 0.97888 | -0.14819 | 0.01284 | 0.0032181
19 | 0.97675 | -0.16345 | 0 | 0
20 | 0.97564 | -0.17138 | 0 | 0
21 | 0.97549 | -0.17247 | 0.001747 | 0.00043783
22 | 0.97548 | -0.17255 | 0.0017444 | 0.00043719
23 | 0.97562 | -0.17155 | 0 | 0
24 | 0.97527 | -0.17407 | 0.0050411 | 0.0012634
25 | 0.97509 | -0.1753 | 0.0026382 | 0.0006612
26 | 0.97503 | -0.17574 | 0.0064588 | 0.0016187
27 | 0.99751 | -0.01726 | 0 | 0
28 | 1 | 0 | -0.23128 | -0.05809
29 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.007661 | 0.0019195 | -0.0076538 | -0.0019179 | 7.2425e-06 | 1.6346e-06 | 0.011448 | 0.011448 | 0.011448 | 0.99579 | -0.029346 | 0.99482 | -0.036181 | 4.24
1 | -0.0086286 | -0.002162 | 0.0086294 | 0.0021622 | 7.5e-07 | 1.944e-07 | 0.012894 | 0.012894 | 0.012894 | 0.99579 | -0.029346 | 0.99588 | -0.028718 | 4.7754
2 | 0.0076538 | 0.0019179 | -0.0076487 | -0.0019167 | 5.1334e-06 | 1.16e-06 | 0.011448 | 0.011448 | 0.011448 | 0.99482 | -0.036181 | 0.99413 | -0.041029 | 4.2402
3 | -0.0086294 | -0.0021622 | 0.0086348 | 0.0021636 | 5.4638e-06 | 1.4157e-06 | 0.012894 | 0.012893 | 0.012894 | 0.99588 | -0.028718 | 0.99653 | -0.024144 | 4.7754
4 | 0.0041233 | 0.0010332 | -0.0041228 | -0.0010333 | 4.5958e-07 | -7.3919e-08 | 0.0061716 | 0.0061717 | 0.0061717 | 0.99413 | -0.041029 | 0.99402 | -0.041834 | 2.2858
5 | -0.0086348 | -0.0021636 | 0.0086374 | 0.0021643 | 2.5479e-06 | 6.5986e-07 | 0.012893 | 0.012893 | 0.012893 | 0.99653 | -0.024144 | 0.99684 | -0.022012 | 4.7753
6 | -0.011034 | -0.002765 | 0.011037 | 0.002766 | 3.1484e-06 | 9.684e-07 | 0.016471 | 0.016471 | 0.016471 | 0.99684 | -0.022012 | 0.99713 | -0.019951 | 6.1004
7 | 0.088067 | 0.022175 | -0.087632 | -0.02201 | 0.00043454 | 0.00016511 | 0.1327 | 0.1327 | 0.1327 | 0.98782 | -0.084864 | 0.98279 | -0.12035 | 24.5738
8 | -0.088067 | -0.022175 | 0.088666 | 0.022403 | 0.0005986 | 0.00022742 | 0.1327 | 0.1327 | 0.1327 | 0.98782 | -0.084864 | 0.99475 | -0.036556 | 24.5737
9 | 0.087632 | 0.02201 | -0.087567 | -0.021985 | 6.5872e-05 | 2.5259e-05 | 0.1327 | 0.1327 | 0.1327 | 0.98279 | -0.12035 | 0.98203 | -0.12576 | 49.1476
10 | -0.16225 | -0.040844 | 0.16238 | 0.040895 | 0.00013392 | 5.1084e-05 | 0.24276 | 0.24276 | 0.24276 | 0.99475 | -0.036556 | 0.99559 | -0.030651 | 29.9708
11 | 0.076406 | 0.019188 | -0.076353 | -0.019167 | 5.296e-05 | 2.0289e-05 | 0.11579 | 0.11579 | 0.11579 | 0.98203 | -0.12576 | 0.98133 | -0.13075 | 42.8841
12 | -0.014388 | -0.0036058 | 0.014394 | 0.0036076 | 5.3602e-06 | 1.8185e-06 | 0.021472 | 0.021472 | 0.021472 | 0.99713 | -0.019951 | 0.99751 | -0.01726 | 7.9525
13 | -0.21513 | -0.054115 | 0.21553 | 0.054269 | 0.00040252 | 0.00015408 | 0.3216 | 0.3216 | 0.3216 | 0.99559 | -0.030651 | 0.99751 | -0.01726 | 39.7042
14 | 0.069775 | 0.017519 | -0.06964 | -0.017467 | 0.00013443 | 5.1462e-05 | 0.10581 | 0.10581 | 0.10581 | 0.98133 | -0.13075 | 0.97938 | -0.14465 | 39.1898
15 | 0.0053368 | 0.0013374 | -0.005336 | -0.0013373 | 8.1208e-07 | 6.3802e-08 | 0.0081126 | 0.0081127 | 0.0081127 | 0.97888 | -0.14822 | 0.97873 | -0.14931 | 3.0047
16 | -0.014052 | -0.0035216 | 0.014059 | 0.003524 | 6.9457e-06 | 2.3646e-06 | 0.021361 | 0.02136 | 0.021361 | 0.97888 | -0.14822 | 0.97938 | -0.14465 | 7.9113
17 | 0.042735 | 0.010723 | -0.042667 | -0.010698 | 6.7182e-05 | 2.5519e-05 | 0.064933 | 0.064933 | 0.064933 | 0.97938 | -0.14465 | 0.97779 | -0.15599 | 24.0494
18 | 0.012847 | 0.0032202 | -0.01284 | -0.0032181 | 6.3028e-06 | 2.0907e-06 | 0.019519 | 0.019519 | 0.019519 | 0.97938 | -0.14465 | 0.97888 | -0.14819 | 7.2292
19 | 0.017675 | 0.0044339 | -0.017657 | -0.0044274 | 1.8253e-05 | 6.5139e-06 | 0.026899 | 0.0269 | 0.0269 | 0.97779 | -0.15599 | 0.97675 | -0.16345 | 9.9628
20 | 0.017657 | 0.0044274 | -0.017637 | -0.0044204 | 1.94e-05 | 6.9244e-06 | 0.0269 | 0.0269 | 0.0269 | 0.97675 | -0.16345 | 0.97564 | -0.17138 | 9.9629
21 | 0.014145 | 0.0035456 | -0.01414 | -0.0035438 | 5.2692e-06 | 1.8001e-06 | 0.021574 | 0.021574 | 0.021574 | 0.97564 | -0.17138 | 0.97527 | -0.17407 | 7.9904
22 | 0.0034919 | 0.0008748 | -0.0034918 | -0.00087483 | 8.2827e-08 | -2.6585e-08 | 0.0053256 | 0.0053256 | 0.0053256 | 0.97564 | -0.17138 | 0.97562 | -0.17155 | 1.9725
23 | 0.0017444 | 0.00043714 | -0.0017444 | -0.00043719 | 1.8978e-08 | -4.6325e-08 | 0.0026609 | 0.0026609 | 0.0026609 | 0.97549 | -0.17247 | 0.97548 | -0.17255 | 0.98553
24 | -0.0034914 | -0.00087497 | 0.0034918 | 0.00087483 | 4.4445e-07 | -1.426e-07 | 0.0053258 | 0.0053256 | 0.0053258 | 0.97549 | -0.17247 | 0.97562 | -0.17155 | 1.9725
25 | 0.0090989 | 0.0022804 | -0.0090974 | -0.00228 | 1.5472e-06 | 4.3456e-07 | 0.013883 | 0.013883 | 0.013883 | 0.97527 | -0.17407 | 0.97509 | -0.1753 | 5.1418
26 | 0.0064592 | 0.0016188 | -0.0064588 | -0.0016187 | 3.9101e-07 | 6.9942e-08 | 0.0098568 | 0.0098569 | 0.0098569 | 0.97509 | -0.1753 | 0.97503 | -0.17574 | 3.6507
27 | -0.22993 | -0.057877 | 0.23048 | 0.05809 | 0.00055559 | 0.0002128 | 0.34307 | 0.34307 | 0.34307 | 0.99751 | -0.01726 | 1 | 0 | 42.3549

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.2368 | 0.059474

## res_load
| p_mw | q_mvar
0 | 0.00096758 | 0.0002425
1 | 0.0035254 | 0.00088354
2 | 0.0041228 | 0.0010333
3 | 0.0023969 | 0.00060072
4 | 0.07358 | 0.018441
5 | 0.011161 | 0.0027972
6 | 0.003351 | 0.00083983
7 | 0.05275 | 0.01322
8 | 0.0065781 | 0.0016486
9 | 0.0087151 | 0.0021842
10 | 0.005336 | 0.0013373
11 | 0.024993 | 0.0062637
12 | 0.01284 | 0.0032181
13 | 0.001747 | 0.00043783
14 | 0.0017444 | 0.00043719
15 | 0.0050411 | 0.0012634
16 | 0.0026382 | 0.0006612
17 | 0.0064588 | 0.0016187
18 | 0.0055223 | 0.001384

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1