## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1404-4_1_2_node_6 | 0.4 | n |  | TRUE
1 | bus_LV_1404-4_1_2_node_7 | 0.4 | n |  | TRUE
2 | bus_LV_1404-4_1_2_node_8 | 0.4 | n |  | TRUE
3 | bus_LV_1404-4_1_2_node_9 | 0.4 | n |  | TRUE
4 | bus_LV_1404-4_1_2_node_10 | 0.4 | n |  | TRUE
5 | bus_LV_1404-4_1_2_node_11 | 0.4 | n |  | TRUE
6 | bus_LV_1404-4_1_2_node_22 | 0.4 | n |  | TRUE
7 | bus_LV_1404-4_1_2_node_28 | 0.4 | n |  | TRUE
8 | bus_LV_1404-4_1_2_node_12 | 0.4 | n |  | TRUE
9 | bus_LV_1404-4_1_2_node_13 | 0.4 | n |  | TRUE
10 | bus_LV_1404-4_1_2_node_14 | 0.4 | n |  | TRUE
11 | bus_LV_1404-4_1_2_node_15 | 0.4 | n |  | TRUE
12 | bus_LV_1404-4_1_2_node_16 | 0.4 | n |  | TRUE
13 | bus_LV_1404-4_1_2_node_17 | 0.4 | n |  | TRUE
14 | bus_LV_1404-4_1_2_node_18 | 0.4 | n |  | TRUE
15 | bus_LV_1404-4_1_2_node_19 | 0.4 | n |  | TRUE
16 | bus_LV_1404-4_1_2_node_23 | 0.4 | n |  | TRUE
17 | bus_LV_1404-4_1_2_node_20 | 0.4 | n |  | TRUE
18 | bus_LV_1404-4_1_2_node_24 | 0.4 | n |  | TRUE
19 | bus_LV_1404-4_1_2_node_25 | 0.4 | n |  | TRUE
20 | bus_LV_1404-4_1_2_node_94 | 0.4 | n |  | TRUE
21 | bus_LV_1404-4_1_2_node_99 | 0.4 | n |  | TRUE
22 | bus_LV_1404-4_1_2_node_26 | 0.4 | n |  | TRUE
23 | bus_LV_1404-4_1_2_node_27 | 0.4 | n |  | TRUE
24 | bus_LV_1404-4_1_2_node_103 | 0.4 | n |  | TRUE
25 | bus_LV_1404-4_1_2_node_86 | 0.4 | n |  | TRUE
26 | bus_LV_1404-4_1_2_node_87 | 0.4 | n |  | TRUE
27 | bus_LV_1404-4_1_2_node_88 | 0.4 | n |  | TRUE
28 | bus_LV_1404-4_1_2_node_89 | 0.4 | n |  | TRUE
29 | bus_LV_1404-4_1_2_node_90 | 0.4 | n |  | TRUE
30 | bus_LV_1404-4_1_2_node_93 | 0.4 | n |  | TRUE
31 | bus_LV_1404-4_1_2_node_91 | 0.4 | n |  | TRUE
32 | bus_LV_1404-4_1_2_node_92 | 0.4 | n |  | TRUE
33 | bus_LV_1404-4_1_2_node_97 | 0.4 | n |  | TRUE
34 | bus_LV_1404-4_1_2_node_100 | 0.4 | n |  | TRUE
35 | bus_LV_1404-4_1_2_node_95 | 0.4 | n |  | TRUE
36 | bus_LV_1404-4_1_2_node_98 | 0.4 | n |  | TRUE
37 | bus_LV_1404-4_1_2_node_101 | 0.4 | n |  | TRUE
38 | bus_LV_1404-4_1_2_node_102 | 0.4 | n |  | TRUE
39 | bus_MV_140_0_node_60 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1404-4_1_2_load_6 | 0 | 0.0025273 | 0.00063339 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1404-4_1_2_load_7 | 1 | 0.0011314 | 0.00028355 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1404-4_1_2_load_9 | 3 | 0.0010921 | 0.00027371 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1404-4_1_2_load_11 | 5 | 0.0010924 | 0.00027377 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1404-4_1_2_load_22 | 6 | 0.0011323 | 0.00028379 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1404-4_1_2_load_28 | 7 | 0.0057339 | 0.0014371 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1404-4_1_2_load_12 | 8 | 0.0010925 | 0.00027381 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1404-4_1_2_load_13 | 9 | 0.0011313 | 0.00028353 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1404-4_1_2_load_14 | 10 | 0.0016587 | 0.00041572 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1404-4_1_2_load_15 | 11 | 0.0026206 | 0.00065678 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1404-4_1_2_load_17 | 13 | 0.0014011 | 0.00035114 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1404-4_1_2_load_18 | 14 | 0.0029897 | 0.0007493 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1404-4_1_2_load_19 | 15 | 0.0041633 | 0.0010434 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1404-4_1_2_load_20 | 17 | 0.0018562 | 0.0004652 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1404-4_1_2_load_24 | 18 | 0.00069706 | 0.0001747 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1404-4_1_2_load_25 | 19 | 0.00082166 | 0.00020593 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1404-4_1_2_load_94 | 20 | 0.0039241 | 0.00098348 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1404-4_1_2_load_26 | 22 | 0.0017213 | 0.00043139 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1404-4_1_2_load_27 | 23 | 0.0012124 | 0.00030385 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1404-4_1_2_load_103 | 24 | 0.0059196 | 0.0014836 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1404-4_1_2_load_86 | 25 | 0.0038242 | 0.00095843 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1404-4_1_2_load_87 | 26 | 0.0027252 | 0.00068299 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1404-4_1_2_load_89 | 28 | 0.0028323 | 0.00070984 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1404-4_1_2_load_90 | 29 | 0.0023092 | 0.00057875 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1404-4_1_2_load_93 | 30 | 0.0022139 | 0.00055486 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1404-4_1_2_load_92 | 32 | 0.0021233 | 0.00053216 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1404-4_1_2_load_97 | 33 | 0.011429 | 0.0028644 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1404-4_1_2_load_95 | 35 | 0.0064362 | 0.0016131 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1404-4_1_2_load_98 | 36 | 0.0011613 | 0.00029105 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1404-4_1_2_load_101 | 37 | 0.0035354 | 0.00088606 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1404-4_1_2_load_102 | 38 | 0.0075637 | 0.0018956 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 19 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1404-4_1_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.010205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1404-4_1_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.01781 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1404-4_1_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.020947 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1404-4_1_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.06978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1404-4_1_2_line_4 | NAYY 4x150 SE | 2 | 5 | 0.023518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1404-4_1_2_line_5 | NAYY 4x150 SE | 3 | 6 | 0.0072515 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1404-4_1_2_line_6 | NAYY 4x150 SE | 4 | 7 | 0.025747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1404-4_1_2_line_7 | NAYY 4x150 SE | 5 | 8 | 0.031762 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1404-4_1_2_line_8 | NAYY 4x150 SE | 7 | 23 | 0.022401 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1404-4_1_2_line_9 | NAYY 4x150 SE | 8 | 9 | 0.0053157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1404-4_1_2_line_10 | NAYY 4x150 SE | 9 | 10 | 0.024017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1404-4_1_2_line_11 | NAYY 4x150 SE | 10 | 11 | 0.019042 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1404-4_1_2_line_12 | NAYY 4x150 SE | 11 | 12 | 0.01922 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1404-4_1_2_line_13 | NAYY 4x150 SE | 12 | 13 | 0.0028053 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1404-4_1_2_line_14 | NAYY 4x150 SE | 12 | 14 | 0.027808 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1404-4_1_2_line_15 | NAYY 4x150 SE | 13 | 15 | 0.039686 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1404-4_1_2_line_16 | NAYY 4x150 SE | 14 | 16 | 0.063455 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1404-4_1_2_line_17 | NAYY 4x150 SE | 15 | 17 | 0.021969 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1404-4_1_2_line_18 | NAYY 4x150 SE | 16 | 18 | 0.028376 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1404-4_1_2_line_19 | NAYY 4x150 SE | 16 | 19 | 0.13744 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1404-4_1_2_line_20 | NAYY 4x150 SE | 18 | 20 | 0.12771 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1404-4_1_2_line_21 | NAYY 4x150 SE | 19 | 21 | 0.0078201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1404-4_1_2_line_22 | NAYY 4x150 SE | 20 | 35 | 0.0023843 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1404-4_1_2_line_23 | NAYY 4x150 SE | 21 | 36 | 0.025182 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1404-4_1_2_line_24 | NAYY 4x150 SE | 22 | 23 | 0.0064872 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1404-4_1_2_line_25 | NAYY 4x150 SE | 22 | 24 | 0.10781 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1404-4_1_2_line_26 | NAYY 4x150 SE | 25 | 26 | 0.075184 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1404-4_1_2_line_27 | NAYY 4x150 SE | 25 | 27 | 0.033881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1404-4_1_2_line_28 | NAYY 4x150 SE | 26 | 28 | 0.041966 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1404-4_1_2_line_29 | NAYY 4x150 SE | 27 | 29 | 0.018082 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1404-4_1_2_line_30 | NAYY 4x150 SE | 28 | 30 | 0.049518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1404-4_1_2_line_31 | NAYY 4x150 SE | 29 | 31 | 0.14736 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1404-4_1_2_line_32 | NAYY 4x150 SE | 30 | 34 | 0.16264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1404-4_1_2_line_33 | NAYY 4x150 SE | 31 | 32 | 0.025545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1404-4_1_2_line_34 | NAYY 4x150 SE | 32 | 33 | 0.023775 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1404-4_1_2_line_35 | NAYY 4x150 SE | 34 | 37 | 0.029703 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1404-4_1_2_line_36 | NAYY 4x150 SE | 34 | 38 | 0.033973 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1404-4_1_2_line_37 | NAYY 4x150 SE | 34 | 36 | 0.046595 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1404-4_1_2_trafo_25 | 0.25 MVA 20/0.4 kV | 39 | 19 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2662788.6023 | 1194394.8672 | 2662778.7436 | 1194397.5037
1 | 2662805.9932 | 1194391.1033 | 2662796.1213 | 1194392.8563 | 2662788.6023 | 1194394.8672
2 | 2662778.7436 | 1194397.5037 | 2662758.5075 | 1194402.9155
3 | 2662805.9932 | 1194391.1033 | 2662814.0423 | 1194390.2095 | 2662819.5227 | 1194390.0892 | 2662827.3596 | 1194390.5384 | 2662834.4355 | 1194391.6133 | 2662842.2515 | 1194393.3186 | 2662848.941 | 1194395.6235 | 2662860.0352 | 1194400.8319 | 2662872.3476 | 1194407.5874
4 | 2662805.9932 | 1194391.1033 | 2662806.4478 | 1194397.1561 | 2662803.96 | 1194414.4259
5 | 2662758.5075 | 1194402.9155 | 2662751.5022 | 1194404.789
6 | 2662872.3476 | 1194407.5874 | 2662894.4887 | 1194420.7289
7 | 2662796.4909 | 1194445.0735 | 2662797.0846 | 1194444.0963 | 2662799.7407 | 1194437.8983 | 2662801.7543 | 1194429.7369 | 2662803.96 | 1194414.4259
8 | 2662894.4887 | 1194420.7289 | 2662913.752 | 1194432.1623
9 | 2662796.4909 | 1194445.0735 | 2662793.731 | 1194449.6165
10 | 2662780.5261 | 1194469.6024 | 2662783.964 | 1194465.6934 | 2662793.731 | 1194449.6165
11 | 2662780.5261 | 1194469.6024 | 2662767.951 | 1194483.901
12 | 2662755.258 | 1194498.3336 | 2662767.951 | 1194483.901
13 | 2662755.258 | 1194498.3336 | 2662754.1523 | 1194495.7554
14 | 2662755.258 | 1194498.3336 | 2662768.3632 | 1194522.8604
15 | 2662754.1523 | 1194495.7554 | 2662745.5731 | 1194475.7522 | 2662734.0501 | 1194462.0277
16 | 2662800.7832 | 1194577.3794 | 2662776.513 | 1194538.113 | 2662768.3632 | 1194522.8604
17 | 2662734.0501 | 1194462.0277 | 2662728.0289 | 1194454.8561 | 2662720.7379 | 1194444.5743
18 | 2662800.7832 | 1194577.3794 | 2662782.7554 | 1194578.6465 | 2662772.7523 | 1194581.1165
19 | 2662800.7832 | 1194577.3794 | 2662797.0893 | 1194595.34 | 2662794.8944 | 1194628.7475 | 2662811.1873 | 1194664.9619 | 2662820.6277 | 1194689.731 | 2662823.8376 | 1194708.8704
20 | 2662652.7844 | 1194611.3232 | 2662673.9893 | 1194617.2734 | 2662696.3437 | 1194611.7933 | 2662720.044 | 1194599.3343 | 2662753.3867 | 1194585.8983 | 2662772.7523 | 1194581.1165
21 | 2662825.1311 | 1194716.5828 | 2662823.8376 | 1194708.8704
22 | 2662650.4888 | 1194610.679 | 2662652.7844 | 1194611.3232
23 | 2662825.1311 | 1194716.5828 | 2662832.3109 | 1194717.1585 | 2662842.8747 | 1194722.0167 | 2662846.6356 | 1194727.1351
24 | 2662919.3305 | 1194435.4734 | 2662913.752 | 1194432.1623
25 | 2662919.3305 | 1194435.4734 | 2662967.5381 | 1194531.9052
26 | 2663123.6537 | 1194940.1718 | 2663116.4881 | 1194929.6397 | 2663099.8001 | 1194898.6234 | 2663086.1571 | 1194875.0634
27 | 2663145.1234 | 1194965.0291 | 2663137.8037 | 1194961.8611 | 2663132.8682 | 1194953.7154 | 2663123.6537 | 1194940.1718
28 | 2663086.1571 | 1194875.0634 | 2663083.8525 | 1194871.0836 | 2663062.402 | 1194851.5906 | 2663055.6931 | 1194846.5648
29 | 2663145.1234 | 1194965.0291 | 2663142.2528 | 1194980.708 | 2663141.2132 | 1194982.5811
30 | 2663055.6931 | 1194846.5648 | 2663030.5504 | 1194827.73 | 2663015.5775 | 1194817.5552
31 | 2663010.1236 | 1195037.226 | 2663016.0725 | 1195038.8785 | 2663027.3557 | 1195037.5855 | 2663069.5192 | 1195026.4343 | 2663081.3268 | 1195023.1124 | 2663092.6161 | 1195019.0846 | 2663108.6158 | 1195011.3266 | 2663122.9912 | 1195002.2396 | 2663130.2332 | 1194996.8906 | 2663137.5845 | 1194989.1192 | 2663141.2132 | 1194982.5811
32 | 2662859.7334 | 1194771.0446 | 2663015.5775 | 1194817.5552
33 | 2663010.1236 | 1195037.226 | 2663007.4067 | 1195036.9083 | 2662995.976 | 1195029.7727 | 2662988.5168 | 1195024.1616
34 | 2662969.0678 | 1195010.4893 | 2662986.4127 | 1195022.5789 | 2662988.5168 | 1195024.1616
35 | 2662842.8568 | 1194795.5149 | 2662859.7334 | 1194771.0446
36 | 2662833.2221 | 1194752.2774 | 2662843.7692 | 1194754.3783 | 2662854.3591 | 1194763.2725 | 2662859.7334 | 1194771.0446
37 | 2662859.7334 | 1194771.0446 | 2662859.5934 | 1194759.7143 | 2662856.2653 | 1194747.2053 | 2662848.374 | 1194729.501 | 2662846.6356 | 1194727.1351

## bus_geodata
| x | y | coords
0 | 2662788.6023 | 1194394.8672
1 | 2662778.7436 | 1194397.5037
2 | 2662805.9932 | 1194391.1033
3 | 2662758.5075 | 1194402.9155
4 | 2662872.3476 | 1194407.5874
5 | 2662803.96 | 1194414.4259
6 | 2662751.5022 | 1194404.789
7 | 2662894.4887 | 1194420.7289
8 | 2662796.4909 | 1194445.0735
9 | 2662793.731 | 1194449.6165
10 | 2662780.5261 | 1194469.6024
11 | 2662767.951 | 1194483.901
12 | 2662755.258 | 1194498.3336
13 | 2662754.1523 | 1194495.7554
14 | 2662768.3632 | 1194522.8604
15 | 2662734.0501 | 1194462.0277
16 | 2662800.7832 | 1194577.3794
17 | 2662720.7379 | 1194444.5743
18 | 2662772.7523 | 1194581.1165
19 | 2662823.8376 | 1194708.8704
20 | 2662652.7844 | 1194611.3232
21 | 2662825.1311 | 1194716.5828
22 | 2662919.3305 | 1194435.4734
23 | 2662913.752 | 1194432.1623
24 | 2662967.5381 | 1194531.9052
25 | 2663123.6537 | 1194940.1718
26 | 2663086.1571 | 1194875.0634
27 | 2663145.1234 | 1194965.0291
28 | 2663055.6931 | 1194846.5648
29 | 2663141.2132 | 1194982.5811
30 | 2663015.5775 | 1194817.5552
31 | 2663010.1236 | 1195037.226
32 | 2662988.5168 | 1195024.1616
33 | 2662969.0678 | 1195010.4893
34 | 2662859.7334 | 1194771.0446
35 | 2662650.4888 | 1194610.679
36 | 2662846.6356 | 1194727.1351
37 | 2662842.8568 | 1194795.5149
38 | 2662833.2221 | 1194752.2774
39 | 2662825.1311 | 1194716.5828

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9808 | -0.13474 | 0.0025273 | 0.00063339
1 | 0.98075 | -0.1351 | 0.0011314 | 0.00028355
2 | 0.98095 | -0.13366 | 0 | 0
3 | 0.98069 | -0.13558 | 0.0010921 | 0.00027371
4 | 0.97947 | -0.14424 | 0 | 0
5 | 0.98166 | -0.12866 | 0.0010924 | 0.00027377
6 | 0.98067 | -0.13567 | 0.0011323 | 0.00028379
7 | 0.97892 | -0.14816 | 0.0057339 | 0.0014371
8 | 0.98265 | -0.12156 | 0.0010925 | 0.00027381
9 | 0.98283 | -0.12032 | 0.0011313 | 0.00028353
10 | 0.98366 | -0.11441 | 0.0016587 | 0.00041572
11 | 0.98436 | -0.10941 | 0.0026206 | 0.00065678
12 | 0.98515 | -0.10385 | 0 | 0
13 | 0.98512 | -0.10406 | 0.0014011 | 0.00035114
14 | 0.98658 | -0.093704 | 0.0029897 | 0.0007493
15 | 0.98477 | -0.10652 | 0.0041633 | 0.0010434
16 | 0.99013 | -0.068727 | 0 | 0
17 | 0.98471 | -0.10694 | 0.0018562 | 0.0004652
18 | 0.98967 | -0.071927 | 0.00069706 | 0.0001747
19 | 1 | 0 | -0.09142 | -0.022875
20 | 0.98777 | -0.085443 | 0.0039241 | 0.00098348
21 | 0.99955 | -0.0031066 | 0 | 0
22 | 0.97856 | -0.15074 | 0.0017213 | 0.00043139
23 | 0.97864 | -0.15022 | 0.0012124 | 0.00030385
24 | 0.97763 | -0.1574 | 0.0059196 | 0.0014836
25 | 0.98369 | -0.11425 | 0.0038242 | 0.00095843
26 | 0.98585 | -0.099 | 0.0027252 | 0.00068299
27 | 0.98291 | -0.11981 | 0 | 0
28 | 0.98721 | -0.089342 | 0.0028323 | 0.00070984
29 | 0.98249 | -0.12278 | 0.0023092 | 0.00057875
30 | 0.98903 | -0.076546 | 0.0022139 | 0.00055486
31 | 0.97958 | -0.1435 | 0 | 0
32 | 0.97908 | -0.14711 | 0.0021233 | 0.00053216
33 | 0.97869 | -0.14994 | 0.011429 | 0.0028644
34 | 0.99551 | -0.031203 | 0 | 0
35 | 0.98774 | -0.0856 | 0.0064362 | 0.0016131
36 | 0.99811 | -0.013129 | 0.0011613 | 0.00029105
37 | 0.99536 | -0.032261 | 0.0035354 | 0.00088606
38 | 0.99514 | -0.033793 | 0.0075637 | 0.0018956
39 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0033562 | 0.0008407 | -0.003356 | -0.00084076 | 1.6509e-07 | -6.529e-08 | 0.0050916 | 0.0050917 | 0.0050917 | 0.9808 | -0.13474 | 0.98075 | -0.1351 | 1.8858
1 | -0.0058834 | -0.0014741 | 0.0058843 | 0.0014742 | 8.8539e-07 | 1.1573e-07 | 0.0089259 | 0.0089258 | 0.0089259 | 0.9808 | -0.13474 | 0.98095 | -0.13366 | 3.3059
2 | 0.0022246 | 0.00055721 | -0.0022245 | -0.00055742 | 1.489e-07 | -2.0705e-07 | 0.0033751 | 0.0033752 | 0.0033752 | 0.98075 | -0.1351 | 0.98069 | -0.13558 | 1.2501
3 | 0.014625 | 0.0036675 | -0.014604 | -0.0036602 | 2.1432e-05 | 7.3635e-06 | 0.022186 | 0.022186 | 0.022186 | 0.98095 | -0.13366 | 0.97947 | -0.14424 | 8.217
4 | -0.020509 | -0.0051417 | 0.020524 | 0.0051469 | 1.4204e-05 | 5.1661e-06 | 0.031111 | 0.031111 | 0.031111 | 0.98095 | -0.13366 | 0.98166 | -0.12866 | 11.5227
5 | 0.0011324 | 0.0002837 | -0.0011323 | -0.00028379 | 1.3357e-08 | -8.6357e-08 | 0.0017181 | 0.0017181 | 0.0017181 | 0.98069 | -0.13558 | 0.98067 | -0.13567 | 0.63635
6 | 0.014604 | 0.0036602 | -0.014596 | -0.0036575 | 7.9081e-06 | 2.7177e-06 | 0.022186 | 0.022186 | 0.022186 | 0.97947 | -0.14424 | 0.97892 | -0.14816 | 8.2171
7 | -0.021616 | -0.0054207 | 0.021637 | 0.0054285 | 2.128e-05 | 7.7825e-06 | 0.032767 | 0.032767 | 0.032767 | 0.98166 | -0.12866 | 0.98265 | -0.12156 | 12.136
8 | 0.0088618 | 0.0022204 | -0.0088592 | -0.0022197 | 2.5363e-06 | 6.9395e-07 | 0.01347 | 0.01347 | 0.01347 | 0.97892 | -0.14816 | 0.97864 | -0.15022 | 4.989
9 | -0.02273 | -0.0057023 | 0.022734 | 0.0057037 | 3.9301e-06 | 1.4442e-06 | 0.034421 | 0.034421 | 0.034421 | 0.98265 | -0.12156 | 0.98283 | -0.12032 | 12.7486
10 | -0.023865 | -0.0059873 | 0.023885 | 0.0059945 | 1.9568e-05 | 7.2214e-06 | 0.036134 | 0.036134 | 0.036134 | 0.98283 | -0.12032 | 0.98366 | -0.11441 | 13.383
11 | -0.025543 | -0.0064102 | 0.025561 | 0.0064168 | 1.7743e-05 | 6.5825e-06 | 0.038643 | 0.038643 | 0.038643 | 0.98366 | -0.11441 | 0.98436 | -0.10941 | 14.3123
12 | -0.028182 | -0.0070736 | 0.028203 | 0.0070817 | 2.177e-05 | 8.1284e-06 | 0.042605 | 0.042605 | 0.042605 | 0.98436 | -0.10941 | 0.98515 | -0.10385 | 15.7795
13 | 0.0074229 | 0.0018599 | -0.0074227 | -0.0018598 | 2.2004e-07 | 4.8915e-08 | 0.011212 | 0.011212 | 0.011212 | 0.98515 | -0.10385 | 0.98512 | -0.10406 | 4.1525
14 | -0.035626 | -0.0089415 | 0.035677 | 0.0089605 | 5.0256e-05 | 1.8975e-05 | 0.053816 | 0.053816 | 0.053816 | 0.98515 | -0.10385 | 0.98658 | -0.093704 | 19.932
15 | 0.0060216 | 0.0015087 | -0.0060196 | -0.0015084 | 2.0487e-06 | 2.8287e-07 | 0.0090955 | 0.0090957 | 0.0090957 | 0.98512 | -0.10406 | 0.98477 | -0.10652 | 3.3688
16 | -0.038666 | -0.0097098 | 0.038801 | 0.0097608 | 0.0001347 | 5.0994e-05 | 0.058325 | 0.058325 | 0.058325 | 0.98658 | -0.093704 | 0.99013 | -0.068727 | 21.602
17 | 0.0018563 | 0.00046496 | -0.0018562 | -0.0004652 | 1.0785e-07 | -2.3801e-07 | 0.0028048 | 0.0028049 | 0.0028049 | 0.98477 | -0.10652 | 0.98471 | -0.10694 | 1.0388
18 | 0.011082 | 0.0027786 | -0.011077 | -0.0027771 | 4.9115e-06 | 1.5243e-06 | 0.016655 | 0.016655 | 0.016655 | 0.99013 | -0.068727 | 0.98967 | -0.071927 | 6.1685
19 | -0.049883 | -0.012539 | 0.050365 | 0.012723 | 0.00048215 | 0.00018366 | 0.07498 | 0.074979 | 0.07498 | 0.99013 | -0.068727 | 1 | 0 | 27.7704
20 | 0.01038 | 0.0026024 | -0.01036 | -0.0025966 | 1.9412e-05 | 5.8281e-06 | 0.015607 | 0.015607 | 0.015607 | 0.98967 | -0.071927 | 0.98777 | -0.085443 | 5.7806
21 | 0.040255 | 0.010152 | -0.040238 | -0.010145 | 1.7522e-05 | 6.6366e-06 | 0.059923 | 0.059923 | 0.059923 | 1 | 0 | 0.99955 | -0.0031066 | 22.1936
22 | 0.0064363 | 0.0016131 | -0.0064362 | -0.0016131 | 1.3987e-07 | 2.3278e-08 | 0.009696 | 0.009696 | 0.009696 | 0.98777 | -0.085443 | 0.98774 | -0.0856 | 3.5911
23 | 0.040238 | 0.010145 | -0.040181 | -0.010124 | 5.6423e-05 | 2.1371e-05 | 0.059923 | 0.059923 | 0.059923 | 0.99955 | -0.0031066 | 0.99811 | -0.013129 | 22.1936
24 | -0.0076463 | -0.0019157 | 0.0076469 | 0.0019159 | 5.4722e-07 | 1.2897e-07 | 0.011627 | 0.011627 | 0.011627 | 0.97856 | -0.15074 | 0.97864 | -0.15022 | 4.3062
25 | 0.0059251 | 0.0014843 | -0.0059196 | -0.0014836 | 5.461e-06 | 7.4726e-07 | 0.0090095 | 0.00901 | 0.00901 | 0.97856 | -0.15074 | 0.97763 | -0.1574 | 3.337
26 | -0.019755 | -0.0049571 | 0.019797 | 0.0049723 | 4.19e-05 | 1.5159e-05 | 0.029885 | 0.029885 | 0.029885 | 0.98369 | -0.11425 | 0.98585 | -0.099 | 11.0685
27 | 0.015931 | 0.0039987 | -0.015918 | -0.0039944 | 1.228e-05 | 4.2932e-06 | 0.0241 | 0.0241 | 0.0241 | 0.98369 | -0.11425 | 0.98291 | -0.11981 | 8.9261
28 | -0.022522 | -0.0056553 | 0.022552 | 0.0056664 | 3.0268e-05 | 1.1106e-05 | 0.033998 | 0.033998 | 0.033998 | 0.98585 | -0.099 | 0.98721 | -0.089342 | 12.5918
29 | 0.015918 | 0.0039944 | -0.015912 | -0.0039921 | 6.5535e-06 | 2.2915e-06 | 0.0241 | 0.0241 | 0.0241 | 0.98291 | -0.11981 | 0.98249 | -0.12278 | 8.9261
30 | -0.025384 | -0.0063762 | 0.02543 | 0.006393 | 4.5247e-05 | 1.6768e-05 | 0.038267 | 0.038267 | 0.038267 | 0.98721 | -0.089342 | 0.98903 | -0.076546 | 14.1729
31 | 0.013603 | 0.0034134 | -0.013564 | -0.0034002 | 3.9034e-05 | 1.3153e-05 | 0.020603 | 0.020604 | 0.020604 | 0.98249 | -0.12278 | 0.97958 | -0.1435 | 7.631
32 | -0.027644 | -0.0069479 | 0.027819 | 0.0070133 | 0.0001756 | 6.5438e-05 | 0.041597 | 0.041597 | 0.041597 | 0.98903 | -0.076546 | 0.99551 | -0.031203 | 15.4065
33 | 0.013564 | 0.0034002 | -0.013557 | -0.0033979 | 6.7667e-06 | 2.2811e-06 | 0.020604 | 0.020604 | 0.020604 | 0.97958 | -0.1435 | 0.97908 | -0.14711 | 7.631
34 | 0.011433 | 0.0028658 | -0.011429 | -0.0028644 | 4.4797e-06 | 1.4241e-06 | 0.017377 | 0.017377 | 0.017377 | 0.97908 | -0.14711 | 0.97869 | -0.14994 | 6.4359
35 | 0.003536 | 0.00088588 | -0.0035354 | -0.00088606 | 5.1775e-07 | -1.87e-07 | 0.0052852 | 0.0052853 | 0.0052853 | 0.99551 | -0.031203 | 0.99536 | -0.032261 | 1.9575
36 | 0.0075664 | 0.0018962 | -0.0075637 | -0.0018956 | 2.7116e-06 | 6.0138e-07 | 0.01131 | 0.01131 | 0.01131 | 0.99551 | -0.031203 | 0.99514 | -0.033793 | 4.1888
37 | -0.038922 | -0.0097954 | 0.03902 | 0.0098327 | 9.8455e-05 | 3.726e-05 | 0.058192 | 0.058191 | 0.058192 | 0.99551 | -0.031203 | 0.99811 | -0.013129 | 21.5524

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.092242 | 0.023081

## res_load
| p_mw | q_mvar
0 | 0.0025273 | 0.00063339
1 | 0.0011314 | 0.00028355
2 | 0.0010921 | 0.00027371
3 | 0.0010924 | 0.00027377
4 | 0.0011323 | 0.00028379
5 | 0.0057339 | 0.0014371
6 | 0.0010925 | 0.00027381
7 | 0.0011313 | 0.00028353
8 | 0.0016587 | 0.00041572
9 | 0.0026206 | 0.00065678
10 | 0.0014011 | 0.00035114
11 | 0.0029897 | 0.0007493
12 | 0.0041633 | 0.0010434
13 | 0.0018562 | 0.0004652
14 | 0.00069706 | 0.0001747
15 | 0.00082166 | 0.00020593
16 | 0.0039241 | 0.00098348
17 | 0.0017213 | 0.00043139
18 | 0.0012124 | 0.00030385
19 | 0.0059196 | 0.0014836
20 | 0.0038242 | 0.00095843
21 | 0.0027252 | 0.00068299
22 | 0.0028323 | 0.00070984
23 | 0.0023092 | 0.00057875
24 | 0.0022139 | 0.00055486
25 | 0.0021233 | 0.00053216
26 | 0.011429 | 0.0028644
27 | 0.0064362 | 0.0016131
28 | 0.0011613 | 0.00029105
29 | 0.0035354 | 0.00088606
30 | 0.0075637 | 0.0018956

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1