## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1404-7_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1404-7_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1404-7_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1404-7_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1404-7_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1404-7_0_3_node_10 | 0.4 | n |  | TRUE
6 | bus_LV_1404-7_0_3_node_21 | 0.4 | n |  | TRUE
7 | bus_LV_1404-7_0_3_node_28 | 0.4 | n |  | TRUE
8 | bus_LV_1404-7_0_3_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_1404-7_0_3_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_1404-7_0_3_node_22 | 0.4 | n |  | TRUE
11 | bus_LV_1404-7_0_3_node_29 | 0.4 | n |  | TRUE
12 | bus_LV_1404-7_0_3_node_5 | 0.4 | n |  | TRUE
13 | bus_LV_1404-7_0_3_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_1404-7_0_3_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_1404-7_0_3_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_1404-7_0_3_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_1404-7_0_3_node_23 | 0.4 | n |  | TRUE
18 | bus_LV_1404-7_0_3_node_19 | 0.4 | n |  | TRUE
19 | bus_LV_1404-7_0_3_node_34 | 0.4 | n |  | TRUE
20 | bus_LV_1404-7_0_3_node_20 | 0.4 | n |  | TRUE
21 | bus_LV_1404-7_0_3_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_1404-7_0_3_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_1404-7_0_3_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_1404-7_0_3_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_1404-7_0_3_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_1404-7_0_3_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_1404-7_0_3_node_68 | 0.4 | n |  | TRUE
28 | bus_LV_1404-7_0_3_node_37 | 0.4 | n |  | TRUE
29 | bus_LV_1404-7_0_3_node_69 | 0.4 | n |  | TRUE
30 | bus_LV_1404-7_0_3_node_38 | 0.4 | n |  | TRUE
31 | bus_LV_1404-7_0_3_node_104 | 0.4 | n |  | TRUE
32 | bus_LV_1404-7_0_3_node_102 | 0.4 | n |  | TRUE
33 | bus_LV_1404-7_0_3_node_26 | 0.4 | n |  | TRUE
34 | bus_LV_1404-7_0_3_node_32 | 0.4 | n |  | TRUE
35 | bus_LV_1404-7_0_3_node_24 | 0.4 | n |  | TRUE
36 | bus_LV_1404-7_0_3_node_25 | 0.4 | n |  | TRUE
37 | bus_LV_1404-7_0_3_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_1404-7_0_3_node_45 | 0.4 | n |  | TRUE
39 | bus_LV_1404-7_0_3_node_35 | 0.4 | n |  | TRUE
40 | bus_LV_1404-7_0_3_node_105 | 0.4 | n |  | TRUE
41 | bus_LV_1404-7_0_3_node_106 | 0.4 | n |  | TRUE
42 | bus_LV_1404-7_0_3_node_65 | 0.4 | n |  | TRUE
43 | bus_LV_1404-7_0_3_node_30 | 0.4 | n |  | TRUE
44 | bus_LV_1404-7_0_3_node_31 | 0.4 | n |  | TRUE
45 | bus_LV_1404-7_0_3_node_33 | 0.4 | n |  | TRUE
46 | bus_LV_1404-7_0_3_node_36 | 0.4 | n |  | TRUE
47 | bus_LV_1404-7_0_3_node_46 | 0.4 | n |  | TRUE
48 | bus_LV_1404-7_0_3_node_77 | 0.4 | n |  | TRUE
49 | bus_LV_1404-7_0_3_node_53 | 0.4 | n |  | TRUE
50 | bus_LV_1404-7_0_3_node_51 | 0.4 | n |  | TRUE
51 | bus_LV_1404-7_0_3_node_52 | 0.4 | n |  | TRUE
52 | bus_LV_1404-7_0_3_node_54 | 0.4 | n |  | TRUE
53 | bus_LV_1404-7_0_3_node_55 | 0.4 | n |  | TRUE
54 | bus_LV_1404-7_0_3_node_50 | 0.4 | n |  | TRUE
55 | bus_LV_1404-7_0_3_node_39 | 0.4 | n |  | TRUE
56 | bus_LV_1404-7_0_3_node_40 | 0.4 | n |  | TRUE
57 | bus_LV_1404-7_0_3_node_41 | 0.4 | n |  | TRUE
58 | bus_LV_1404-7_0_3_node_42 | 0.4 | n |  | TRUE
59 | bus_LV_1404-7_0_3_node_110 | 0.4 | n |  | TRUE
60 | bus_LV_1404-7_0_3_node_62 | 0.4 | n |  | TRUE
61 | bus_LV_1404-7_0_3_node_114 | 0.4 | n |  | TRUE
62 | bus_LV_1404-7_0_3_node_61 | 0.4 | n |  | TRUE
63 | bus_LV_1404-7_0_3_node_43 | 0.4 | n |  | TRUE
64 | bus_LV_1404-7_0_3_node_44 | 0.4 | n |  | TRUE
65 | bus_LV_1404-7_0_3_node_96 | 0.4 | n |  | TRUE
66 | bus_LV_1404-7_0_3_node_94 | 0.4 | n |  | TRUE
67 | bus_LV_1404-7_0_3_node_100 | 0.4 | n |  | TRUE
68 | bus_LV_1404-7_0_3_node_103 | 0.4 | n |  | TRUE
69 | bus_LV_1404-7_0_3_node_98 | 0.4 | n |  | TRUE
70 | bus_LV_1404-7_0_3_node_101 | 0.4 | n |  | TRUE
71 | bus_LV_1404-7_0_3_node_95 | 0.4 | n |  | TRUE
72 | bus_LV_1404-7_0_3_node_97 | 0.4 | n |  | TRUE
73 | bus_LV_1404-7_0_3_node_75 | 0.4 | n |  | TRUE
74 | bus_LV_1404-7_0_3_node_47 | 0.4 | n |  | TRUE
75 | bus_LV_1404-7_0_3_node_48 | 0.4 | n |  | TRUE
76 | bus_LV_1404-7_0_3_node_49 | 0.4 | n |  | TRUE
77 | bus_LV_1404-7_0_3_node_116 | 0.4 | n |  | TRUE
78 | bus_LV_1404-7_0_3_node_117 | 0.4 | n |  | TRUE
79 | bus_LV_1404-7_0_3_node_56 | 0.4 | n |  | TRUE
80 | bus_LV_1404-7_0_3_node_57 | 0.4 | n |  | TRUE
81 | bus_LV_1404-7_0_3_node_59 | 0.4 | n |  | TRUE
82 | bus_LV_1404-7_0_3_node_60 | 0.4 | n |  | TRUE
83 | bus_LV_1404-7_0_3_node_63 | 0.4 | n |  | TRUE
84 | bus_LV_1404-7_0_3_node_64 | 0.4 | n |  | TRUE
85 | bus_LV_1404-7_0_3_node_66 | 0.4 | n |  | TRUE
86 | bus_LV_1404-7_0_3_node_67 | 0.4 | n |  | TRUE
87 | bus_LV_1404-7_0_3_node_107 | 0.4 | n |  | TRUE
88 | bus_LV_1404-7_0_3_node_108 | 0.4 | n |  | TRUE
89 | bus_LV_1404-7_0_3_node_70 | 0.4 | n |  | TRUE
90 | bus_LV_1404-7_0_3_node_71 | 0.4 | n |  | TRUE
91 | bus_LV_1404-7_0_3_node_72 | 0.4 | n |  | TRUE
92 | bus_LV_1404-7_0_3_node_73 | 0.4 | n |  | TRUE
93 | bus_LV_1404-7_0_3_node_74 | 0.4 | n |  | TRUE
94 | bus_LV_1404-7_0_3_node_76 | 0.4 | n |  | TRUE
95 | bus_LV_1404-7_0_3_node_78 | 0.4 | n |  | TRUE
96 | bus_LV_1404-7_0_3_node_79 | 0.4 | n |  | TRUE
97 | bus_LV_1404-7_0_3_node_80 | 0.4 | n |  | TRUE
98 | bus_LV_1404-7_0_3_node_81 | 0.4 | n |  | TRUE
99 | bus_LV_1404-7_0_3_node_82 | 0.4 | n |  | TRUE
100 | bus_LV_1404-7_0_3_node_90 | 0.4 | n |  | TRUE
101 | bus_LV_1404-7_0_3_node_91 | 0.4 | n |  | TRUE
102 | bus_LV_1404-7_0_3_node_83 | 0.4 | n |  | TRUE
103 | bus_LV_1404-7_0_3_node_84 | 0.4 | n |  | TRUE
104 | bus_LV_1404-7_0_3_node_85 | 0.4 | n |  | TRUE
105 | bus_LV_1404-7_0_3_node_89 | 0.4 | n |  | TRUE
106 | bus_LV_1404-7_0_3_node_87 | 0.4 | n |  | TRUE
107 | bus_LV_1404-7_0_3_node_86 | 0.4 | n |  | TRUE
108 | bus_LV_1404-7_0_3_node_88 | 0.4 | n |  | TRUE
109 | bus_LV_1404-7_0_3_node_93 | 0.4 | n |  | TRUE
110 | bus_LV_1404-7_0_3_node_99 | 0.4 | n |  | TRUE
111 | bus_LV_1404-7_0_3_node_109 | 0.4 | n |  | TRUE
112 | bus_LV_1404-7_0_3_node_111 | 0.4 | n |  | TRUE
113 | bus_LV_1404-7_0_3_node_112 | 0.4 | n |  | TRUE
114 | bus_LV_1404-7_0_3_node_113 | 0.4 | n |  | TRUE
115 | bus_LV_1404-7_0_3_node_115 | 0.4 | n |  | TRUE
116 | bus_MV_140_0_node_86 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1404-7_0_3_load_0 | 0 | 0.0009514 | 0.00023844 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1404-7_0_3_load_1 | 1 | 0.00073676 | 0.00018465 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1404-7_0_3_load_3 | 3 | 0.0026415 | 0.00066203 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1404-7_0_3_load_4 | 4 | 0.0014419 | 0.00036139 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1404-7_0_3_load_10 | 5 | 0.0008502 | 0.00021308 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1404-7_0_3_load_21 | 6 | 0.00086644 | 0.00021715 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1404-7_0_3_load_28 | 7 | 0.00078184 | 0.00019595 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1404-7_0_3_load_11 | 8 | 0.0012218 | 0.00030621 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1404-7_0_3_load_12 | 9 | 0.0026916 | 0.00067457 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1404-7_0_3_load_22 | 10 | 0.0008578 | 0.00021499 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1404-7_0_3_load_29 | 11 | 0.0017065 | 0.00042769 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1404-7_0_3_load_5 | 12 | 0.001298 | 0.00032532 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1404-7_0_3_load_6 | 13 | 0.00034686 | 8.6932e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1404-7_0_3_load_7 | 14 | 0.00094643 | 0.0002372 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1404-7_0_3_load_8 | 15 | 0.0011086 | 0.00027785 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1404-7_0_3_load_9 | 16 | 0.0013083 | 0.00032789 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1404-7_0_3_load_23 | 17 | 0.00054383 | 0.0001363 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1404-7_0_3_load_19 | 18 | 0.00035698 | 8.9467e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1404-7_0_3_load_20 | 20 | 0.0024197 | 0.00060644 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1404-7_0_3_load_13 | 21 | 0.00036847 | 9.2347e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1404-7_0_3_load_14 | 22 | 0.00020852 | 5.2261e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1404-7_0_3_load_16 | 24 | 0.00092553 | 0.00023196 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1404-7_0_3_load_18 | 26 | 0.000359 | 8.9975e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1404-7_0_3_load_68 | 27 | 0.00032565 | 8.1616e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1404-7_0_3_load_37 | 28 | 0.00040878 | 0.00010245 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1404-7_0_3_load_69 | 29 | 0.00050308 | 0.00012608 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1404-7_0_3_load_104 | 31 | 0.0012124 | 0.00030386 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1404-7_0_3_load_102 | 32 | 0.001471 | 0.00036867 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1404-7_0_3_load_26 | 33 | 0.00065219 | 0.00016345 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1404-7_0_3_load_32 | 34 | 0.0013204 | 0.00033092 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1404-7_0_3_load_24 | 35 | 0.00070164 | 0.00017585 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1404-7_0_3_load_27 | 37 | 0.0008831 | 0.00022133 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1404-7_0_3_load_45 | 38 | 0.002084 | 0.0005223 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1404-7_0_3_load_106 | 41 | 0.0015662 | 0.00039254 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1404-7_0_3_load_65 | 42 | 0.0034167 | 0.00085631 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1404-7_0_3_load_30 | 43 | 0.00083136 | 0.00020836 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1404-7_0_3_load_31 | 44 | 0.00084554 | 0.00021191 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1404-7_0_3_load_33 | 45 | 0.0010212 | 0.00025595 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1404-7_0_3_load_36 | 46 | 0.0018237 | 0.00045705 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1404-7_0_3_load_46 | 47 | 0.00065341 | 0.00016376 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1404-7_0_3_load_77 | 48 | 0.00019082 | 4.7823e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1404-7_0_3_load_53 | 49 | 0.002786 | 0.00069823 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1404-7_0_3_load_51 | 50 | 0.00088818 | 0.0002226 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1404-7_0_3_load_52 | 51 | 0.0006116 | 0.00015328 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1404-7_0_3_load_54 | 52 | 0.00062118 | 0.00015568 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1404-7_0_3_load_55 | 53 | 0.0006649 | 0.00016664 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1404-7_0_3_load_39 | 55 | 0.025317 | 0.006345 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1404-7_0_3_load_41 | 57 | 0.0044861 | 0.0011243 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1404-7_0_3_load_110 | 59 | 0.0074351 | 0.0018634 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1404-7_0_3_load_62 | 60 | 0.0077239 | 0.0019358 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1404-7_0_3_load_114 | 61 | 0.0029005 | 0.00072694 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1404-7_0_3_load_61 | 62 | 0.003192 | 0.0008 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1404-7_0_3_load_43 | 63 | 0.0014617 | 0.00036634 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1404-7_0_3_load_96 | 65 | 0.0023393 | 0.0005863 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1404-7_0_3_load_94 | 66 | 0.0021326 | 0.00053447 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1404-7_0_3_load_103 | 68 | 0.0013582 | 0.0003404 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1404-7_0_3_load_98 | 69 | 0.001453 | 0.00036416 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1404-7_0_3_load_101 | 70 | 0.001675 | 0.00041979 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1404-7_0_3_load_97 | 72 | 0.0013186 | 0.00033048 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1404-7_0_3_load_75 | 73 | 0.00036248 | 9.0845e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1404-7_0_3_load_47 | 74 | 0.00088251 | 0.00022118 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1404-7_0_3_load_49 | 76 | 0.00066587 | 0.00016688 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1404-7_0_3_load_116 | 77 | 0.0019496 | 0.00048862 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1404-7_0_3_load_117 | 78 | 0.0011681 | 0.00029275 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1404-7_0_3_load_56 | 79 | 0.0025419 | 0.00063707 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1404-7_0_3_load_59 | 81 | 0.0042832 | 0.0010735 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1404-7_0_3_load_60 | 82 | 0.0054705 | 0.001371 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1404-7_0_3_load_64 | 84 | 0.0023041 | 0.00057745 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1404-7_0_3_load_66 | 85 | 0.0024726 | 0.0006197 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1404-7_0_3_load_67 | 86 | 0.0069794 | 0.0017492 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1404-7_0_3_load_107 | 87 | 0.0054216 | 0.0013588 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1404-7_0_3_load_108 | 88 | 0.010527 | 0.0026384 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1404-7_0_3_load_70 | 89 | 0.0010065 | 0.00025224 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1404-7_0_3_load_71 | 90 | 0.00039297 | 9.8486e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1404-7_0_3_load_72 | 91 | 0.00044617 | 0.00011182 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1404-7_0_3_load_73 | 92 | 0.00019438 | 4.8715e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1404-7_0_3_load_76 | 94 | 0.0029582 | 0.00074138 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1404-7_0_3_load_78 | 95 | 0.00059145 | 0.00014823 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1404-7_0_3_load_79 | 96 | 0.0014139 | 0.00035435 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1404-7_0_3_load_81 | 98 | 0.0026261 | 0.00065817 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1404-7_0_3_load_82 | 99 | 0.0010138 | 0.00025407 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1404-7_0_3_load_90 | 100 | 0.0017796 | 0.000446 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1404-7_0_3_load_91 | 101 | 0.0012797 | 0.00032072 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1404-7_0_3_load_84 | 103 | 0.0040677 | 0.0010195 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1404-7_0_3_load_85 | 104 | 0.0013537 | 0.00033926 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1404-7_0_3_load_89 | 105 | 0.00094905 | 0.00023785 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1404-7_0_3_load_87 | 106 | 0.0005611 | 0.00014063 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1404-7_0_3_load_86 | 107 | 0.0012425 | 0.0003114 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1404-7_0_3_load_88 | 108 | 0.00058534 | 0.0001467 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1404-7_0_3_load_93 | 109 | 0.0029127 | 0.00072999 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1404-7_0_3_load_109 | 111 | 0.0098088 | 0.0024583 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1404-7_0_3_load_111 | 112 | 0.0070076 | 0.0017563 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1404-7_0_3_load_112 | 113 | 0.0027361 | 0.00068573 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1404-7_0_3_load_113 | 114 | 0.007161 | 0.0017947 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1404-7_0_3_load_115 | 115 | 0.0059583 | 0.0014933 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 7 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1404-7_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0010021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1404-7_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.050375 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1404-7_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.018707 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1404-7_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.019559 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1404-7_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.093939 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1404-7_0_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.0013962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1404-7_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.058256 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1404-7_0_3_line_7 | NAYY 4x150 SE | 5 | 8 | 0.012818 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1404-7_0_3_line_8 | NAYY 4x150 SE | 6 | 10 | 0.011176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1404-7_0_3_line_9 | NAYY 4x150 SE | 7 | 11 | 0.012862 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
10 | LV_1404-7_0_3_line_10 | NAYY 4x150 SE | 8 | 9 | 0.023691 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1404-7_0_3_line_11 | NAYY 4x150 SE | 9 | 18 | 0.095832 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1404-7_0_3_line_12 | NAYY 4x150 SE | 10 | 31 | 0.025186 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1404-7_0_3_line_13 | NAYY 4x150 SE | 11 | 40 | 0.012085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
14 | LV_1404-7_0_3_line_14 | NAYY 4x150 SE | 12 | 13 | 0.010248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1404-7_0_3_line_15 | NAYY 4x150 SE | 12 | 14 | 0.033558 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1404-7_0_3_line_16 | NAYY 4x150 SE | 13 | 15 | 0.031024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1404-7_0_3_line_17 | NAYY 4x150 SE | 14 | 16 | 0.036406 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1404-7_0_3_line_18 | NAYY 4x150 SE | 15 | 17 | 0.012267 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1404-7_0_3_line_19 | NAYY 4x150 SE | 16 | 18 | 0.029806 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1404-7_0_3_line_20 | NAYY 4x150 SE | 17 | 19 | 0.01004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1404-7_0_3_line_21 | NAYY 4x150 SE | 18 | 20 | 0.014474 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1404-7_0_3_line_22 | NAYY 4x150 SE | 19 | 33 | 0.012168 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1404-7_0_3_line_23 | NAYY 4x150 SE | 19 | 34 | 0.020296 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1404-7_0_3_line_24 | NAYY 4x150 SE | 21 | 22 | 0.0087643 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1404-7_0_3_line_25 | NAYY 4x150 SE | 21 | 23 | 0.038507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1404-7_0_3_line_26 | NAYY 4x150 SE | 22 | 24 | 0.050632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1404-7_0_3_line_27 | NAYY 4x150 SE | 23 | 25 | 0.068054 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1404-7_0_3_line_28 | NAYY 4x150 SE | 23 | 26 | 0.021154 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1404-7_0_3_line_29 | NAYY 4x150 SE | 25 | 27 | 0.073382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1404-7_0_3_line_30 | NAYY 4x150 SE | 26 | 28 | 0.04165 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1404-7_0_3_line_31 | NAYY 4x150 SE | 27 | 29 | 0.013894 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1404-7_0_3_line_32 | NAYY 4x150 SE | 28 | 30 | 0.016562 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1404-7_0_3_line_33 | NAYY 4x150 SE | 29 | 89 | 0.012597 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1404-7_0_3_line_34 | NAYY 4x150 SE | 30 | 49 | 0.17547 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1404-7_0_3_line_35 | NAYY 4x150 SE | 31 | 32 | 0.012938 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1404-7_0_3_line_36 | NAYY 4x150 SE | 32 | 67 | 0.0080173 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1404-7_0_3_line_37 | NAYY 4x150 SE | 33 | 36 | 0.015567 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1404-7_0_3_line_38 | NAYY 4x150 SE | 34 | 43 | 0.013265 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1404-7_0_3_line_39 | NAYY 4x150 SE | 35 | 36 | 0.018811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1404-7_0_3_line_40 | NAYY 4x150 SE | 36 | 37 | 0.03693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1404-7_0_3_line_41 | NAYY 4x150 SE | 37 | 38 | 0.026551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1404-7_0_3_line_42 | NAYY 4x150 SE | 38 | 39 | 0.022636 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1404-7_0_3_line_43 | NAYY 4x150 SE | 39 | 47 | 0.076426 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1404-7_0_3_line_44 | NAYY 4x150 SE | 40 | 41 | 0.029403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1404-7_0_3_line_45 | NAYY 4x150 SE | 40 | 42 | 0.011036 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
46 | LV_1404-7_0_3_line_46 | NAYY 4x150 SE | 41 | 77 | 0.045577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1404-7_0_3_line_47 | NAYY 4x150 SE | 42 | 83 | 0.038433 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
48 | LV_1404-7_0_3_line_48 | NAYY 4x150 SE | 43 | 44 | 0.00065417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1404-7_0_3_line_49 | NAYY 4x150 SE | 44 | 45 | 0.0046809 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1404-7_0_3_line_50 | NAYY 4x150 SE | 45 | 46 | 0.041485 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1404-7_0_3_line_51 | NAYY 4x150 SE | 47 | 48 | 0.0027289 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1404-7_0_3_line_52 | NAYY 4x150 SE | 48 | 73 | 0.016147 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1404-7_0_3_line_53 | NAYY 4x150 SE | 49 | 50 | 0.016948 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1404-7_0_3_line_54 | NAYY 4x150 SE | 50 | 51 | 0.0048682 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1404-7_0_3_line_55 | NAYY 4x150 SE | 51 | 52 | 0.018596 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1404-7_0_3_line_56 | NAYY 4x150 SE | 52 | 53 | 0.00066683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1404-7_0_3_line_57 | NAYY 4x150 SE | 53 | 54 | 0.062742 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1404-7_0_3_line_58 | NAYY 4x150 SE | 54 | 75 | 0.081608 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1404-7_0_3_line_59 | NAYY 4x150 SE | 55 | 56 | 0.0068083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1404-7_0_3_line_60 | NAYY 4x150 SE | 56 | 57 | 0.033333 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1404-7_0_3_line_61 | NAYY 4x150 SE | 56 | 58 | 0.012114 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1404-7_0_3_line_62 | NAYY 4x150 SE | 58 | 59 | 0.019757 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1404-7_0_3_line_63 | NAYY 4x150 SE | 58 | 60 | 0.0085006 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1404-7_0_3_line_64 | NAYY 4x150 SE | 59 | 61 | 0.00021804 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1404-7_0_3_line_65 | NAYY 4x150 SE | 60 | 62 | 0.0076863 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1404-7_0_3_line_66 | NAYY 4x150 SE | 61 | 82 | 0.026893 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1404-7_0_3_line_67 | NAYY 4x150 SE | 62 | 83 | 0.037049 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1404-7_0_3_line_68 | NAYY 4x150 SE | 63 | 64 | 0.013716 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1404-7_0_3_line_69 | NAYY 4x150 SE | 64 | 65 | 0.01609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1404-7_0_3_line_70 | NAYY 4x150 SE | 64 | 66 | 0.017979 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1404-7_0_3_line_71 | NAYY 4x150 SE | 65 | 70 | 0.022472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1404-7_0_3_line_72 | NAYY 4x150 SE | 66 | 71 | 0.040033 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1404-7_0_3_line_73 | NAYY 4x150 SE | 67 | 68 | 0.01005 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1404-7_0_3_line_74 | NAYY 4x150 SE | 67 | 69 | 0.0055858 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1404-7_0_3_line_75 | NAYY 4x150 SE | 69 | 72 | 0.020971 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1404-7_0_3_line_76 | NAYY 4x150 SE | 70 | 100 | 0.072232 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1404-7_0_3_line_77 | NAYY 4x150 SE | 70 | 109 | 0.011382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1404-7_0_3_line_78 | NAYY 4x150 SE | 71 | 110 | 0.059917 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1404-7_0_3_line_79 | NAYY 4x150 SE | 72 | 110 | 0.021349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1404-7_0_3_line_80 | NAYY 4x150 SE | 73 | 93 | 0.014019 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1404-7_0_3_line_81 | NAYY 4x150 SE | 74 | 75 | 0.013171 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1404-7_0_3_line_82 | NAYY 4x150 SE | 74 | 76 | 0.02452 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1404-7_0_3_line_83 | NAYY 4x150 SE | 75 | 77 | 0.12175 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1404-7_0_3_line_84 | NAYY 4x150 SE | 77 | 78 | 0.0082904 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1404-7_0_3_line_85 | NAYY 4x150 SE | 79 | 80 | 0.051066 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1404-7_0_3_line_86 | NAYY 4x150 SE | 80 | 81 | 0.026848 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1404-7_0_3_line_87 | NAYY 4x150 SE | 80 | 82 | 0.031219 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1404-7_0_3_line_88 | NAYY 4x150 SE | 83 | 84 | 0.016063 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1404-7_0_3_line_89 | NAYY 4x150 SE | 84 | 85 | 0.020104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1404-7_0_3_line_90 | NAYY 4x150 SE | 85 | 86 | 0.0059887 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1404-7_0_3_line_91 | NAYY 4x150 SE | 86 | 87 | 0.0054825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1404-7_0_3_line_92 | NAYY 4x150 SE | 87 | 88 | 0.026357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1404-7_0_3_line_93 | NAYY 4x150 SE | 88 | 111 | 0.029102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1404-7_0_3_line_94 | NAYY 4x150 SE | 90 | 91 | 0.013534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1404-7_0_3_line_95 | NAYY 4x150 SE | 91 | 92 | 0.0058482 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1404-7_0_3_line_96 | NAYY 4x150 SE | 92 | 93 | 0.016121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1404-7_0_3_line_97 | NAYY 4x150 SE | 93 | 94 | 0.083626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1404-7_0_3_line_98 | NAYY 4x150 SE | 94 | 95 | 0.011747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1404-7_0_3_line_99 | NAYY 4x150 SE | 95 | 96 | 0.0062504 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1404-7_0_3_line_100 | NAYY 4x150 SE | 96 | 97 | 0.051686 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1404-7_0_3_line_101 | NAYY 4x150 SE | 97 | 98 | 0.030761 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1404-7_0_3_line_102 | NAYY 4x150 SE | 99 | 100 | 0.11439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1404-7_0_3_line_103 | NAYY 4x150 SE | 100 | 101 | 0.0024439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1404-7_0_3_line_104 | NAYY 4x150 SE | 101 | 104 | 0.028496 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1404-7_0_3_line_105 | NAYY 4x150 SE | 102 | 103 | 0.006246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1404-7_0_3_line_106 | NAYY 4x150 SE | 102 | 104 | 0.029439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1404-7_0_3_line_107 | NAYY 4x150 SE | 103 | 105 | 0.082723 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1404-7_0_3_line_108 | NAYY 4x150 SE | 105 | 106 | 0.045045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1404-7_0_3_line_109 | NAYY 4x150 SE | 106 | 107 | 0.053785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1404-7_0_3_line_110 | NAYY 4x150 SE | 107 | 108 | 0.022492 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_1404-7_0_3_line_111 | NAYY 4x150 SE | 111 | 112 | 0.0060932 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_1404-7_0_3_line_112 | NAYY 4x150 SE | 112 | 113 | 0.021298 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_1404-7_0_3_line_113 | NAYY 4x150 SE | 113 | 114 | 0.0056622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_1404-7_0_3_line_114 | NAYY 4x150 SE | 114 | 115 | 0.026814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1404-7_0_3_trafo_28 | 0.25 MVA 20/0.4 kV | 116 | 7 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2665437.7645 | 1195910.2901 | 2665438.5289 | 1195909.6422
1 | 2665399.3364 | 1195942.8615 | 2665437.7645 | 1195910.2901
2 | 2665438.5289 | 1195909.6422 | 2665440.801 | 1195907.7164 | 2665451.0063 | 1195897.6221 | 2665451.8566 | 1195896.5426
3 | 2665399.3364 | 1195942.8615 | 2665388.8171 | 1195926.3725
4 | 2665399.3364 | 1195942.8615 | 2665455.091 | 1196018.4651
5 | 2665451.8566 | 1195896.5426 | 2665452.7206 | 1195895.4458
6 | 2665355.9255 | 1195878.439 | 2665364.1244 | 1195887.6664 | 2665388.8171 | 1195926.3725
7 | 2665465.4928 | 1196025.9369 | 2665463.3521 | 1196024.6543 | 2665455.091 | 1196018.4651
8 | 2665459.1047 | 1195886.2974 | 2665456.3373 | 1195890.8542 | 2665452.7206 | 1195895.4458
9 | 2665347.3826 | 1195868.8244 | 2665355.9255 | 1195878.439
10 | 2665465.4928 | 1196025.9369 | 2665485.8157 | 1196038.113
11 | 2665571.324 | 1195994.8457 | 2665485.8157 | 1196038.113
12 | 2665466.5526 | 1195862.5825 | 2665466.216 | 1195866.7592 | 2665464.7533 | 1195874.4033 | 2665461.8304 | 1195881.809 | 2665459.1047 | 1195886.2974
13 | 2665339.3557 | 1195859.7905 | 2665347.3826 | 1195868.8244
14 | 2665616.0819 | 1196082.3948 | 2665624.6738 | 1196087.9813 | 2665624.6738 | 1196087.9813
15 | 2665596.8557 | 1196055.6607 | 2665607.4272 | 1196075.3291 | 2665611.7687 | 1196079.5903 | 2665616.0819 | 1196082.3948
16 | 2665624.6738 | 1196087.9813 | 2665626.558 | 1196094.0055 | 2665624.4498 | 1196108.3908 | 2665622.0583 | 1196118.2786
17 | 2665596.8557 | 1196055.6607 | 2665591.6662 | 1196046.0056 | 2665581.0513 | 1196022.8809
18 | 2665619.1746 | 1196130.2014 | 2665622.0583 | 1196118.2786
19 | 2665571.324 | 1195994.8457 | 2665574.9914 | 1196009.6792 | 2665581.0513 | 1196022.8809
20 | 2665613.3936 | 1196138.4095 | 2665619.1746 | 1196130.2014 | 2665619.1746 | 1196130.2014
21 | 2665571.324 | 1195994.8457 | 2665570.0964 | 1195989.8805 | 2665567.3618 | 1195980.9294
22 | 2665613.3936 | 1196138.4095 | 2665604.3513 | 1196130.267
23 | 2665613.3936 | 1196138.4095 | 2665628.0615 | 1196152.4374
24 | 2665287.7418 | 1196319.9641 | 2665290.3343 | 1196317.6586 | 2665295.3209 | 1196315.8782
25 | 2665333.2946 | 1196310.579 | 2665325.2134 | 1196312.5141 | 2665298.9154 | 1196314.5949 | 2665295.3209 | 1196315.8782
26 | 2665251.7778 | 1196355.4269 | 2665263.1631 | 1196341.8208 | 2665287.7418 | 1196319.9641
27 | 2665333.2946 | 1196310.579 | 2665339.6544 | 1196378.3217
28 | 2665333.2946 | 1196310.579 | 2665330.8667 | 1196289.5646
29 | 2665339.6544 | 1196378.3217 | 2665345.9292 | 1196377.8567 | 2665368.0564 | 1196379.5661 | 2665383.3632 | 1196379.3888 | 2665398.2622 | 1196377.4839 | 2665409.0061 | 1196375.8782 | 2665412.2666 | 1196374.118
30 | 2665330.8667 | 1196289.5646 | 2665328.2416 | 1196266.8425 | 2665325.4166 | 1196248.2794
31 | 2665412.2666 | 1196374.118 | 2665412.9221 | 1196373.7642 | 2665414.6814 | 1196371.0262 | 2665415.854 | 1196366.9033 | 2665415.4538 | 1196363.786 | 2665414.0054 | 1196361.7912
32 | 2665320.5414 | 1196232.5048 | 2665324.8725 | 1196244.7037 | 2665325.4166 | 1196248.2794
33 | 2665403.8709 | 1196355.0431 | 2665404.7176 | 1196357.0313 | 2665414.0054 | 1196361.7912
34 | 2665320.5414 | 1196232.5048 | 2665178.1067 | 1196130.0242
35 | 2665466.5526 | 1195862.5825 | 2665466.8596 | 1195858.7727 | 2665466.3715 | 1195849.6694
36 | 2665465.9422 | 1195841.6637 | 2665466.3715 | 1195849.6694
37 | 2665592.7836 | 1196119.8503 | 2665604.3513 | 1196130.267
38 | 2665637.6478 | 1196161.6054 | 2665628.0615 | 1196152.4374
39 | 2665592.7836 | 1196119.8503 | 2665578.8041 | 1196107.263
40 | 2665592.7836 | 1196119.8503 | 2665586.1872 | 1196127.3825 | 2665562.3908 | 1196139.9633
41 | 2665556.5254 | 1196162.5525 | 2665556.286 | 1196160.6188 | 2665553.8055 | 1196149.9186 | 2665555.8388 | 1196145.8163 | 2665558.4782 | 1196142.0318 | 2665562.3908 | 1196139.9633
42 | 2665558.6973 | 1196184.5816 | 2665556.5306 | 1196179.9996 | 2665557.5528 | 1196170.8498 | 2665556.5254 | 1196162.5525
43 | 2665558.6973 | 1196184.5816 | 2665540.005 | 1196225.3008 | 2665532.0208 | 1196255.8981
44 | 2665339.3557 | 1195859.7905 | 2665320.726 | 1195882.5389
45 | 2665339.3557 | 1195859.7905 | 2665331.047 | 1195852.5268
46 | 2665320.726 | 1195882.5389 | 2665313.5109 | 1195891.3492 | 2665304.8475 | 1195908.8649 | 2665317.3057 | 1195916.5691
47 | 2665302.1125 | 1195827.2314 | 2665331.047 | 1195852.5268
48 | 2665638.1205 | 1196162.0576 | 2665637.6478 | 1196161.6054
49 | 2665638.1205 | 1196162.0576 | 2665641.5035 | 1196165.2929
50 | 2665670.9569 | 1196194.4904 | 2665660.8683 | 1196183.8127 | 2665641.5035 | 1196165.2929
51 | 2665530.7031 | 1196258.2878 | 2665532.0208 | 1196255.8981
52 | 2665522.1889 | 1196271.968 | 2665526.0124 | 1196266.7942 | 2665530.7031 | 1196258.2878
53 | 2665178.1067 | 1196130.0242 | 2665188.4735 | 1196116.6163
54 | 2665188.4735 | 1196116.6163 | 2665191.4513 | 1196112.765
55 | 2665191.4513 | 1196112.765 | 2665202.8259 | 1196098.0536
56 | 2665202.8259 | 1196098.0536 | 2665203.2338 | 1196097.526
57 | 2665241.6113 | 1196047.8902 | 2665203.2338 | 1196097.526
58 | 2665209.3723 | 1195972.8946 | 2665241.6113 | 1196047.8902
59 | 2665256.869 | 1195796.7865 | 2665255.9239 | 1195798.9108 | 2665256.0061 | 1195801.1574 | 2665257.1048 | 1195803.1039
60 | 2665256.869 | 1195796.7865 | 2665254.4082 | 1195797.4712 | 2665251.6561 | 1195796.9297 | 2665249.4277 | 1195795.1711 | 2665239.7157 | 1195785.9041 | 2665237.7919 | 1195784.8603 | 2665235.5446 | 1195784.8358 | 2665233.4876 | 1195785.5249 | 2665231.6517 | 1195785.5049 | 2665229.7169 | 1195784.7722 | 2665228.5214 | 1195784.6616
61 | 2665265.7815 | 1195788.5566 | 2665256.869 | 1195796.7865
62 | 2665265.7815 | 1195788.5566 | 2665254.237 | 1195772.5237
63 | 2665265.7815 | 1195788.5566 | 2665270.745 | 1195795.4576
64 | 2665254.237 | 1195772.5237 | 2665254.1096 | 1195772.3468
65 | 2665275.5525 | 1195801.4286 | 2665273.6317 | 1195799.4709 | 2665270.745 | 1195795.4576
66 | 2665238.0598 | 1195750.7879 | 2665241.1721 | 1195754.3792 | 2665254.1096 | 1195772.3468
67 | 2665302.1125 | 1195827.2314 | 2665292.1678 | 1195818.3621 | 2665275.5525 | 1195801.4286
68 | 2665526.9628 | 1195822.7539 | 2665529.8011 | 1195836.1732
69 | 2665526.9628 | 1195822.7539 | 2665535.5383 | 1195819.5792 | 2665537.4203 | 1195812.8928
70 | 2665526.9628 | 1195822.7539 | 2665526.2106 | 1195817.6982 | 2665522.569 | 1195805.3566
71 | 2665543.4185 | 1195791.2363 | 2665541.9676 | 1195796.7362 | 2665537.4203 | 1195812.8928
72 | 2665511.2393 | 1195766.9599 | 2665522.569 | 1195805.3566
73 | 2665465.9422 | 1195841.6637 | 2665459.4819 | 1195842.3156 | 2665455.9681 | 1195841.7657
74 | 2665465.9422 | 1195841.6637 | 2665464.9472 | 1195836.1672
75 | 2665460.5466 | 1195815.6696 | 2665463.5283 | 1195828.3294 | 2665464.9472 | 1195836.1672
76 | 2665610.2595 | 1195818.6182 | 2665543.4185 | 1195791.2363
77 | 2665546.3216 | 1195780.2309 | 2665543.4185 | 1195791.2363
78 | 2665458.0171 | 1195794.4825 | 2665511.2393 | 1195766.9599
79 | 2665458.0171 | 1195794.4825 | 2665460.1574 | 1195814.0174 | 2665460.5466 | 1195815.6696
80 | 2665511.9059 | 1196281.1704 | 2665518.612 | 1196276.808 | 2665522.1889 | 1196271.968
81 | 2665209.3723 | 1195972.8946 | 2665199.567 | 1195981.6883
82 | 2665181.3128 | 1195998.0592 | 2665199.567 | 1195981.6883
83 | 2665317.3057 | 1195916.5691 | 2665209.3723 | 1195972.8946
84 | 2665324.3568 | 1195920.9294 | 2665317.3057 | 1195916.5691
85 | 2665217.6137 | 1195727.1953 | 2665213.3282 | 1195729.6278 | 2665198.7031 | 1195749.5912 | 2665184.6323 | 1195765.7028
86 | 2665217.6137 | 1195727.1953 | 2665223.0765 | 1195723.0079 | 2665235.3205 | 1195712.5019 | 2665237.777 | 1195709.5616
87 | 2665217.6137 | 1195727.1953 | 2665238.0598 | 1195750.7879
88 | 2665302.1125 | 1195827.2314 | 2665315.7661 | 1195818.7706
89 | 2665315.7661 | 1195818.7706 | 2665318.4206 | 1195817.1257 | 2665327.2992 | 1195810.6077 | 2665331.9464 | 1195806.8648
90 | 2665336.6105 | 1195803.1083 | 2665331.9464 | 1195806.8648
91 | 2665340.8804 | 1195799.6694 | 2665336.6105 | 1195803.1083
92 | 2665340.8804 | 1195799.6694 | 2665356.7846 | 1195786.8602 | 2665357.2197 | 1195784.697 | 2665357.0547 | 1195780.9708 | 2665357.0547 | 1195780.9708
93 | 2665357.0547 | 1195780.9708 | 2665348.0461 | 1195761.0384 | 2665345.7748 | 1195754.176
94 | 2665512.7117 | 1196314.699 | 2665509.2614 | 1196301.6125
95 | 2665509.2614 | 1196301.6125 | 2665507.7705 | 1196295.9576
96 | 2665511.9059 | 1196281.1704 | 2665508.0946 | 1196286.2317 | 2665507.482 | 1196294.8634 | 2665507.7705 | 1196295.9576
97 | 2665511.9059 | 1196281.1704 | 2665507.1436 | 1196280.5513 | 2665503.5363 | 1196278.1214 | 2665498.3831 | 1196272.8619 | 2665489.5887 | 1196259.9135 | 2665478.1129 | 1196243.456 | 2665466.6051 | 1196229.2328 | 2665457.6153 | 1196219.7047
98 | 2665448.9103 | 1196211.8511 | 2665454.5857 | 1196216.4937 | 2665457.6153 | 1196219.7047
99 | 2665448.9103 | 1196211.8511 | 2665444.0724 | 1196207.8936
100 | 2665400.0206 | 1196181.2095 | 2665418.6436 | 1196190.6187 | 2665434.6668 | 1196200.1996 | 2665444.0724 | 1196207.8936
101 | 2665425.9155 | 1196164.4939 | 2665400.0206 | 1196181.2095
102 | 2665610.2595 | 1195818.6182 | 2665703.4195 | 1195752.2375
103 | 2665610.2595 | 1195818.6182 | 2665611.4522 | 1195820.7513
104 | 2665625.0367 | 1195845.7895 | 2665622.8574 | 1195841.1491 | 2665611.4522 | 1195820.7513
105 | 2665645.181 | 1195866.0865 | 2665647.6024 | 1195871.844
106 | 2665645.181 | 1195866.0865 | 2665642.8001 | 1195863.6589 | 2665635.2164 | 1195859.7734 | 2665631.6765 | 1195856.7328 | 2665627.287 | 1195850.581 | 2665625.0367 | 1195845.7895
107 | 2665698.0265 | 1195936.474 | 2665685.3857 | 1195915.9905 | 2665656.683 | 1195887.8144 | 2665649.8736 | 1195877.2445 | 2665647.6024 | 1195871.844
108 | 2665715.7074 | 1195976.1149 | 2665716.7998 | 1195972.6356 | 2665716.4501 | 1195966.328 | 2665698.0265 | 1195936.474
109 | 2665743.2451 | 1195972.7299 | 2665724.3059 | 1195991.1956 | 2665718.3268 | 1195993.8315 | 2665713.7554 | 1195991.0797 | 2665712.876 | 1195985.1332 | 2665715.7074 | 1195976.1149
110 | 2665760.2391 | 1195972.8463 | 2665750.7133 | 1195965.4484 | 2665743.2451 | 1195972.7299
111 | 2665343.8602 | 1195748.3914 | 2665345.7748 | 1195754.176
112 | 2665343.8602 | 1195748.3914 | 2665342.9349 | 1195745.5957 | 2665339.2207 | 1195727.622
113 | 2665338.0749 | 1195722.0769 | 2665339.2207 | 1195727.622
114 | 2665338.0749 | 1195722.0769 | 2665338.0142 | 1195721.7835 | 2665335.6363 | 1195702.335 | 2665335.4838 | 1195695.4152

## bus_geodata
| x | y | coords
0 | 2665437.7645 | 1195910.2901
1 | 2665438.5289 | 1195909.6422
2 | 2665399.3364 | 1195942.8615
3 | 2665451.8566 | 1195896.5426
4 | 2665388.8171 | 1195926.3725
5 | 2665455.091 | 1196018.4651
6 | 2665452.7206 | 1195895.4458
7 | 2665355.9255 | 1195878.439
8 | 2665465.4928 | 1196025.9369
9 | 2665485.8157 | 1196038.113
10 | 2665459.1047 | 1195886.2974
11 | 2665347.3826 | 1195868.8244
12 | 2665616.0819 | 1196082.3948
13 | 2665624.6738 | 1196087.9813
14 | 2665596.8557 | 1196055.6607
15 | 2665622.0583 | 1196118.2786
16 | 2665581.0513 | 1196022.8809
17 | 2665619.1746 | 1196130.2014
18 | 2665571.324 | 1195994.8456
19 | 2665613.3936 | 1196138.4095
20 | 2665567.3618 | 1195980.9294
21 | 2665295.3209 | 1196315.8782
22 | 2665287.7418 | 1196319.9641
23 | 2665333.2946 | 1196310.579
24 | 2665251.7778 | 1196355.4269
25 | 2665339.6544 | 1196378.3217
26 | 2665330.8667 | 1196289.5646
27 | 2665412.2666 | 1196374.118
28 | 2665325.4166 | 1196248.2794
29 | 2665414.0054 | 1196361.7912
30 | 2665320.5414 | 1196232.5048
31 | 2665466.5526 | 1195862.5825
32 | 2665466.3715 | 1195849.6694
33 | 2665604.3513 | 1196130.267
34 | 2665628.0615 | 1196152.4374
35 | 2665578.8041 | 1196107.263
36 | 2665592.7836 | 1196119.8503
37 | 2665562.3908 | 1196139.9633
38 | 2665556.5254 | 1196162.5525
39 | 2665558.6973 | 1196184.5816
40 | 2665339.3557 | 1195859.7905
41 | 2665320.726 | 1195882.5389
42 | 2665331.047 | 1195852.5268
43 | 2665637.6478 | 1196161.6054
44 | 2665638.1205 | 1196162.0576
45 | 2665641.5035 | 1196165.2929
46 | 2665670.9569 | 1196194.4904
47 | 2665532.0208 | 1196255.8981
48 | 2665530.7031 | 1196258.2878
49 | 2665178.1067 | 1196130.0242
50 | 2665188.4735 | 1196116.6163
51 | 2665191.4513 | 1196112.765
52 | 2665202.8259 | 1196098.0536
53 | 2665203.2338 | 1196097.526
54 | 2665241.6113 | 1196047.8902
55 | 2665257.1048 | 1195803.1039
56 | 2665256.869 | 1195796.7865
57 | 2665228.5214 | 1195784.6616
58 | 2665265.7815 | 1195788.5566
59 | 2665254.237 | 1195772.5237
60 | 2665270.745 | 1195795.4576
61 | 2665254.1096 | 1195772.3468
62 | 2665275.5525 | 1195801.4286
63 | 2665529.8011 | 1195836.1732
64 | 2665526.9628 | 1195822.7539
65 | 2665537.4203 | 1195812.8928
66 | 2665522.569 | 1195805.3566
67 | 2665465.9422 | 1195841.6637
68 | 2665455.9681 | 1195841.7657
69 | 2665464.9472 | 1195836.1672
70 | 2665543.4185 | 1195791.2363
71 | 2665511.2393 | 1195766.9599
72 | 2665460.5466 | 1195815.6696
73 | 2665522.1889 | 1196271.968
74 | 2665199.567 | 1195981.6883
75 | 2665209.3723 | 1195972.8946
76 | 2665181.3128 | 1195998.0592
77 | 2665317.3057 | 1195916.5691
78 | 2665324.3568 | 1195920.9294
79 | 2665184.6323 | 1195765.7028
80 | 2665217.6137 | 1195727.1953
81 | 2665237.777 | 1195709.5616
82 | 2665238.0598 | 1195750.7879
83 | 2665302.1125 | 1195827.2314
84 | 2665315.7661 | 1195818.7706
85 | 2665331.9464 | 1195806.8648
86 | 2665336.6105 | 1195803.1083
87 | 2665340.8804 | 1195799.6694
88 | 2665357.0547 | 1195780.9708
89 | 2665403.8709 | 1196355.0431
90 | 2665512.7117 | 1196314.699
91 | 2665509.2614 | 1196301.6125
92 | 2665507.7705 | 1196295.9576
93 | 2665511.9059 | 1196281.1704
94 | 2665457.6153 | 1196219.7047
95 | 2665448.9103 | 1196211.8511
96 | 2665444.0724 | 1196207.8936
97 | 2665400.0206 | 1196181.2095
98 | 2665425.9155 | 1196164.4939
99 | 2665703.4195 | 1195752.2375
100 | 2665610.2595 | 1195818.6182
101 | 2665611.4522 | 1195820.7513
102 | 2665645.181 | 1195866.0865
103 | 2665647.6024 | 1195871.844
104 | 2665625.0367 | 1195845.7895
105 | 2665698.0265 | 1195936.474
106 | 2665715.7074 | 1195976.1149
107 | 2665743.2451 | 1195972.7299
108 | 2665760.2391 | 1195972.8463
109 | 2665546.3216 | 1195780.2309
110 | 2665458.0171 | 1195794.4825
111 | 2665345.7748 | 1195754.176
112 | 2665343.8602 | 1195748.3914
113 | 2665339.2207 | 1195727.622
114 | 2665338.0749 | 1195722.0769
115 | 2665335.4838 | 1195695.4152
116 | 2665339.3557 | 1195859.7905

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98938 | -0.073827 | 0.0009514 | 0.00023844
1 | 0.98933 | -0.074188 | 0.00073676 | 0.00018465
2 | 0.99203 | -0.055235 | 0 | 0
3 | 0.98839 | -0.080795 | 0.0026415 | 0.00066203
4 | 0.994 | -0.041482 | 0.0014419 | 0.00036139
5 | 0.9875 | -0.086979 | 0.0008502 | 0.00021308
6 | 0.98833 | -0.081251 | 0.00086644 | 0.00021715
7 | 1 | 0 | -0.2194 | -0.055157
8 | 0.98689 | -0.091221 | 0.0012218 | 0.00030621
9 | 0.98582 | -0.098777 | 0.0026916 | 0.00067457
10 | 0.98782 | -0.084804 | 0.0008578 | 0.00021499
11 | 0.99866 | -0.0093128 | 0.0017065 | 0.00042769
12 | 0.97831 | -0.1521 | 0.001298 | 0.00032532
13 | 0.97798 | -0.15445 | 0.00034686 | 8.6932e-05
14 | 0.97945 | -0.14393 | 0.00094643 | 0.0002372
15 | 0.977 | -0.16148 | 0.0011086 | 0.00027785
16 | 0.98074 | -0.13474 | 0.0013083 | 0.00032789
17 | 0.97663 | -0.16413 | 0.00054383 | 0.0001363
18 | 0.98185 | -0.12683 | 0.00035698 | 8.9467e-05
19 | 0.97633 | -0.16623 | 0 | 0
20 | 0.9818 | -0.1272 | 0.0024197 | 0.00060644
21 | 0.98983 | -0.071656 | 0.00036847 | 9.2347e-05
22 | 0.98981 | -0.071758 | 0.00020852 | 5.2261e-05
23 | 0.98991 | -0.071064 | 0 | 0
24 | 0.98975 | -0.072237 | 0.00092553 | 0.00023196
25 | 0.98973 | -0.072345 | 0 | 0
26 | 0.99001 | -0.070339 | 0.000359 | 8.9975e-05
27 | 0.98954 | -0.073722 | 0.00032565 | 8.1616e-05
28 | 0.99024 | -0.068759 | 0.00040878 | 0.00010245
29 | 0.98951 | -0.073936 | 0.00050308 | 0.00012608
30 | 0.99033 | -0.068062 | 0 | 0
31 | 0.98672 | -0.092601 | 0.0012124 | 0.00030386
32 | 0.98617 | -0.096452 | 0.001471 | 0.00036867
33 | 0.97608 | -0.16804 | 0.00065219 | 0.00016345
34 | 0.97616 | -0.16747 | 0.0013204 | 0.00033092
35 | 0.97575 | -0.17039 | 0.00070164 | 0.00017585
36 | 0.97577 | -0.17025 | 0 | 0
37 | 0.97508 | -0.17522 | 0.0008831 | 0.00022133
38 | 0.97462 | -0.17855 | 0.002084 | 0.0005223
39 | 0.97429 | -0.1809 | 0 | 0
40 | 0.99741 | -0.017982 | 0 | 0
41 | 0.99674 | -0.022705 | 0.0015662 | 0.00039254
42 | 0.9964 | -0.025031 | 0.0034167 | 0.00085631
43 | 0.97607 | -0.1681 | 0.00083136 | 0.00020836
44 | 0.97607 | -0.16813 | 0.00084554 | 0.00021191
45 | 0.97605 | -0.16827 | 0.0010212 | 0.00025595
46 | 0.97594 | -0.16906 | 0.0018237 | 0.00045705
47 | 0.97319 | -0.18883 | 0.00065341 | 0.00016376
48 | 0.97315 | -0.18909 | 0.00019082 | 4.7823e-05
49 | 0.99137 | -0.060665 | 0.002786 | 0.00069823
50 | 0.99154 | -0.05947 | 0.00088818 | 0.0002226
51 | 0.99159 | -0.059083 | 0.0006116 | 0.00015328
52 | 0.99182 | -0.05749 | 0.00062118 | 0.00015568
53 | 0.99183 | -0.057428 | 0.0006649 | 0.00016664
54 | 0.9927 | -0.051237 | 0 | 0
55 | 0.9875 | -0.087596 | 0.025317 | 0.006345
56 | 0.98775 | -0.085833 | 0 | 0
57 | 0.98753 | -0.087363 | 0.0044861 | 0.0011243
58 | 0.98827 | -0.082141 | 0 | 0
59 | 0.98762 | -0.086716 | 0.0074351 | 0.0018634
60 | 0.98891 | -0.077587 | 0.0077239 | 0.0019358
61 | 0.98762 | -0.08675 | 0.0029005 | 0.00072694
62 | 0.98958 | -0.07287 | 0.003192 | 0.0008
63 | 0.98017 | -0.13907 | 0.0014617 | 0.00036634
64 | 0.9802 | -0.13887 | 0 | 0
65 | 0.97974 | -0.14218 | 0.0023393 | 0.0005863
66 | 0.98076 | -0.13489 | 0.0021326 | 0.00053447
67 | 0.98585 | -0.098719 | 0 | 0
68 | 0.98583 | -0.09886 | 0.0013582 | 0.0003404
69 | 0.98564 | -0.10022 | 0.001453 | 0.00036416
70 | 0.97917 | -0.14626 | 0.001675 | 0.00041979
71 | 0.98212 | -0.12519 | 0 | 0
72 | 0.98488 | -0.10556 | 0.0013186 | 0.00033048
73 | 0.97294 | -0.19062 | 0.00036248 | 9.0845e-05
74 | 0.99381 | -0.043402 | 0.00088251 | 0.00022118
75 | 0.99384 | -0.043195 | 0 | 0
76 | 0.99378 | -0.043567 | 0.00066587 | 0.00016688
77 | 0.9958 | -0.029318 | 0.0019496 | 0.00048862
78 | 0.99579 | -0.029415 | 0.0011681 | 0.00029275
79 | 0.98664 | -0.093656 | 0.0025419 | 0.00063707
80 | 0.98683 | -0.092324 | 0 | 0
81 | 0.98667 | -0.093503 | 0.0042832 | 0.0010735
82 | 0.98714 | -0.090138 | 0.0054705 | 0.001371
83 | 0.99297 | -0.049023 | 0 | 0
84 | 0.99156 | -0.058855 | 0.0023041 | 0.00057745
85 | 0.98988 | -0.070729 | 0.0024726 | 0.0006197
86 | 0.9894 | -0.074123 | 0.0069794 | 0.0017492
87 | 0.98901 | -0.076843 | 0.0054216 | 0.0013588
88 | 0.98737 | -0.088482 | 0.010527 | 0.0026384
89 | 0.98949 | -0.074065 | 0.0010065 | 0.00025224
90 | 0.97272 | -0.19219 | 0.00039297 | 9.8486e-05
91 | 0.97273 | -0.19213 | 0.00044617 | 0.00011182
92 | 0.97274 | -0.19208 | 0.00019438 | 4.8715e-05
93 | 0.97276 | -0.1919 | 0 | 0
94 | 0.97183 | -0.19861 | 0.0029582 | 0.00074138
95 | 0.97175 | -0.19919 | 0.00059145 | 0.00014823
96 | 0.97171 | -0.19946 | 0.0014139 | 0.00035435
97 | 0.97152 | -0.2009 | 0 | 0
98 | 0.9714 | -0.20175 | 0.0026261 | 0.00065817
99 | 0.97765 | -0.15717 | 0.0010138 | 0.00025407
100 | 0.97782 | -0.15595 | 0.0017796 | 0.000446
101 | 0.97778 | -0.15621 | 0.0012797 | 0.00032072
102 | 0.9771 | -0.16111 | 0 | 0
103 | 0.97703 | -0.16159 | 0.0040677 | 0.0010195
104 | 0.97742 | -0.15882 | 0.0013537 | 0.00033926
105 | 0.97663 | -0.16449 | 0.00094905 | 0.00023785
106 | 0.97647 | -0.16562 | 0.0005611 | 0.00014063
107 | 0.97633 | -0.16666 | 0.0012425 | 0.0003114
108 | 0.97631 | -0.16679 | 0.00058534 | 0.0001467
109 | 0.97912 | -0.14661 | 0.0029127 | 0.00072999
110 | 0.98416 | -0.1107 | 0 | 0
111 | 0.98599 | -0.098232 | 0.0098088 | 0.0024583
112 | 0.98579 | -0.099663 | 0.0070076 | 0.0017563
113 | 0.9853 | -0.10313 | 0.0027361 | 0.00068573
114 | 0.98519 | -0.1039 | 0.007161 | 0.0017947
115 | 0.98496 | -0.10554 | 0.0059583 | 0.0014933
116 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.035554 | 0.0089391 | -0.035552 | -0.0089384 | 1.7886e-06 | 6.7504e-07 | 0.053483 | 0.053483 | 0.053483 | 0.98938 | -0.073827 | 0.98933 | -0.074188 | 19.8085
1 | -0.036505 | -0.0091775 | 0.0366 | 0.0092133 | 9.4789e-05 | 3.5809e-05 | 0.054914 | 0.054914 | 0.054914 | 0.98938 | -0.073827 | 0.99203 | -0.055235 | 20.3385
2 | 0.034816 | 0.0087537 | -0.034783 | -0.0087417 | 3.2021e-05 | 1.2076e-05 | 0.052375 | 0.052375 | 0.052375 | 0.98933 | -0.074188 | 0.98839 | -0.080795 | 19.3981
3 | -0.070176 | -0.017682 | 0.070311 | 0.017734 | 0.00013531 | 5.1791e-05 | 0.1053 | 0.1053 | 0.1053 | 0.99203 | -0.055235 | 0.994 | -0.041482 | 38.9982
4 | 0.033576 | 0.0084687 | -0.033427 | -0.0084127 | 0.00014879 | 5.602e-05 | 0.050382 | 0.050382 | 0.050382 | 0.99203 | -0.055235 | 0.9875 | -0.086979 | 18.66
5 | 0.032142 | 0.0080796 | -0.03214 | -0.0080789 | 2.0407e-06 | 7.6699e-07 | 0.048398 | 0.048398 | 0.048398 | 0.98839 | -0.080795 | 0.98833 | -0.081251 | 17.9252
6 | -0.071753 | -0.018095 | 0.072173 | 0.018256 | 0.00041972 | 0.00016067 | 0.10745 | 0.10745 | 0.10745 | 0.994 | -0.041482 | 1 | 0 | 39.7977
7 | 0.032577 | 0.0081996 | -0.032557 | -0.0081923 | 1.9283e-05 | 7.2527e-06 | 0.049101 | 0.049101 | 0.049101 | 0.9875 | -0.086979 | 0.98689 | -0.091221 | 18.1855
8 | 0.031273 | 0.0078617 | -0.031258 | -0.0078559 | 1.5467e-05 | 5.8057e-06 | 0.047094 | 0.047094 | 0.047094 | 0.98833 | -0.081251 | 0.98782 | -0.084804 | 17.4421
9 | 0.14642 | 0.036901 | -0.14623 | -0.036828 | 0.00019063 | 7.2981e-05 | 0.21795 | 0.21795 | 0.21795 | 1 | 0 | 0.99866 | -0.0093128 | 40.3619
10 | 0.031336 | 0.0078861 | -0.031303 | -0.0078737 | 3.3017e-05 | 1.2396e-05 | 0.047259 | 0.047259 | 0.047259 | 0.98689 | -0.091221 | 0.98582 | -0.098777 | 17.5033
11 | 0.028611 | 0.0071991 | -0.028499 | -0.0071574 | 0.00011158 | 4.1699e-05 | 0.043196 | 0.043197 | 0.043197 | 0.98582 | -0.098777 | 0.98185 | -0.12683 | 15.9987
12 | 0.0304 | 0.0076409 | -0.030367 | -0.0076286 | 3.2969e-05 | 1.2358e-05 | 0.045802 | 0.045802 | 0.045802 | 0.98782 | -0.084804 | 0.98672 | -0.092601 | 16.9636
13 | 0.14453 | 0.0364 | -0.14435 | -0.036333 | 0.00017496 | 6.6975e-05 | 0.21541 | 0.21541 | 0.21541 | 0.99866 | -0.0093128 | 0.99741 | -0.017982 | 39.8911
14 | 0.022084 | 0.0055395 | -0.022077 | -0.0055369 | 7.2161e-06 | 2.6468e-06 | 0.033592 | 0.033592 | 0.033592 | 0.97831 | -0.1521 | 0.97798 | -0.15445 | 12.4413
15 | -0.023382 | -0.0058648 | 0.023408 | 0.0058746 | 2.6487e-05 | 9.7656e-06 | 0.035566 | 0.035566 | 0.035566 | 0.97831 | -0.1521 | 0.97945 | -0.14393 | 13.1726
16 | 0.02173 | 0.0054499 | -0.021709 | -0.0054422 | 2.1164e-05 | 7.751e-06 | 0.033064 | 0.033064 | 0.033064 | 0.97798 | -0.15445 | 0.977 | -0.16148 | 12.2459
17 | -0.024355 | -0.0061118 | 0.024386 | 0.0061233 | 3.1106e-05 | 1.1505e-05 | 0.037004 | 0.037003 | 0.037004 | 0.97945 | -0.14393 | 0.98074 | -0.13474 | 13.705
18 | 0.0206 | 0.0051643 | -0.020593 | -0.0051616 | 7.5351e-06 | 2.7446e-06 | 0.031375 | 0.031376 | 0.031376 | 0.977 | -0.16148 | 0.97663 | -0.16413 | 11.6206
19 | -0.025694 | -0.0064512 | 0.025723 | 0.0064617 | 2.8272e-05 | 1.0497e-05 | 0.038988 | 0.038988 | 0.038988 | 0.98074 | -0.13474 | 0.98185 | -0.12683 | 14.4402
20 | 0.020049 | 0.0050253 | -0.020043 | -0.0050232 | 5.8457e-06 | 2.1228e-06 | 0.030547 | 0.030547 | 0.030547 | 0.97663 | -0.16413 | 0.97633 | -0.16623 | 11.3137
21 | 0.0024199 | 0.00060631 | -0.0024197 | -0.00060644 | 1.2147e-07 | -1.3633e-07 | 0.0036673 | 0.0036673 | 0.0036673 | 0.98185 | -0.12683 | 0.9818 | -0.1272 | 1.3583
22 | 0.014199 | 0.0035593 | -0.014195 | -0.0035581 | 3.5559e-06 | 1.2155e-06 | 0.021641 | 0.021641 | 0.021641 | 0.97633 | -0.16623 | 0.97608 | -0.16804 | 8.0151
23 | 0.0058439 | 0.0014638 | -0.0058429 | -0.0014637 | 1.0046e-06 | 1.3262e-07 | 0.0089063 | 0.0089064 | 0.0089064 | 0.97633 | -0.16623 | 0.97616 | -0.16747 | 3.2987
24 | 0.0011341 | 0.00028349 | -0.0011341 | -0.00028359 | 1.5893e-08 | -1.0654e-07 | 0.0017047 | 0.0017047 | 0.0017047 | 0.98983 | -0.071656 | 0.98981 | -0.071758 | 0.63138
25 | -0.0015026 | -0.00037583 | 0.0015027 | 0.00037539 | 1.2256e-07 | -4.4786e-07 | 0.0022586 | 0.0022584 | 0.0022586 | 0.98983 | -0.071656 | 0.98991 | -0.071064 | 0.83652
26 | 0.00092559 | 0.00023133 | -0.00092553 | -0.00023196 | 6.1163e-08 | -6.2723e-07 | 0.0013912 | 0.0013915 | 0.0013915 | 0.98981 | -0.071758 | 0.98975 | -0.072237 | 0.51536
27 | 0.0018359 | 0.00045807 | -0.0018356 | -0.00045882 | 3.2329e-07 | -7.504e-07 | 0.002759 | 0.0027593 | 0.0027593 | 0.98991 | -0.071064 | 0.98973 | -0.072345 | 1.022
28 | -0.0033387 | -0.00083345 | 0.003339 | 0.00083331 | 3.323e-07 | -1.4418e-07 | 0.0050174 | 0.0050173 | 0.0050174 | 0.98991 | -0.071064 | 0.99001 | -0.070339 | 1.8583
29 | 0.0018356 | 0.00045882 | -0.0018353 | -0.00045963 | 3.4868e-07 | -8.0876e-07 | 0.0027593 | 0.0027596 | 0.0027596 | 0.98973 | -0.072345 | 0.98954 | -0.073722 | 1.0221
30 | -0.003698 | -0.00092328 | 0.0036988 | 0.00092306 | 8.0252e-07 | -2.2702e-07 | 0.0055569 | 0.0055567 | 0.0055569 | 0.99001 | -0.070339 | 0.99024 | -0.068759 | 2.0581
31 | 0.0015096 | 0.00037801 | -0.0015096 | -0.00037817 | 4.4674e-08 | -1.613e-07 | 0.0022699 | 0.00227 | 0.00227 | 0.98954 | -0.073722 | 0.98951 | -0.073936 | 0.84075
32 | -0.0041076 | -0.0010255 | 0.004108 | 0.0010254 | 3.9355e-07 | -6.1713e-08 | 0.006171 | 0.0061709 | 0.006171 | 0.99024 | -0.068759 | 0.99033 | -0.068062 | 2.2856
33 | 0.0010065 | 0.00025209 | -0.0010065 | -0.00025224 | 1.8007e-08 | -1.5489e-07 | 0.0015135 | 0.0015135 | 0.0015135 | 0.98951 | -0.073936 | 0.98949 | -0.074065 | 0.56057
34 | -0.004108 | -0.0010254 | 0.0041121 | 0.0010248 | 4.169e-06 | -6.5666e-07 | 0.0061709 | 0.0061701 | 0.0061709 | 0.99033 | -0.068062 | 0.99137 | -0.060665 | 2.2855
35 | 0.029155 | 0.0073247 | -0.029139 | -0.0073189 | 1.5612e-05 | 5.8393e-06 | 0.043973 | 0.043973 | 0.043973 | 0.98672 | -0.092601 | 0.98617 | -0.096452 | 16.2864
36 | 0.027668 | 0.0069502 | -0.027659 | -0.0069469 | 8.7217e-06 | 3.2523e-06 | 0.041754 | 0.041754 | 0.041754 | 0.98617 | -0.096452 | 0.98585 | -0.098719 | 15.4644
37 | 0.013543 | 0.0033947 | -0.013539 | -0.0033933 | 4.1407e-06 | 1.3981e-06 | 0.020646 | 0.020647 | 0.020647 | 0.97608 | -0.16804 | 0.97577 | -0.17025 | 7.6469
38 | 0.0045225 | 0.0011328 | -0.0045221 | -0.0011328 | 3.9335e-07 | -1.452e-08 | 0.0068936 | 0.0068937 | 0.0068937 | 0.97616 | -0.16747 | 0.97607 | -0.1681 | 2.5532
39 | -0.00070164 | -0.00017585 | 0.00070165 | 0.00017562 | 1.3438e-08 | -2.298e-07 | 0.00107 | 0.0010699 | 0.00107 | 0.97575 | -0.17039 | 0.97577 | -0.17025 | 0.39629
40 | 0.012837 | 0.0032176 | -0.012829 | -0.0032147 | 8.8316e-06 | 2.9358e-06 | 0.019577 | 0.019577 | 0.019577 | 0.97577 | -0.17025 | 0.97508 | -0.17522 | 7.2507
41 | 0.011945 | 0.0029934 | -0.01194 | -0.0029916 | 5.5055e-06 | 1.7865e-06 | 0.018229 | 0.018229 | 0.018229 | 0.97508 | -0.17522 | 0.97462 | -0.17855 | 6.7516
42 | 0.009856 | 0.0024693 | -0.0098528 | -0.0024683 | 3.1983e-06 | 9.4811e-07 | 0.015048 | 0.015048 | 0.015048 | 0.97462 | -0.17855 | 0.97429 | -0.1809 | 5.5732
43 | 0.0098528 | 0.0024683 | -0.009842 | -0.0024651 | 1.0799e-05 | 3.2027e-06 | 0.015048 | 0.015048 | 0.015048 | 0.97429 | -0.1809 | 0.97319 | -0.18883 | 5.5733
44 | 0.015984 | 0.0040037 | -0.015974 | -0.0040001 | 1.0433e-05 | 3.6291e-06 | 0.023845 | 0.023846 | 0.023846 | 0.99741 | -0.017982 | 0.99674 | -0.022705 | 8.8317
45 | 0.12837 | 0.03233 | -0.12824 | -0.032281 | 0.00012636 | 4.8312e-05 | 0.19157 | 0.19157 | 0.19157 | 0.99741 | -0.017982 | 0.9964 | -0.025031 | 35.4752
46 | 0.014407 | 0.0036075 | -0.014394 | -0.0036031 | 1.3155e-05 | 4.4663e-06 | 0.021507 | 0.021508 | 0.021508 | 0.99674 | -0.022705 | 0.9958 | -0.029318 | 7.9658
47 | 0.12483 | 0.031425 | -0.12441 | -0.031266 | 0.00041691 | 0.00015935 | 0.18646 | 0.18646 | 0.18646 | 0.9964 | -0.025031 | 0.99297 | -0.049023 | 34.5304
48 | 0.0036907 | 0.00092443 | -0.0036907 | -0.00092444 | 1.2922e-08 | -3.2066e-09 | 0.0056263 | 0.0056263 | 0.0056263 | 0.97607 | -0.1681 | 0.97607 | -0.16813 | 2.0838
49 | 0.0028452 | 0.00071252 | -0.0028451 | -0.00071256 | 5.4948e-08 | -3.7372e-08 | 0.0043373 | 0.0043373 | 0.0043373 | 0.97607 | -0.16813 | 0.97605 | -0.16827 | 1.6064
50 | 0.0018239 | 0.00045661 | -0.0018237 | -0.00045705 | 2.0013e-07 | -4.4147e-07 | 0.0027804 | 0.0027805 | 0.0027805 | 0.97605 | -0.16827 | 0.97594 | -0.16906 | 1.0298
51 | 0.0091886 | 0.0023014 | -0.0091883 | -0.0023013 | 3.361e-07 | 9.5361e-08 | 0.014049 | 0.014049 | 0.014049 | 0.97319 | -0.18883 | 0.97315 | -0.18909 | 5.2033
52 | 0.0089974 | 0.0022535 | -0.0089955 | -0.0022529 | 1.907e-06 | 5.3287e-07 | 0.013757 | 0.013757 | 0.013757 | 0.97315 | -0.18909 | 0.97294 | -0.19062 | 5.0953
53 | -0.0068981 | -0.001723 | 0.0068992 | 0.0017232 | 1.1333e-06 | 2.1731e-07 | 0.010352 | 0.010352 | 0.010352 | 0.99137 | -0.060665 | 0.99154 | -0.05947 | 3.834
54 | -0.0077874 | -0.0019458 | 0.0077878 | 0.0019459 | 4.1474e-07 | 9.6722e-08 | 0.011685 | 0.011685 | 0.011685 | 0.99154 | -0.05947 | 0.99159 | -0.059083 | 4.3276
55 | -0.0083994 | -0.0020992 | 0.0084013 | 0.0020997 | 1.8429e-06 | 4.6888e-07 | 0.012602 | 0.012602 | 0.012602 | 0.99159 | -0.059083 | 0.99182 | -0.05749 | 4.6675
56 | -0.0090225 | -0.0022554 | 0.0090225 | 0.0022554 | 7.622e-08 | 2.071e-08 | 0.013534 | 0.013534 | 0.013534 | 0.99182 | -0.05749 | 0.99183 | -0.057428 | 5.0127
57 | -0.0096874 | -0.002422 | 0.0096957 | 0.0024244 | 8.2674e-06 | 2.3693e-06 | 0.014532 | 0.014531 | 0.014532 | 0.99183 | -0.057428 | 0.9927 | -0.051237 | 5.3821
58 | -0.0096957 | -0.0024244 | 0.0097065 | 0.0024275 | 1.0753e-05 | 3.0795e-06 | 0.014531 | 0.014531 | 0.014531 | 0.9927 | -0.051237 | 0.99384 | -0.043195 | 5.382
59 | -0.025317 | -0.006345 | 0.025323 | 0.0063473 | 6.1829e-06 | 2.2909e-06 | 0.038149 | 0.038149 | 0.038149 | 0.9875 | -0.087596 | 0.98775 | -0.085833 | 14.1292
60 | 0.004487 | 0.0011243 | -0.0044861 | -0.0011243 | 9.5038e-07 | -6.1028e-08 | 0.0067595 | 0.0067597 | 0.0067597 | 0.98775 | -0.085833 | 0.98753 | -0.087363 | 2.5036
61 | -0.02981 | -0.0074716 | 0.029825 | 0.0074773 | 1.5245e-05 | 5.7083e-06 | 0.044908 | 0.044908 | 0.044908 | 0.98775 | -0.085833 | 0.98827 | -0.082141 | 16.6327
62 | 0.022655 | 0.005679 | -0.02264 | -0.0056737 | 1.4345e-05 | 5.2643e-06 | 0.034111 | 0.034111 | 0.034111 | 0.98827 | -0.082141 | 0.98762 | -0.086716 | 12.6338
63 | -0.05248 | -0.013156 | 0.052513 | 0.013169 | 3.3121e-05 | 1.263e-05 | 0.07902 | 0.07902 | 0.07902 | 0.98827 | -0.082141 | 0.98891 | -0.077587 | 29.2665
64 | 0.015205 | 0.0038103 | -0.015205 | -0.0038103 | 7.1405e-08 | 2.4673e-08 | 0.022909 | 0.022909 | 0.022909 | 0.98762 | -0.086716 | 0.98762 | -0.08675 | 8.4848
65 | -0.060237 | -0.015105 | 0.060277 | 0.01512 | 3.9405e-05 | 1.5057e-05 | 0.090642 | 0.090642 | 0.090642 | 0.98891 | -0.077587 | 0.98958 | -0.07287 | 33.571
66 | 0.012305 | 0.0030833 | -0.012299 | -0.0030814 | 5.7676e-06 | 1.8743e-06 | 0.018539 | 0.018539 | 0.018539 | 0.98762 | -0.08675 | 0.98714 | -0.090138 | 6.8663
67 | -0.063469 | -0.01592 | 0.063679 | 0.016 | 0.00021059 | 8.0518e-05 | 0.095442 | 0.095441 | 0.095442 | 0.98958 | -0.07287 | 0.99297 | -0.049023 | 35.3487
68 | -0.0014617 | -0.00036634 | 0.0014618 | 0.00036618 | 4.2144e-08 | -1.5668e-07 | 0.002219 | 0.002219 | 0.002219 | 0.98017 | -0.13907 | 0.9802 | -0.13887 | 0.82187
69 | 0.019804 | 0.004963 | -0.019795 | -0.0049598 | 9.0751e-06 | 3.2877e-06 | 0.030064 | 0.030064 | 0.030064 | 0.9802 | -0.13887 | 0.97974 | -0.14218 | 11.1349
70 | -0.021266 | -0.0053292 | 0.021278 | 0.0053335 | 1.1692e-05 | 4.2703e-06 | 0.032283 | 0.032283 | 0.032283 | 0.9802 | -0.13887 | 0.98076 | -0.13489 | 11.9567
71 | 0.017456 | 0.0043735 | -0.017446 | -0.0043699 | 9.8558e-06 | 3.5079e-06 | 0.026511 | 0.026511 | 0.026511 | 0.97974 | -0.14218 | 0.97917 | -0.14626 | 9.819
72 | -0.02341 | -0.005868 | 0.023442 | 0.0058796 | 3.1515e-05 | 1.1615e-05 | 0.035519 | 0.035518 | 0.035519 | 0.98076 | -0.13489 | 0.98212 | -0.12519 | 13.155
73 | 0.0013582 | 0.00034028 | -0.0013582 | -0.0003404 | 2.6356e-08 | -1.18e-07 | 0.00205 | 0.0020501 | 0.0020501 | 0.98585 | -0.098719 | 0.98583 | -0.09886 | 0.75929
74 | 0.026301 | 0.0066067 | -0.026296 | -0.0066046 | 5.4945e-06 | 2.0421e-06 | 0.039704 | 0.039704 | 0.039704 | 0.98585 | -0.098719 | 0.98564 | -0.10022 | 14.7051
75 | 0.024843 | 0.0062404 | -0.024824 | -0.0062336 | 1.8412e-05 | 6.8146e-06 | 0.03751 | 0.03751 | 0.03751 | 0.98564 | -0.10022 | 0.98488 | -0.10556 | 13.8927
76 | 0.012858 | 0.0032203 | -0.012841 | -0.0032145 | 1.7208e-05 | 5.7113e-06 | 0.019539 | 0.01954 | 0.01954 | 0.97917 | -0.14626 | 0.97782 | -0.15595 | 7.2369
77 | 0.0029128 | 0.0007299 | -0.0029127 | -0.00072999 | 1.3916e-07 | -8.9635e-08 | 0.0044265 | 0.0044265 | 0.0044265 | 0.97917 | -0.14626 | 0.97912 | -0.14661 | 1.6395
78 | -0.023442 | -0.0058796 | 0.023489 | 0.005897 | 4.7167e-05 | 1.7381e-05 | 0.035518 | 0.035518 | 0.035518 | 0.98212 | -0.12519 | 0.98416 | -0.1107 | 13.1549
79 | 0.023506 | 0.0059032 | -0.023489 | -0.005897 | 1.6806e-05 | 6.1924e-06 | 0.035518 | 0.035518 | 0.035518 | 0.98488 | -0.10556 | 0.98416 | -0.1107 | 13.1548
80 | 0.0086331 | 0.0021621 | -0.0086315 | -0.0021617 | 1.5248e-06 | 4.1241e-07 | 0.013203 | 0.013203 | 0.013203 | 0.97294 | -0.19062 | 0.97276 | -0.1919 | 4.89
81 | -0.0015484 | -0.00038775 | 0.0015484 | 0.0003876 | 4.417e-08 | -1.5368e-07 | 0.0023183 | 0.0023182 | 0.0023183 | 0.99381 | -0.043402 | 0.99384 | -0.043195 | 0.85863
82 | 0.00066588 | 0.00016657 | -0.00066587 | -0.00016688 | 1.5208e-08 | -3.1185e-07 | 0.00099691 | 0.00099702 | 0.00099702 | 0.99381 | -0.043402 | 0.99378 | -0.043567 | 0.36927
83 | -0.011255 | -0.0028151 | 0.011276 | 0.0028218 | 2.1567e-05 | 6.7143e-06 | 0.016849 | 0.016849 | 0.016849 | 0.99384 | -0.043195 | 0.9958 | -0.029318 | 6.2405
84 | 0.0011681 | 0.00029265 | -0.0011681 | -0.00029275 | 1.5761e-08 | -1.0179e-07 | 0.0017455 | 0.0017455 | 0.0017455 | 0.9958 | -0.029318 | 0.99579 | -0.029415 | 0.64648
85 | -0.0025419 | -0.00063707 | 0.0025424 | 0.0006366 | 4.6829e-07 | -4.7219e-07 | 0.0038336 | 0.0038334 | 0.0038336 | 0.98664 | -0.093656 | 0.98683 | -0.092324 | 1.4199
86 | 0.0042839 | 0.0010734 | -0.0042832 | -0.0010735 | 6.9903e-07 | -7.4095e-08 | 0.0064595 | 0.0064596 | 0.0064596 | 0.98683 | -0.092324 | 0.98667 | -0.093503 | 2.3924
87 | -0.0068263 | -0.00171 | 0.0068284 | 0.0017104 | 2.0638e-06 | 3.948e-07 | 0.010293 | 0.010293 | 0.010293 | 0.98683 | -0.092324 | 0.98714 | -0.090138 | 3.8122
88 | 0.06073 | 0.015265 | -0.060647 | -0.015234 | 8.3043e-05 | 3.1732e-05 | 0.091023 | 0.091023 | 0.091023 | 0.99297 | -0.049023 | 0.99156 | -0.058855 | 33.7122
89 | 0.058343 | 0.014656 | -0.058246 | -0.01462 | 9.6191e-05 | 3.6738e-05 | 0.087565 | 0.087565 | 0.087565 | 0.99156 | -0.058855 | 0.98988 | -0.070729 | 32.4316
90 | 0.055774 | 0.014 | -0.055747 | -0.01399 | 2.6273e-05 | 1.0028e-05 | 0.083848 | 0.083848 | 0.083848 | 0.98988 | -0.070729 | 0.9894 | -0.074123 | 31.055
91 | 0.048768 | 0.012241 | -0.04875 | -0.012234 | 1.8407e-05 | 7.0093e-06 | 0.073352 | 0.073352 | 0.073352 | 0.9894 | -0.074123 | 0.98901 | -0.076843 | 27.1673
92 | 0.043328 | 0.010875 | -0.043258 | -0.010848 | 6.9906e-05 | 2.6549e-05 | 0.065195 | 0.065195 | 0.065195 | 0.98901 | -0.076843 | 0.98737 | -0.088482 | 24.1462
93 | 0.032731 | 0.0082099 | -0.032687 | -0.0081933 | 4.4191e-05 | 1.6625e-05 | 0.04933 | 0.04933 | 0.04933 | 0.98737 | -0.088482 | 0.98599 | -0.098232 | 18.2704
94 | -0.00039297 | -9.8486e-05 | 0.00039297 | 9.832e-05 | 3.0514e-09 | -1.6683e-07 | 0.00060114 | 0.00060108 | 0.00060114 | 0.97272 | -0.19219 | 0.97273 | -0.19213 | 0.22264
95 | -0.00083914 | -0.00021014 | 0.00083914 | 0.00021007 | 6.0124e-09 | -7.0284e-08 | 0.0012836 | 0.0012836 | 0.0012836 | 0.97273 | -0.19213 | 0.97274 | -0.19208 | 0.4754
96 | -0.0010335 | -0.00025878 | 0.0010335 | 0.00025859 | 2.514e-08 | -1.9045e-07 | 0.0015809 | 0.0015808 | 0.0015809 | 0.97274 | -0.19208 | 0.97276 | -0.1919 | 0.58552
97 | 0.007598 | 0.0019031 | -0.0075909 | -0.0019014 | 7.0487e-06 | 1.6739e-06 | 0.011622 | 0.011622 | 0.011622 | 0.97276 | -0.1919 | 0.97183 | -0.19861 | 4.3046
98 | 0.0046328 | 0.00116 | -0.0046324 | -0.00116 | 3.6879e-07 | -3.6965e-09 | 0.0070931 | 0.0070931 | 0.0070931 | 0.97183 | -0.19861 | 0.97175 | -0.19919 | 2.6271
99 | 0.004041 | 0.0010118 | -0.0040408 | -0.0010118 | 1.4932e-07 | -2e-08 | 0.0061875 | 0.0061875 | 0.0061875 | 0.97175 | -0.19919 | 0.97171 | -0.19946 | 2.2917
100 | 0.002627 | 0.00065747 | -0.0026264 | -0.00065791 | 5.2186e-07 | -4.3942e-07 | 0.0040224 | 0.0040226 | 0.0040226 | 0.97171 | -0.19946 | 0.97152 | -0.2009 | 1.4899
101 | 0.0026264 | 0.00065791 | -0.0026261 | -0.00065817 | 3.1062e-07 | -2.6139e-07 | 0.0040226 | 0.0040228 | 0.0040228 | 0.97152 | -0.2009 | 0.9714 | -0.20175 | 1.4899
102 | -0.0010138 | -0.00025407 | 0.0010139 | 0.0002527 | 1.6988e-07 | -1.3693e-06 | 0.001543 | 0.0015425 | 0.001543 | 0.97765 | -0.15717 | 0.97782 | -0.15595 | 0.57147
103 | 0.010047 | 0.0025158 | -0.010047 | -0.0025157 | 3.5648e-07 | 1.0645e-07 | 0.015289 | 0.015289 | 0.015289 | 0.97782 | -0.15595 | 0.97778 | -0.15621 | 5.6626
104 | 0.0087673 | 0.002195 | -0.0087642 | -0.0021942 | 3.1652e-06 | 8.6008e-07 | 0.013342 | 0.013342 | 0.013342 | 0.97778 | -0.15621 | 0.97742 | -0.15882 | 4.9414
105 | 0.0074082 | 0.0018544 | -0.0074077 | -0.0018542 | 4.96e-07 | 1.1254e-07 | 0.011281 | 0.011281 | 0.011281 | 0.9771 | -0.16111 | 0.97703 | -0.16159 | 4.1782
106 | -0.0074082 | -0.0018544 | 0.0074105 | 0.0018549 | 2.3377e-06 | 5.3028e-07 | 0.011281 | 0.011281 | 0.011281 | 0.9771 | -0.16111 | 0.97742 | -0.15882 | 4.1782
107 | 0.00334 | 0.00083478 | -0.0033386 | -0.00083531 | 1.3353e-06 | -5.2197e-07 | 0.0050859 | 0.0050863 | 0.0050863 | 0.97703 | -0.16159 | 0.97663 | -0.16449 | 1.8838
108 | 0.0023896 | 0.00059745 | -0.0023892 | -0.00059787 | 3.7251e-07 | -4.203e-07 | 0.0036403 | 0.0036405 | 0.0036405 | 0.97663 | -0.16449 | 0.97647 | -0.16562 | 1.3483
109 | 0.0018281 | 0.00045725 | -0.0018278 | -0.00045782 | 2.6042e-07 | -5.7254e-07 | 0.0027855 | 0.0027857 | 0.0027857 | 0.97647 | -0.16562 | 0.97633 | -0.16666 | 1.0317
110 | 0.00058535 | 0.00014642 | -0.00058534 | -0.0001467 | 1.1169e-08 | -2.7697e-07 | 0.00089203 | 0.00089213 | 0.00089213 | 0.97633 | -0.16666 | 0.97631 | -0.16679 | 0.33042
111 | 0.022878 | 0.005735 | -0.022873 | -0.0057333 | 4.5325e-06 | 1.6656e-06 | 0.034527 | 0.034527 | 0.034527 | 0.98599 | -0.098232 | 0.98579 | -0.099663 | 12.7877
112 | 0.015866 | 0.003977 | -0.015858 | -0.0039744 | 7.6227e-06 | 2.6604e-06 | 0.023949 | 0.023949 | 0.023949 | 0.98579 | -0.099663 | 0.9853 | -0.10313 | 8.8701
113 | 0.013122 | 0.0032887 | -0.013121 | -0.0032882 | 1.3876e-06 | 4.6157e-07 | 0.019817 | 0.019817 | 0.019817 | 0.9853 | -0.10313 | 0.98519 | -0.1039 | 7.3397
114 | 0.0059597 | 0.0014935 | -0.0059583 | -0.0014933 | 1.3557e-06 | 1.8007e-07 | 0.0090013 | 0.0090014 | 0.0090014 | 0.98519 | -0.1039 | 0.98496 | -0.10554 | 3.3339

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.22018 | 0.055353

## res_load
| p_mw | q_mvar
0 | 0.0009514 | 0.00023844
1 | 0.00073676 | 0.00018465
2 | 0.0026415 | 0.00066203
3 | 0.0014419 | 0.00036139
4 | 0.0008502 | 0.00021308
5 | 0.00086644 | 0.00021715
6 | 0.00078184 | 0.00019595
7 | 0.0012218 | 0.00030621
8 | 0.0026916 | 0.00067457
9 | 0.0008578 | 0.00021499
10 | 0.0017065 | 0.00042769
11 | 0.001298 | 0.00032532
12 | 0.00034686 | 8.6932e-05
13 | 0.00094643 | 0.0002372
14 | 0.0011086 | 0.00027785
15 | 0.0013083 | 0.00032789
16 | 0.00054383 | 0.0001363
17 | 0.00035698 | 8.9467e-05
18 | 0.0024197 | 0.00060644
19 | 0.00036847 | 9.2347e-05
20 | 0.00020852 | 5.2261e-05
21 | 0.00092553 | 0.00023196
22 | 0.000359 | 8.9975e-05
23 | 0.00032565 | 8.1616e-05
24 | 0.00040878 | 0.00010245
25 | 0.00050308 | 0.00012608
26 | 0.0012124 | 0.00030386
27 | 0.001471 | 0.00036867
28 | 0.00065219 | 0.00016345
29 | 0.0013204 | 0.00033092
30 | 0.00070164 | 0.00017585
31 | 0.0008831 | 0.00022133
32 | 0.002084 | 0.0005223
33 | 0.0015662 | 0.00039254
34 | 0.0034167 | 0.00085631
35 | 0.00083136 | 0.00020836
36 | 0.00084554 | 0.00021191
37 | 0.0010212 | 0.00025595
38 | 0.0018237 | 0.00045705
39 | 0.00065341 | 0.00016376
40 | 0.00019082 | 4.7823e-05
41 | 0.002786 | 0.00069823
42 | 0.00088818 | 0.0002226
43 | 0.0006116 | 0.00015328
44 | 0.00062118 | 0.00015568
45 | 0.0006649 | 0.00016664
46 | 0.025317 | 0.006345
47 | 0.0044861 | 0.0011243
48 | 0.0074351 | 0.0018634
49 | 0.0077239 | 0.0019358
50 | 0.0029005 | 0.00072694
51 | 0.003192 | 0.0008
52 | 0.0014617 | 0.00036634
53 | 0.0023393 | 0.0005863
54 | 0.0021326 | 0.00053447
55 | 0.0013582 | 0.0003404
56 | 0.001453 | 0.00036416
57 | 0.001675 | 0.00041979
58 | 0.0013186 | 0.00033048
59 | 0.00036248 | 9.0845e-05
60 | 0.00088251 | 0.00022118
61 | 0.00066587 | 0.00016688
62 | 0.0019496 | 0.00048862
63 | 0.0011681 | 0.00029275
64 | 0.0025419 | 0.00063707
65 | 0.0042832 | 0.0010735
66 | 0.0054705 | 0.001371
67 | 0.0023041 | 0.00057745
68 | 0.0024726 | 0.0006197
69 | 0.0069794 | 0.0017492
70 | 0.0054216 | 0.0013588
71 | 0.010527 | 0.0026384
72 | 0.0010065 | 0.00025224
73 | 0.00039297 | 9.8486e-05
74 | 0.00044617 | 0.00011182
75 | 0.00019438 | 4.8715e-05
76 | 0.0029582 | 0.00074138
77 | 0.00059145 | 0.00014823
78 | 0.0014139 | 0.00035435
79 | 0.0026261 | 0.00065817
80 | 0.0010138 | 0.00025407
81 | 0.0017796 | 0.000446
82 | 0.0012797 | 0.00032072
83 | 0.0040677 | 0.0010195
84 | 0.0013537 | 0.00033926
85 | 0.00094905 | 0.00023785
86 | 0.0005611 | 0.00014063
87 | 0.0012425 | 0.0003114
88 | 0.00058534 | 0.0001467
89 | 0.0029127 | 0.00072999
90 | 0.0098088 | 0.0024583
91 | 0.0070076 | 0.0017563
92 | 0.0027361 | 0.00068573
93 | 0.007161 | 0.0017947
94 | 0.0059583 | 0.0014933

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1