## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1405-19_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1405-19_0_2_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_1405-19_0_2_node_4 | 0.4 | n |  | TRUE
3 | bus_LV_1405-19_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1405-19_0_2_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_1405-19_0_2_node_22 | 0.4 | n |  | TRUE
6 | bus_LV_1405-19_0_2_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_1405-19_0_2_node_62 | 0.4 | n |  | TRUE
8 | bus_LV_1405-19_0_2_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_1405-19_0_2_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_1405-19_0_2_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_1405-19_0_2_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_1405-19_0_2_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_1405-19_0_2_node_12 | 0.4 | n |  | TRUE
14 | bus_LV_1405-19_0_2_node_13 | 0.4 | n |  | TRUE
15 | bus_LV_1405-19_0_2_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_1405-19_0_2_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_1405-19_0_2_node_16 | 0.4 | n |  | TRUE
18 | bus_LV_1405-19_0_2_node_17 | 0.4 | n |  | TRUE
19 | bus_LV_1405-19_0_2_node_54 | 0.4 | n |  | TRUE
20 | bus_LV_1405-19_0_2_node_57 | 0.4 | n |  | TRUE
21 | bus_LV_1405-19_0_2_node_61 | 0.4 | n |  | TRUE
22 | bus_LV_1405-19_0_2_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_1405-19_0_2_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_1405-19_0_2_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_1405-19_0_2_node_46 | 0.4 | n |  | TRUE
26 | bus_LV_1405-19_0_2_node_48 | 0.4 | n |  | TRUE
27 | bus_LV_1405-19_0_2_node_65 | 0.4 | n |  | TRUE
28 | bus_LV_1405-19_0_2_node_53 | 0.4 | n |  | TRUE
29 | bus_LV_1405-19_0_2_node_58 | 0.4 | n |  | TRUE
30 | bus_LV_1405-19_0_2_node_59 | 0.4 | n |  | TRUE
31 | bus_LV_1405-19_0_2_node_60 | 0.4 | n |  | TRUE
32 | bus_LV_1405-19_0_2_node_63 | 0.4 | n |  | TRUE
33 | bus_LV_1405-19_0_2_node_113 | 0.4 | n |  | TRUE
34 | bus_MV_0_node_13 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1405-19_0_2_load_0 | 0 | 0.0028861 | 0.00072332 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1405-19_0_2_load_6 | 4 | 0.0026909 | 0.00067441 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1405-19_0_2_load_5 | 6 | 0.002852 | 0.00071478 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1405-19_0_2_load_62 | 7 | 0.0011611 | 0.000291 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1405-19_0_2_load_7 | 8 | 0.0035637 | 0.00089315 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1405-19_0_2_load_10 | 11 | 0.0024662 | 0.00061808 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1405-19_0_2_load_11 | 12 | 0.0032878 | 0.00082401 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1405-19_0_2_load_12 | 13 | 0.0017724 | 0.00044422 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1405-19_0_2_load_13 | 14 | 0.0008499 | 0.00021301 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1405-19_0_2_load_14 | 15 | 0.0074236 | 0.0018605 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1405-19_0_2_load_15 | 16 | 0.0011448 | 0.00028691 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1405-19_0_2_load_17 | 18 | 0.0015227 | 0.00038162 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1405-19_0_2_load_54 | 19 | 0.0012921 | 0.00032384 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1405-19_0_2_load_57 | 20 | 0.00083082 | 0.00020822 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1405-19_0_2_load_61 | 21 | 0.00063672 | 0.00015958 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1405-19_0_2_load_18 | 22 | 0.0037714 | 0.0009452 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1405-19_0_2_load_21 | 24 | 0.0016755 | 0.00041991 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1405-19_0_2_load_53 | 28 | 0.0067185 | 0.0016838 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1405-19_0_2_load_59 | 30 | 0.004173 | 0.0010459 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1405-19_0_2_load_60 | 31 | 0.0068298 | 0.0017117 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1405-19_0_2_load_63 | 32 | 0.0017084 | 0.00042817 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1405-19_0_2_load_113 | 33 | 0.00046245 | 0.0001159 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 14 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1405-19_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.022971 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1405-19_0_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.011684 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1405-19_0_2_line_2 | NAYY 4x150 SE | 2 | 6 | 0.066201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1405-19_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.013425 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1405-19_0_2_line_4 | NAYY 4x150 SE | 3 | 4 | 0.13993 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1405-19_0_2_line_5 | NAYY 4x150 SE | 3 | 5 | 0.021957 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1405-19_0_2_line_6 | NAYY 4x150 SE | 5 | 15 | 0.015499 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1405-19_0_2_line_7 | NAYY 4x150 SE | 5 | 23 | 0.072969 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1405-19_0_2_line_8 | NAYY 4x150 SE | 6 | 7 | 0.014483 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1405-19_0_2_line_9 | NAYY 4x150 SE | 7 | 32 | 0.023358 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1405-19_0_2_line_10 | NAYY 4x150 SE | 8 | 9 | 0.012317 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1405-19_0_2_line_11 | NAYY 4x150 SE | 8 | 10 | 0.026012 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1405-19_0_2_line_12 | NAYY 4x150 SE | 9 | 11 | 0.0078293 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1405-19_0_2_line_13 | NAYY 4x150 SE | 9 | 12 | 0.0071379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1405-19_0_2_line_14 | NAYY 4x150 SE | 10 | 13 | 0.17928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1405-19_0_2_line_15 | NAYY 4x150 SE | 10 | 14 | 0.035953 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1405-19_0_2_line_16 | NAYY 4x150 SE | 11 | 15 | 0.042251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1405-19_0_2_line_17 | NAYY 4x150 SE | 12 | 16 | 0.03693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1405-19_0_2_line_18 | NAYY 4x150 SE | 13 | 17 | 0.0033891 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1405-19_0_2_line_19 | NAYY 4x150 SE | 14 | 18 | 0.053482 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1405-19_0_2_line_20 | NAYY 4x150 SE | 17 | 19 | 0.033056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1405-19_0_2_line_21 | NAYY 4x150 SE | 17 | 20 | 0.035162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1405-19_0_2_line_22 | NAYY 4x150 SE | 18 | 21 | 0.0034302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1405-19_0_2_line_23 | NAYY 4x150 SE | 19 | 26 | 0.05752 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1405-19_0_2_line_24 | NAYY 4x150 SE | 22 | 23 | 0.019509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1405-19_0_2_line_25 | NAYY 4x150 SE | 23 | 24 | 0.006553 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1405-19_0_2_line_26 | NAYY 4x150 SE | 25 | 26 | 0.064503 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1405-19_0_2_line_27 | NAYY 4x150 SE | 25 | 27 | 0.21132 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1405-19_0_2_line_28 | NAYY 4x150 SE | 26 | 28 | 0.11278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1405-19_0_2_line_29 | NAYY 4x150 SE | 27 | 33 | 0.046676 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1405-19_0_2_line_30 | NAYY 4x150 SE | 28 | 29 | 0.0064728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1405-19_0_2_line_31 | NAYY 4x150 SE | 29 | 30 | 0.16037 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1405-19_0_2_line_32 | NAYY 4x150 SE | 29 | 31 | 0.055909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1405-19_0_2_trafo_13 | 0.25 MVA 20/0.4 kV | 34 | 14 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2655558.6421 | 1182071.5434 | 2655551.6243 | 1182065.7974 | 2655542.9062 | 1182059.7689 | 2655539.8908 | 1182058.4249
1 | 2655558.6421 | 1182071.5434 | 2655559.8904 | 1182072.8001 | 2655567.4592 | 1182079.2293
2 | 2655567.4592 | 1182079.2293 | 2655578.8349 | 1182083.5816 | 2655595.5303 | 1182087.3829 | 2655621.3192 | 1182093.7811 | 2655631.6053 | 1182094.7092
3 | 2655567.4592 | 1182079.2293 | 2655556.0541 | 1182086.3109
4 | 2655427.454 | 1182140.868 | 2655432.1225 | 1182138.0762 | 2655466.39 | 1182125.197 | 2655505.7579 | 1182110.7421 | 2655535.6054 | 1182096.933 | 2655553.5579 | 1182087.8609 | 2655556.0541 | 1182086.3109
5 | 2655442.4648 | 1182156.7266 | 2655434.9916 | 1182150.6764 | 2655427.454 | 1182140.868
6 | 2655442.4648 | 1182156.7266 | 2655451.2719 | 1182161.3773 | 2655456.4712 | 1182163.2898
7 | 2655444.7455 | 1182209.8216 | 2655445.7271 | 1182208.5411 | 2655447.3106 | 1182206.588 | 2655451.2199 | 1182201.6658 | 2655464.9411 | 1182184.4053 | 2655467.0555 | 1182179.5333 | 2655466.2561 | 1182175.9795 | 2655463.5563 | 1182173.1418 | 2655448.7854 | 1182165.2009 | 2655444.2457 | 1182161.4902 | 2655442.4648 | 1182156.7266
8 | 2655631.6053 | 1182094.7092 | 2655633.1299 | 1182094.8468 | 2655646.077 | 1182094.4697
9 | 2655646.077 | 1182094.4697 | 2655669.425 | 1182093.7898
10 | 2655503.1174 | 1182181.4902 | 2655510.5688 | 1182185.7505 | 2655513.2086 | 1182188.3904
11 | 2655525.795 | 1182210.4718 | 2655520.9053 | 1182196.7522 | 2655516.9681 | 1182191.4906 | 2655513.5422 | 1182188.7241 | 2655513.2086 | 1182188.3904
12 | 2655503.1174 | 1182181.4902 | 2655495.8777 | 1182178.5096
13 | 2655503.1174 | 1182181.4902 | 2655508.9313 | 1182177.8754 | 2655509.2178 | 1182177.82
14 | 2655525.795 | 1182210.4718 | 2655541.2113 | 1182270.7035 | 2655542.0819 | 1182282.2291 | 2655541.0017 | 1182292.5025 | 2655535.7558 | 1182314.7663 | 2655536.2636 | 1182325.0656 | 2655540.0169 | 1182343.5662 | 2655541.2653 | 1182357.1742 | 2655540.9783 | 1182386.6672
15 | 2655525.795 | 1182210.4718 | 2655560.5992 | 1182201.4558 | 2655560.5992 | 1182201.4558
16 | 2655456.4712 | 1182163.2898 | 2655479.3607 | 1182171.7095 | 2655495.8777 | 1182178.5096
17 | 2655545.946 | 1182178.3628 | 2655516.558 | 1182176.4007 | 2655509.2178 | 1182177.82
18 | 2655540.9453 | 1182390.0562 | 2655540.9783 | 1182386.6672
19 | 2655588.5037 | 1182167.7071 | 2655586.7232 | 1182184.0104 | 2655582.0488 | 1182198.1416 | 2655573.4856 | 1182201.7865 | 2655560.5992 | 1182201.4558
20 | 2655540.9453 | 1182390.0562 | 2655542.047 | 1182398.8935 | 2655544.2691 | 1182405.4733 | 2655549.1809 | 1182413.4899 | 2655555.0489 | 1182418.6338
21 | 2655540.9453 | 1182390.0562 | 2655538.8279 | 1182391.126 | 2655523.0666 | 1182415.9828 | 2655522.6145 | 1182419.3096
22 | 2655588.8761 | 1182164.2972 | 2655588.5037 | 1182167.7071
23 | 2655589.4353 | 1182463.813 | 2655582.2955 | 1182449.0387 | 2655577.7087 | 1182441.3919 | 2655569.1743 | 1182431.2627 | 2655562.5113 | 1182425.1754 | 2655555.0489 | 1182418.6338
24 | 2655444.7455 | 1182209.8216 | 2655432.3602 | 1182224.8953
25 | 2655444.7455 | 1182209.8216 | 2655444.8943 | 1182211.9019 | 2655448.3114 | 1182214.7907
26 | 2655596.8367 | 1182527.7505 | 2655592.7753 | 1182508.7356 | 2655589.4353 | 1182463.813
27 | 2655596.8367 | 1182527.7505 | 2655807.2079 | 1182547.7711
28 | 2655589.4353 | 1182463.813 | 2655604.2541 | 1182428.6198 | 2655607.8773 | 1182421.6161 | 2655615.8574 | 1182394.375 | 2655619.1316 | 1182376.4399 | 2655620.2995 | 1182356.3791
29 | 2655807.2079 | 1182547.7711 | 2655793.1225 | 1182549.1853 | 2655788.929 | 1182553.4597 | 2655790.079 | 1182559.5183 | 2655804.1584 | 1182574.3353
30 | 2655620.6757 | 1182349.9172 | 2655620.2995 | 1182356.3791
31 | 2655620.6757 | 1182349.9172 | 2655620.0008 | 1182331.3118 | 2655622.0678 | 1182312.6317 | 2655635.0909 | 1182280.1122 | 2655642.5179 | 1182263.1272 | 2655649.714 | 1182251.2874 | 2655648.2379 | 1182242.4911 | 2655645.2718 | 1182236.2712 | 2655642.5689 | 1182227.2078 | 2655644.7788 | 1182215.355 | 2655652.5601 | 1182198.8736
32 | 2655659.681 | 1182310.2571 | 2655647.7862 | 1182324.0433 | 2655634.7436 | 1182339.7421 | 2655620.6757 | 1182349.9172

## bus_geodata
| x | y | coords
0 | 2655539.8908 | 1182058.4249
1 | 2655558.6421 | 1182071.5434
2 | 2655567.4592 | 1182079.2293
3 | 2655427.454 | 1182140.868
4 | 2655556.0541 | 1182086.3109
5 | 2655442.4648 | 1182156.7266
6 | 2655631.6053 | 1182094.7092
7 | 2655646.077 | 1182094.4697
8 | 2655513.2086 | 1182188.3904
9 | 2655503.1174 | 1182181.4902
10 | 2655525.795 | 1182210.4718
11 | 2655495.8777 | 1182178.5096
12 | 2655509.2178 | 1182177.82
13 | 2655540.9783 | 1182386.6672
14 | 2655560.5992 | 1182201.4558
15 | 2655456.4712 | 1182163.2898
16 | 2655545.946 | 1182178.3628
17 | 2655540.9453 | 1182390.0562
18 | 2655588.5037 | 1182167.7071
19 | 2655555.0489 | 1182418.6338
20 | 2655522.6145 | 1182419.3096
21 | 2655588.8761 | 1182164.2972
22 | 2655432.3602 | 1182224.8953
23 | 2655444.7455 | 1182209.8216
24 | 2655448.3114 | 1182214.7906
25 | 2655596.8367 | 1182527.7505
26 | 2655589.4353 | 1182463.813
27 | 2655807.2079 | 1182547.7711
28 | 2655620.2995 | 1182356.3791
29 | 2655620.6757 | 1182349.9172
30 | 2655652.5601 | 1182198.8736
31 | 2655659.681 | 1182310.2571
32 | 2655669.425 | 1182093.7898
33 | 2655804.1584 | 1182574.3353
34 | 2655560.5992 | 1182201.4558

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99014 | -0.06925 | 0.0028861 | 0.00072332
1 | 0.99023 | -0.068575 | 0 | 0
2 | 0.99028 | -0.068232 | 0 | 0
3 | 0.99272 | -0.050976 | 0 | 0
4 | 0.99045 | -0.067054 | 0.0026909 | 0.00067441
5 | 0.99308 | -0.048458 | 0 | 0
6 | 0.98974 | -0.072093 | 0.002852 | 0.00071478
7 | 0.98968 | -0.072517 | 0.0011611 | 0.000291
8 | 0.99577 | -0.029531 | 0.0035637 | 0.00089315
9 | 0.99522 | -0.033391 | 0 | 0
10 | 0.99707 | -0.020462 | 0 | 0
11 | 0.99492 | -0.035497 | 0.0024662 | 0.00061808
12 | 0.99518 | -0.03371 | 0.0032878 | 0.00082401
13 | 0.99135 | -0.060583 | 0.0017724 | 0.00044422
14 | 1 | 0 | -0.060211 | -0.014941
15 | 0.99346 | -0.045826 | 0.0074236 | 0.0018605
16 | 0.99512 | -0.034137 | 0.0011448 | 0.00028691
17 | 0.99125 | -0.061284 | 0 | 0
18 | 0.99984 | -0.0011544 | 0.0015227 | 0.00038162
19 | 0.99032 | -0.067853 | 0.0012921 | 0.00032384
20 | 0.9912 | -0.061582 | 0.00083082 | 0.00020822
21 | 0.99983 | -0.0011762 | 0.00063672 | 0.00015958
22 | 0.99241 | -0.053233 | 0.0037714 | 0.0009452
23 | 0.99251 | -0.052487 | 0 | 0
24 | 0.9925 | -0.052599 | 0.0016755 | 0.00041991
25 | 0.98876 | -0.078874 | 0 | 0
26 | 0.9888 | -0.078552 | 0 | 0
27 | 0.98862 | -0.079904 | 0 | 0
28 | 0.98591 | -0.099044 | 0.0067185 | 0.0016838
29 | 0.98581 | -0.099777 | 0 | 0
30 | 0.98484 | -0.10667 | 0.004173 | 0.0010459
31 | 0.98526 | -0.1037 | 0.0068298 | 0.0017117
32 | 0.98962 | -0.072924 | 0.0017084 | 0.00042817
33 | 0.98859 | -0.080125 | 0.00046245 | 0.0001159
34 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0028861 | -0.00072332 | 0.0028863 | 0.00072313 | 2.6964e-07 | -1.9177e-07 | 0.0043373 | 0.0043372 | 0.0043373 | 0.99014 | -0.06925 | 0.99023 | -0.068575 | 1.6064
1 | -0.0028863 | -0.00072313 | 0.0028865 | 0.00072303 | 1.3715e-07 | -9.7565e-08 | 0.0043372 | 0.0043371 | 0.0043372 | 0.99023 | -0.068575 | 0.99028 | -0.068232 | 1.6064
2 | 0.0057248 | 0.0014339 | -0.0057218 | -0.0014336 | 3.0567e-06 | 3.2442e-07 | 0.0086019 | 0.0086022 | 0.0086022 | 0.99028 | -0.068232 | 0.98974 | -0.072093 | 3.186
3 | -0.0086113 | -0.0021569 | 0.0086127 | 0.0021573 | 1.4025e-06 | 3.6667e-07 | 0.012939 | 0.012939 | 0.012939 | 0.99028 | -0.068232 | 0.99045 | -0.067054 | 4.7923
4 | 0.011329 | 0.0028396 | -0.011304 | -0.0028317 | 2.5179e-05 | 7.8791e-06 | 0.016981 | 0.016982 | 0.016982 | 0.99272 | -0.050976 | 0.99045 | -0.067054 | 6.2896
5 | -0.011329 | -0.0028396 | 0.011333 | 0.0028408 | 3.9508e-06 | 1.2356e-06 | 0.016981 | 0.016981 | 0.016981 | 0.99272 | -0.050976 | 0.99308 | -0.048458 | 6.2893
6 | -0.016783 | -0.004206 | 0.016789 | 0.0042081 | 6.1163e-06 | 2.1518e-06 | 0.025147 | 0.025147 | 0.025147 | 0.99308 | -0.048458 | 0.99346 | -0.045826 | 9.3139
7 | 0.0054503 | 0.0013652 | -0.0054473 | -0.0013649 | 3.0367e-06 | 2.2439e-07 | 0.0081664 | 0.0081667 | 0.0081667 | 0.99308 | -0.048458 | 0.99251 | -0.052487 | 3.0247
8 | 0.0028698 | 0.00071879 | -0.0028696 | -0.00071891 | 1.6823e-07 | -1.2142e-07 | 0.0043144 | 0.0043145 | 0.0043145 | 0.98974 | -0.072093 | 0.98968 | -0.072517 | 1.598
9 | 0.0017085 | 0.00042791 | -0.0017084 | -0.00042817 | 9.6178e-08 | -2.6314e-07 | 0.0025687 | 0.0025688 | 0.0025688 | 0.98968 | -0.072517 | 0.98962 | -0.072924 | 0.95143
10 | 0.031171 | 0.0078191 | -0.031154 | -0.0078129 | 1.6677e-05 | 6.2542e-06 | 0.046582 | 0.046582 | 0.046582 | 0.99577 | -0.029531 | 0.99522 | -0.033391 | 17.2528
11 | -0.034735 | -0.0087123 | 0.034778 | 0.0087288 | 4.3734e-05 | 1.6482e-05 | 0.051908 | 0.051908 | 0.051908 | 0.99577 | -0.029531 | 0.99707 | -0.020462 | 19.2251
12 | 0.026722 | 0.0067024 | -0.026714 | -0.0066995 | 7.7991e-06 | 2.898e-06 | 0.039955 | 0.039955 | 0.039955 | 0.99522 | -0.033391 | 0.99492 | -0.035497 | 14.7981
13 | 0.0044329 | 0.0011104 | -0.0044327 | -0.0011105 | 1.9565e-07 | -1.7498e-08 | 0.0066276 | 0.0066277 | 0.0066277 | 0.99522 | -0.033391 | 0.99518 | -0.03371 | 2.4547
14 | 0.022309 | 0.0056097 | -0.022185 | -0.0055643 | 0.00012407 | 4.5393e-05 | 0.033301 | 0.033302 | 0.033302 | 0.99707 | -0.020462 | 0.99135 | -0.060583 | 12.334
15 | -0.057088 | -0.014338 | 0.057251 | 0.014401 | 0.00016289 | 6.2179e-05 | 0.085209 | 0.085208 | 0.085209 | 0.99707 | -0.020462 | 1 | 0 | 31.5587
16 | 0.024248 | 0.0060815 | -0.024213 | -0.0060687 | 3.4676e-05 | 1.2789e-05 | 0.036266 | 0.036267 | 0.036267 | 0.99492 | -0.035497 | 0.99346 | -0.045826 | 13.4321
17 | 0.0011448 | 0.00028645 | -0.0011448 | -0.00028691 | 6.7518e-08 | -4.5383e-07 | 0.0017116 | 0.0017118 | 0.0017118 | 0.99518 | -0.03371 | 0.99512 | -0.034137 | 0.634
18 | 0.020413 | 0.0051201 | -0.020411 | -0.0051194 | 1.9856e-06 | 7.1998e-07 | 0.030641 | 0.030641 | 0.030641 | 0.99135 | -0.060583 | 0.99125 | -0.061284 | 11.3486
19 | 0.0021598 | 0.00054059 | -0.0021594 | -0.00054115 | 3.4465e-07 | -5.6897e-07 | 0.0032135 | 0.0032138 | 0.0032138 | 1 | 0 | 0.99984 | -0.0011544 | 1.1903
20 | 0.01958 | 0.0049116 | -0.019562 | -0.0049052 | 1.7822e-05 | 6.4289e-06 | 0.029394 | 0.029394 | 0.029394 | 0.99125 | -0.061284 | 0.99032 | -0.067853 | 10.8868
21 | 0.00083085 | 0.00020778 | -0.00083082 | -0.00020822 | 3.4128e-08 | -4.4012e-07 | 0.0012471 | 0.0012472 | 0.0012472 | 0.99125 | -0.061284 | 0.9912 | -0.061582 | 0.46194
22 | 0.00063672 | 0.00015953 | -0.00063672 | -0.00015958 | 1.922e-09 | -4.4247e-08 | 0.00094759 | 0.0009476 | 0.0009476 | 0.99984 | -0.0011544 | 0.99983 | -0.0011762 | 0.35096
23 | 0.01827 | 0.0045813 | -0.018243 | -0.0045717 | 2.7051e-05 | 9.6653e-06 | 0.027453 | 0.027453 | 0.027453 | 0.99032 | -0.067853 | 0.9888 | -0.078552 | 10.1678
24 | -0.0037714 | -0.0009452 | 0.0037718 | 0.0009451 | 3.8928e-07 | -1.0238e-07 | 0.0056548 | 0.0056547 | 0.0056548 | 0.99241 | -0.053233 | 0.99251 | -0.052487 | 2.0944
25 | 0.0016755 | 0.00041984 | -0.0016755 | -0.00041991 | 2.5802e-08 | -7.4763e-08 | 0.002512 | 0.002512 | 0.002512 | 0.99251 | -0.052487 | 0.9925 | -0.052599 | 0.93037
26 | -0.00046253 | -0.00011262 | 0.00046255 | 0.0001118 | 1.9429e-08 | -8.1988e-07 | 0.00069492 | 0.00069464 | 0.00069492 | 0.98876 | -0.078874 | 0.9888 | -0.078552 | 0.25738
27 | 0.00046253 | 0.00011262 | -0.00046247 | -0.00011531 | 6.3766e-08 | -2.6855e-06 | 0.00069492 | 0.00069587 | 0.00069587 | 0.98876 | -0.078874 | 0.98862 | -0.079904 | 0.25773
28 | 0.01778 | 0.0044599 | -0.01773 | -0.0044419 | 5.0392e-05 | 1.7939e-05 | 0.026759 | 0.026759 | 0.026759 | 0.9888 | -0.078552 | 0.98591 | -0.099044 | 9.9108
29 | 0.00046247 | 0.00011531 | -0.00046245 | -0.0001159 | 1.4108e-08 | -5.9305e-07 | 0.00069587 | 0.00069608 | 0.00069608 | 0.98862 | -0.079904 | 0.98859 | -0.080125 | 0.25781
30 | 0.011012 | 0.0027581 | -0.01101 | -0.0027578 | 1.1155e-06 | 3.4652e-07 | 0.016619 | 0.016619 | 0.016619 | 0.98591 | -0.099044 | 0.98581 | -0.099777 | 6.1552
31 | 0.004177 | 0.0010453 | -0.004173 | -0.0010459 | 3.9778e-06 | -5.1272e-07 | 0.0063044 | 0.0063051 | 0.0063051 | 0.98581 | -0.099777 | 0.98484 | -0.10667 | 2.3352
32 | 0.0068335 | 0.0017124 | -0.0068298 | -0.0017117 | 3.7118e-06 | 7.1519e-07 | 0.010315 | 0.010315 | 0.010315 | 0.98581 | -0.099777 | 0.98526 | -0.1037 | 3.8203

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.06106 | 0.015154

## res_load
| p_mw | q_mvar
0 | 0.0028861 | 0.00072332
1 | 0.0026909 | 0.00067441
2 | 0.002852 | 0.00071478
3 | 0.0011611 | 0.000291
4 | 0.0035637 | 0.00089315
5 | 0.0024662 | 0.00061808
6 | 0.0032878 | 0.00082401
7 | 0.0017724 | 0.00044422
8 | 0.0008499 | 0.00021301
9 | 0.0074236 | 0.0018605
10 | 0.0011448 | 0.00028691
11 | 0.0015227 | 0.00038162
12 | 0.0012921 | 0.00032384
13 | 0.00083082 | 0.00020822
14 | 0.00063672 | 0.00015958
15 | 0.0037714 | 0.0009452
16 | 0.0016755 | 0.00041991
17 | 0.0067185 | 0.0016838
18 | 0.004173 | 0.0010459
19 | 0.0068298 | 0.0017117
20 | 0.0017084 | 0.00042817
21 | 0.00046245 | 0.0001159

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1