## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1405-19_1_2_node_23 | 0.4 | n |  | TRUE
1 | bus_LV_1405-19_1_2_node_24 | 0.4 | n |  | TRUE
2 | bus_LV_1405-19_1_2_node_25 | 0.4 | n |  | TRUE
3 | bus_LV_1405-19_1_2_node_27 | 0.4 | n |  | TRUE
4 | bus_LV_1405-19_1_2_node_28 | 0.4 | n |  | TRUE
5 | bus_LV_1405-19_1_2_node_30 | 0.4 | n |  | TRUE
6 | bus_LV_1405-19_1_2_node_31 | 0.4 | n |  | TRUE
7 | bus_LV_1405-19_1_2_node_32 | 0.4 | n |  | TRUE
8 | bus_LV_1405-19_1_2_node_37 | 0.4 | n |  | TRUE
9 | bus_LV_1405-19_1_2_node_41 | 0.4 | n |  | TRUE
10 | bus_LV_1405-19_1_2_node_38 | 0.4 | n |  | TRUE
11 | bus_LV_1405-19_1_2_node_33 | 0.4 | n |  | TRUE
12 | bus_LV_1405-19_1_2_node_34 | 0.4 | n |  | TRUE
13 | bus_LV_1405-19_1_2_node_39 | 0.4 | n |  | TRUE
14 | bus_LV_1405-19_1_2_node_35 | 0.4 | n |  | TRUE
15 | bus_LV_1405-19_1_2_node_36 | 0.4 | n |  | TRUE
16 | bus_LV_1405-19_1_2_node_49 | 0.4 | n |  | TRUE
17 | bus_LV_1405-19_1_2_node_90 | 0.4 | n |  | TRUE
18 | bus_LV_1405-19_1_2_node_100 | 0.4 | n |  | TRUE
19 | bus_LV_1405-19_1_2_node_47 | 0.4 | n |  | TRUE
20 | bus_LV_1405-19_1_2_node_89 | 0.4 | n |  | TRUE
21 | bus_LV_1405-19_1_2_node_40 | 0.4 | n |  | TRUE
22 | bus_LV_1405-19_1_2_node_42 | 0.4 | n |  | TRUE
23 | bus_LV_1405-19_1_2_node_43 | 0.4 | n |  | TRUE
24 | bus_LV_1405-19_1_2_node_56 | 0.4 | n |  | TRUE
25 | bus_LV_1405-19_1_2_node_111 | 0.4 | n |  | TRUE
26 | bus_LV_1405-19_1_2_node_99 | 0.4 | n |  | TRUE
27 | bus_LV_1405-19_1_2_node_110 | 0.4 | n |  | TRUE
28 | bus_LV_1405-19_1_2_node_112 | 0.4 | n |  | TRUE
29 | bus_LV_1405-19_1_2_node_98 | 0.4 | n |  | TRUE
30 | bus_LV_1405-19_1_2_node_44 | 0.4 | n |  | TRUE
31 | bus_LV_1405-19_1_2_node_45 | 0.4 | n |  | TRUE
32 | bus_LV_1405-19_1_2_node_50 | 0.4 | n |  | TRUE
33 | bus_LV_1405-19_1_2_node_51 | 0.4 | n |  | TRUE
34 | bus_LV_1405-19_1_2_node_52 | 0.4 | n |  | TRUE
35 | bus_LV_1405-19_1_2_node_105 | 0.4 | n |  | TRUE
36 | bus_LV_1405-19_1_2_node_106 | 0.4 | n |  | TRUE
37 | bus_LV_1405-19_1_2_node_107 | 0.4 | n |  | TRUE
38 | bus_LV_1405-19_1_2_node_108 | 0.4 | n |  | TRUE
39 | bus_LV_1405-19_1_2_node_109 | 0.4 | n |  | TRUE
40 | bus_LV_1405-19_1_2_node_101 | 0.4 | n |  | TRUE
41 | bus_LV_1405-19_1_2_node_103 | 0.4 | n |  | TRUE
42 | bus_LV_1405-19_1_2_node_104 | 0.4 | n |  | TRUE
43 | bus_LV_1405-19_1_2_node_81 | 0.4 | n |  | TRUE
44 | bus_LV_1405-19_1_2_node_83 | 0.4 | n |  | TRUE
45 | bus_LV_1405-19_1_2_node_80 | 0.4 | n |  | TRUE
46 | bus_LV_1405-19_1_2_node_66 | 0.4 | n |  | TRUE
47 | bus_LV_1405-19_1_2_node_67 | 0.4 | n |  | TRUE
48 | bus_LV_1405-19_1_2_node_68 | 0.4 | n |  | TRUE
49 | bus_LV_1405-19_1_2_node_69 | 0.4 | n |  | TRUE
50 | bus_LV_1405-19_1_2_node_74 | 0.4 | n |  | TRUE
51 | bus_LV_1405-19_1_2_node_70 | 0.4 | n |  | TRUE
52 | bus_LV_1405-19_1_2_node_76 | 0.4 | n |  | TRUE
53 | bus_LV_1405-19_1_2_node_71 | 0.4 | n |  | TRUE
54 | bus_LV_1405-19_1_2_node_72 | 0.4 | n |  | TRUE
55 | bus_LV_1405-19_1_2_node_75 | 0.4 | n |  | TRUE
56 | bus_LV_1405-19_1_2_node_82 | 0.4 | n |  | TRUE
57 | bus_LV_1405-19_1_2_node_77 | 0.4 | n |  | TRUE
58 | bus_LV_1405-19_1_2_node_78 | 0.4 | n |  | TRUE
59 | bus_LV_1405-19_1_2_node_79 | 0.4 | n |  | TRUE
60 | bus_LV_1405-19_1_2_node_84 | 0.4 | n |  | TRUE
61 | bus_LV_1405-19_1_2_node_85 | 0.4 | n |  | TRUE
62 | bus_LV_1405-19_1_2_node_102 | 0.4 | n |  | TRUE
63 | bus_LV_1405-19_1_2_node_86 | 0.4 | n |  | TRUE
64 | bus_LV_1405-19_1_2_node_87 | 0.4 | n |  | TRUE
65 | bus_LV_1405-19_1_2_node_88 | 0.4 | n |  | TRUE
66 | bus_LV_1405-19_1_2_node_91 | 0.4 | n |  | TRUE
67 | bus_LV_1405-19_1_2_node_92 | 0.4 | n |  | TRUE
68 | bus_LV_1405-19_1_2_node_93 | 0.4 | n |  | TRUE
69 | bus_LV_1405-19_1_2_node_94 | 0.4 | n |  | TRUE
70 | bus_LV_1405-19_1_2_node_95 | 0.4 | n |  | TRUE
71 | bus_LV_1405-19_1_2_node_96 | 0.4 | n |  | TRUE
72 | bus_LV_1405-19_1_2_node_97 | 0.4 | n |  | TRUE
73 | bus_MV_138_2_node_243 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1405-19_1_2_load_23 | 0 | 0.0024438 | 0.00061248 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1405-19_1_2_load_24 | 1 | 0.0013442 | 0.00033688 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1405-19_1_2_load_27 | 3 | 0.0018136 | 0.00045454 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1405-19_1_2_load_30 | 5 | 0.0025775 | 0.00064597 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1405-19_1_2_load_31 | 6 | 0.0068803 | 0.0017244 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1405-19_1_2_load_41 | 9 | 0.0017579 | 0.00044058 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1405-19_1_2_load_33 | 11 | 0.0013282 | 0.00033289 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1405-19_1_2_load_34 | 12 | 0.00090639 | 0.00022716 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1405-19_1_2_load_39 | 13 | 0.0014856 | 0.00037232 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1405-19_1_2_load_35 | 14 | 0.0027836 | 0.00069765 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1405-19_1_2_load_90 | 17 | 0.0012142 | 0.00030432 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1405-19_1_2_load_100 | 18 | 0.00053037 | 0.00013292 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1405-19_1_2_load_47 | 19 | 0.00075552 | 0.00018935 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1405-19_1_2_load_89 | 20 | 0.0007295 | 0.00018283 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1405-19_1_2_load_42 | 22 | 0.0011114 | 0.00027855 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1405-19_1_2_load_43 | 23 | 0.001282 | 0.00032129 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1405-19_1_2_load_56 | 24 | 0.0022537 | 0.00056482 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1405-19_1_2_load_111 | 25 | 0.0016918 | 0.000424 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1405-19_1_2_load_99 | 26 | 0.0017901 | 0.00044865 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1405-19_1_2_load_110 | 27 | 0.0013925 | 0.00034899 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1405-19_1_2_load_112 | 28 | 0.0020533 | 0.0005146 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1405-19_1_2_load_98 | 29 | 0.001308 | 0.00032781 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1405-19_1_2_load_44 | 30 | 0.0016538 | 0.00041447 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1405-19_1_2_load_45 | 31 | 0.00079663 | 0.00019965 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1405-19_1_2_load_51 | 33 | 0.0005575 | 0.00013972 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1405-19_1_2_load_52 | 34 | 0.00099555 | 0.00024951 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1405-19_1_2_load_105 | 35 | 0.00048118 | 0.00012059 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1405-19_1_2_load_106 | 36 | 0.0010703 | 0.00026825 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1405-19_1_2_load_107 | 37 | 0.00039577 | 9.9189e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1405-19_1_2_load_108 | 38 | 0.0004772 | 0.0001196 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1405-19_1_2_load_109 | 39 | 0.0013844 | 0.00034697 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1405-19_1_2_load_101 | 40 | 0.0003838 | 9.6189e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1405-19_1_2_load_104 | 42 | 0.00061102 | 0.00015314 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1405-19_1_2_load_81 | 43 | 0.00069028 | 0.000173 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1405-19_1_2_load_80 | 45 | 0.0018982 | 0.00047573 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1405-19_1_2_load_66 | 46 | 0.00083713 | 0.0002098 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1405-19_1_2_load_67 | 47 | 0.00028142 | 7.053e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1405-19_1_2_load_70 | 51 | 0.00035338 | 8.8565e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1405-19_1_2_load_76 | 52 | 0.00050644 | 0.00012692 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1405-19_1_2_load_71 | 53 | 0.00052147 | 0.00013069 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1405-19_1_2_load_72 | 54 | 0.00045556 | 0.00011417 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1405-19_1_2_load_75 | 55 | 0.0040567 | 0.0010167 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1405-19_1_2_load_82 | 56 | 0.00069356 | 0.00017382 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1405-19_1_2_load_77 | 57 | 0.00052183 | 0.00013078 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1405-19_1_2_load_78 | 58 | 0.00044698 | 0.00011202 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1405-19_1_2_load_79 | 59 | 0.00044142 | 0.00011063 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1405-19_1_2_load_84 | 60 | 0.0010293 | 0.00025798 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1405-19_1_2_load_85 | 61 | 0.0006156 | 0.00015428 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1405-19_1_2_load_102 | 62 | 0.00095634 | 0.00023968 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1405-19_1_2_load_86 | 63 | 0.001199 | 0.00030051 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1405-19_1_2_load_87 | 64 | 0.00070415 | 0.00017648 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1405-19_1_2_load_88 | 65 | 0.0011048 | 0.00027689 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1405-19_1_2_load_91 | 66 | 0.0025122 | 0.00062961 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1405-19_1_2_load_92 | 67 | 0.0010035 | 0.0002515 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1405-19_1_2_load_93 | 68 | 0.0015953 | 0.00039981 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1405-19_1_2_load_94 | 69 | 0.001978 | 0.00049573 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1405-19_1_2_load_95 | 70 | 0.0015646 | 0.00039211 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1405-19_1_2_load_97 | 72 | 0.0045656 | 0.0011442 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 72 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1405-19_1_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.015331 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1405-19_1_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.027084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1405-19_1_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.04197 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
3 | LV_1405-19_1_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.009044 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
4 | LV_1405-19_1_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.038252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
5 | LV_1405-19_1_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.086416 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
6 | LV_1405-19_1_2_line_6 | NAYY 4x150 SE | 5 | 7 | 0.18488 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
7 | LV_1405-19_1_2_line_7 | NAYY 4x150 SE | 6 | 8 | 0.019304 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_1405-19_1_2_line_8 | NAYY 4x150 SE | 7 | 11 | 0.02849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1405-19_1_2_line_9 | NAYY 4x150 SE | 7 | 12 | 0.033298 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
10 | LV_1405-19_1_2_line_10 | NAYY 4x150 SE | 8 | 10 | 0.004424 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1405-19_1_2_line_11 | NAYY 4x150 SE | 8 | 13 | 0.045874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
12 | LV_1405-19_1_2_line_12 | NAYY 4x150 SE | 9 | 10 | 0.0096563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1405-19_1_2_line_13 | NAYY 4x150 SE | 10 | 21 | 0.35015 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1405-19_1_2_line_14 | NAYY 4x150 SE | 10 | 22 | 0.013647 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1405-19_1_2_line_15 | NAYY 4x150 SE | 11 | 14 | 0.011407 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1405-19_1_2_line_16 | NAYY 4x150 SE | 12 | 15 | 0.042166 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
17 | LV_1405-19_1_2_line_17 | NAYY 4x150 SE | 13 | 23 | 0.080552 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
18 | LV_1405-19_1_2_line_18 | NAYY 4x150 SE | 15 | 16 | 0.011262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
19 | LV_1405-19_1_2_line_19 | NAYY 4x150 SE | 15 | 17 | 0.016774 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1405-19_1_2_line_20 | NAYY 4x150 SE | 16 | 18 | 0.022428 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
21 | LV_1405-19_1_2_line_21 | NAYY 4x150 SE | 16 | 19 | 0.0068649 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1405-19_1_2_line_22 | NAYY 4x150 SE | 17 | 20 | 0.023144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1405-19_1_2_line_23 | NAYY 4x150 SE | 18 | 40 | 0.014733 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
24 | LV_1405-19_1_2_line_24 | NAYY 4x150 SE | 20 | 64 | 0.0048104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1405-19_1_2_line_25 | NAYY 4x150 SE | 21 | 24 | 0.28077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1405-19_1_2_line_26 | NAYY 4x150 SE | 21 | 25 | 0.60767 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1405-19_1_2_line_27 | NAYY 4x150 SE | 23 | 26 | 0.0040258 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
28 | LV_1405-19_1_2_line_28 | NAYY 4x150 SE | 24 | 27 | 0.066287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1405-19_1_2_line_29 | NAYY 4x150 SE | 25 | 28 | 0.0017444 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1405-19_1_2_line_30 | NAYY 4x150 SE | 26 | 29 | 0.031858 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
31 | LV_1405-19_1_2_line_31 | NAYY 4x150 SE | 29 | 71 | 0.027688 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
32 | LV_1405-19_1_2_line_32 | NAYY 4x150 SE | 30 | 31 | 0.1369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
33 | LV_1405-19_1_2_line_33 | NAYY 4x150 SE | 31 | 32 | 0.17273 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
34 | LV_1405-19_1_2_line_34 | NAYY 4x150 SE | 32 | 33 | 0.0032868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
35 | LV_1405-19_1_2_line_35 | NAYY 4x150 SE | 32 | 34 | 0.11518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
36 | LV_1405-19_1_2_line_36 | NAYY 4x150 SE | 33 | 35 | 0.021885 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
37 | LV_1405-19_1_2_line_37 | NAYY 4x150 SE | 34 | 41 | 0.15775 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1405-19_1_2_line_38 | NAYY 4x150 SE | 35 | 36 | 0.03048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
39 | LV_1405-19_1_2_line_39 | NAYY 4x150 SE | 36 | 37 | 0.013255 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
40 | LV_1405-19_1_2_line_40 | NAYY 4x150 SE | 37 | 38 | 0.009017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
41 | LV_1405-19_1_2_line_41 | NAYY 4x150 SE | 38 | 39 | 0.013819 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
42 | LV_1405-19_1_2_line_42 | NAYY 4x150 SE | 39 | 43 | 0.14903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
43 | LV_1405-19_1_2_line_43 | NAYY 4x150 SE | 40 | 62 | 0.003309 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
44 | LV_1405-19_1_2_line_44 | NAYY 4x150 SE | 41 | 42 | 0.092012 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1405-19_1_2_line_45 | NAYY 4x150 SE | 43 | 44 | 0.097311 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
46 | LV_1405-19_1_2_line_46 | NAYY 4x150 SE | 43 | 45 | 0.053053 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1405-19_1_2_line_47 | NAYY 4x150 SE | 44 | 60 | 0.022164 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
48 | LV_1405-19_1_2_line_48 | NAYY 4x150 SE | 44 | 56 | 0.056492 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
49 | LV_1405-19_1_2_line_49 | NAYY 4x150 SE | 45 | 59 | 0.078588 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1405-19_1_2_line_50 | NAYY 4x150 SE | 46 | 47 | 0.023545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1405-19_1_2_line_51 | NAYY 4x150 SE | 46 | 48 | 0.093864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1405-19_1_2_line_52 | NAYY 4x150 SE | 48 | 49 | 0.12228 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1405-19_1_2_line_53 | NAYY 4x150 SE | 49 | 50 | 0.29625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1405-19_1_2_line_54 | NAYY 4x150 SE | 49 | 51 | 0.17109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1405-19_1_2_line_55 | NAYY 4x150 SE | 50 | 52 | 0.20519 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1405-19_1_2_line_56 | NAYY 4x150 SE | 51 | 53 | 0.33412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
57 | LV_1405-19_1_2_line_57 | NAYY 4x150 SE | 53 | 54 | 0.11951 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
58 | LV_1405-19_1_2_line_58 | NAYY 4x150 SE | 54 | 55 | 0.20167 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
59 | LV_1405-19_1_2_line_59 | NAYY 4x150 SE | 55 | 56 | 0.039344 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
60 | LV_1405-19_1_2_line_60 | NAYY 4x150 SE | 57 | 58 | 0.0084843 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1405-19_1_2_line_61 | NAYY 4x150 SE | 57 | 59 | 0.13219 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1405-19_1_2_line_62 | NAYY 4x150 SE | 60 | 61 | 0.050046 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
63 | LV_1405-19_1_2_line_63 | NAYY 4x150 SE | 61 | 62 | 0.0053946 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
64 | LV_1405-19_1_2_line_64 | NAYY 4x150 SE | 63 | 64 | 0.077563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1405-19_1_2_line_65 | NAYY 4x150 SE | 63 | 65 | 0.013325 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1405-19_1_2_line_66 | NAYY 4x150 SE | 66 | 67 | 0.024394 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
67 | LV_1405-19_1_2_line_67 | NAYY 4x150 SE | 66 | 68 | 0.016423 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
68 | LV_1405-19_1_2_line_68 | NAYY 4x150 SE | 67 | 69 | 0.011917 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
69 | LV_1405-19_1_2_line_69 | NAYY 4x150 SE | 68 | 70 | 0.01158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
70 | LV_1405-19_1_2_line_70 | NAYY 4x150 SE | 69 | 71 | 0.0099172 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
71 | LV_1405-19_1_2_line_71 | NAYY 4x150 SE | 70 | 72 | 0.013706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1405-19_1_2_trafo_97 | 0.25 MVA 20/0.4 kV | 73 | 72 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37 | x38 | y38 | x39 | y39
0 | 2655404.9939 | 1182703.905 | 2655408.8418 | 1182689.0643
1 | 2655397.3689 | 1182729.8279 | 2655399.4495 | 1182725.289 | 2655404.9939 | 1182703.905
2 | 2655397.3689 | 1182729.8279 | 2655397.7612 | 1182731.9883 | 2655395.3263 | 1182745.1286 | 2655395.0033 | 1182755.2979 | 2655400.2479 | 1182766.1191 | 2655402.8378 | 1182769.4387
3 | 2655389.1678 | 1182726.6059 | 2655396.1297 | 1182728.4268 | 2655397.3689 | 1182729.8279
4 | 2655402.8378 | 1182769.4387 | 2655411.876 | 1182781.0237 | 2655425.4866 | 1182793.7343 | 2655429.4728 | 1182796.6451
5 | 2655389.1678 | 1182726.6059 | 2655388.1211 | 1182734.1226 | 2655387.5785 | 1182741.6107 | 2655387.1364 | 1182772.1013 | 2655388.0863 | 1182812.9154
6 | 2655483.5091 | 1182963.3428 | 2655482.7518 | 1182961.0234 | 2655477.5236 | 1182944.3435 | 2655474.7983 | 1182934.4017 | 2655474.5637 | 1182925.9282 | 2655475.817 | 1182917.5462 | 2655474.9675 | 1182912.8135 | 2655472.9261 | 1182908.1809 | 2655469.5747 | 1182899.8898 | 2655468.5525 | 1182894.0104 | 2655468.3011 | 1182858.4772 | 2655466.1978 | 1182846.4955 | 2655464.0421 | 1182835.2249 | 2655462.6069 | 1182828.608 | 2655459.584 | 1182822.7545 | 2655455.1853 | 1182815.4209 | 2655429.4728 | 1182796.6451
7 | 2655388.5355 | 1182832.2142 | 2655388.0863 | 1182812.9154
8 | 2655483.5091 | 1182963.3428 | 2655482.3297 | 1182991.8083
9 | 2655483.5091 | 1182963.3428 | 2655491.0669 | 1182987.3483 | 2655494.4996 | 1182993.4501 | 2655495.2194 | 1182994.3208
10 | 2655384.1269 | 1182831.7177 | 2655388.5355 | 1182832.2142
11 | 2655388.5355 | 1182832.2142 | 2655389.4968 | 1182878.0785
12 | 2655384.1269 | 1182831.7177 | 2655383.8845 | 1182822.0644
13 | 2655174.9544 | 1183008.3876 | 2655177.3505 | 1183004.3852 | 2655184.1392 | 1182996.7768 | 2655188.8376 | 1182993.974 | 2655197.5292 | 1182991.9862 | 2655202.0946 | 1182990.3607 | 2655209.3014 | 1182985.4576 | 2655216.7385 | 1182981.2349 | 2655224.9523 | 1182978.0754 | 2655233.5576 | 1182975.5088 | 2655241.6925 | 1182974.2831 | 2655249.8758 | 1182973.6136 | 2655257.6677 | 1182973.9745 | 2655265.4677 | 1182975.1248 | 2655297.4168 | 1182982.9237 | 2655307.2636 | 1182984.8155 | 2655313.9235 | 1182985.4106 | 2655321.8112 | 1182985.3167 | 2655329.6512 | 1182984.6108 | 2655343.1005 | 1182981.6778 | 2655353.3088 | 1182977.503 | 2655362.1156 | 1182972.9707 | 2655370.2696 | 1182966.3756 | 2655375.6098 | 1182960.2326 | 2655380.1473 | 1182953.3707 | 2655384.4444 | 1182941.1258 | 2655385.492 | 1182933.5202 | 2655385.9575 | 1182924.4528 | 2655384.1269 | 1182831.7177
14 | 2655384.1269 | 1182831.7177 | 2655370.4829 | 1182832.0165
15 | 2655481.8574 | 1183003.2052 | 2655482.3297 | 1182991.8083
16 | 2655504.7298 | 1183032.2664 | 2655507.1331 | 1183019.2592 | 2655507.3649 | 1183012.3575 | 2655505.4476 | 1183006.6921 | 2655495.2194 | 1182994.3208
17 | 2655383.1167 | 1182957.3658 | 2655384.3885 | 1182955.4444 | 2655389.015 | 1182942.2576 | 2655390.1604 | 1182933.9746 | 2655390.4696 | 1182924.4833 | 2655389.4968 | 1182878.0785
18 | 2655511.9511 | 1183040.649 | 2655508.5292 | 1183035.0364 | 2655504.7298 | 1183032.2664
19 | 2655504.7298 | 1183032.2664 | 2655500.0562 | 1183043.0958 | 2655497.2759 | 1183047.2265
20 | 2655511.9511 | 1183040.649 | 2655512.1951 | 1183043.9753 | 2655510.5784 | 1183049.5412 | 2655509.9657 | 1183054.694 | 2655512.1122 | 1183058.6938 | 2655514.0971 | 1183061.6591
21 | 2655511.9511 | 1183040.649 | 2655512.5801 | 1183037.8533 | 2655513.6969 | 1183034.0131
22 | 2655484.3527 | 1183066.4263 | 2655497.2759 | 1183047.2265
23 | 2655514.0971 | 1183061.6591 | 2655514.7555 | 1183062.6427 | 2655517.3594 | 1183068.37 | 2655518.4664 | 1183074.139 | 2655518.456 | 1183075.523
24 | 2655484.3527 | 1183066.4263 | 2655481.6667 | 1183070.4169
25 | 2655174.9544 | 1183008.3876 | 2655171.9924 | 1183013.3297 | 2655168.17 | 1183022.1661 | 2655165.7929 | 1183029.0815 | 2655164.0947 | 1183037.7373 | 2655163.8197 | 1183046.0394 | 2655164.5642 | 1183052.2497 | 2655167.1709 | 1183057.71 | 2655173.4464 | 1183065.2164 | 2655178.17 | 1183072.1081 | 2655186.802 | 1183089.8418 | 2655195.0247 | 1183107.2494 | 2655207.7729 | 1183133.1478 | 2655214.4453 | 1183146.45 | 2655219.647 | 1183156.1254 | 2655226.2435 | 1183166.0584 | 2655234.6349 | 1183175.0851 | 2655244.7408 | 1183188.5968 | 2655254.2064 | 1183202.8253 | 2655275.4707 | 1183239.8863 | 2655284.2437 | 1183253.0899
26 | 2655174.9544 | 1183008.3876 | 2654568.1147 | 1182976.6646
27 | 2655380.8947 | 1182960.7229 | 2655383.1167 | 1182957.3658
28 | 2655324.1194 | 1183305.9605 | 2655309.3644 | 1183288.3035 | 2655295.5158 | 1183270.0545 | 2655284.2437 | 1183253.0899
29 | 2654567.8858 | 1182978.3939 | 2654568.1147 | 1182976.6646
30 | 2655356.8279 | 1182980.9105 | 2655364.7676 | 1182976.8195 | 2655373.5908 | 1182969.6859 | 2655379.3787 | 1182963.0134 | 2655380.8947 | 1182960.7229
31 | 2655330.518 | 1182989.1325 | 2655344.6176 | 1182986.0609 | 2655355.3777 | 1182981.6577 | 2655356.8279 | 1182980.9105
32 | 2655543.2924 | 1182856.9149 | 2655543.2924 | 1182856.9149 | 2655543.6037 | 1182846.3897 | 2655547.3607 | 1182826.5691 | 2655552.1996 | 1182802.8674 | 2655553.4754 | 1182778.0765 | 2655555.3856 | 1182729.3338 | 2655556.8481 | 1182721.0626
33 | 2655543.2924 | 1182856.9149 | 2655693.1116 | 1182942.8744
34 | 2655693.1116 | 1182942.8744 | 2655692.7327 | 1182946.1393
35 | 2655693.1116 | 1182942.8744 | 2655698.5844 | 1182953.7202 | 2655705.6419 | 1182962.4572 | 2655721.6499 | 1182977.5143 | 2655723.4595 | 1182982.4339 | 2655722.1005 | 1183011.9932 | 2655720.8337 | 1183025.0665 | 2655722.265 | 1183028.793 | 2655727.2168 | 1183033.2415 | 2655736.0162 | 1183040.1903
36 | 2655691.5501 | 1182967.968 | 2655691.8086 | 1182954.1019 | 2655692.7327 | 1182946.1393
37 | 2655862.0124 | 1183127.2813 | 2655852.4249 | 1183123.0007 | 2655826.2863 | 1183115.3086 | 2655817.8247 | 1183111.4499 | 2655782.4439 | 1183091.0649 | 2655772.6208 | 1183083.3693 | 2655767.2984 | 1183076.0824 | 2655758.691 | 1183060.805 | 2655753.2438 | 1183053.7949 | 2655736.0162 | 1183040.1903
38 | 2655687.7731 | 1182998.1111 | 2655689.0689 | 1182992.5867 | 2655691.3519 | 1182978.6002 | 2655691.5501 | 1182967.968
39 | 2655687.7731 | 1182998.1111 | 2655687.7731 | 1182998.1111 | 2655685.3681 | 1183000.5679 | 2655675.7234 | 1183002.4016
40 | 2655667.6391 | 1183006.3954 | 2655675.7234 | 1183002.4016
41 | 2655664.1192 | 1183019.5701 | 2655664.5162 | 1183013.815 | 2655667.6391 | 1183006.3954
42 | 2655575.3473 | 1183139.2709 | 2655664.1192 | 1183019.5701
43 | 2655518.456 | 1183075.523 | 2655518.4334 | 1183078.5301 | 2655518.3826 | 1183078.8276
44 | 2655862.0124 | 1183127.2813 | 2655862.4466 | 1183124.9285 | 2655859.3976 | 1183121.9429 | 2655835.4994 | 1183104.8775 | 2655830.8328 | 1183100.1425 | 2655824.1935 | 1183087.5292 | 2655819.7061 | 1183074.2134 | 2655817.7675 | 1183062.6667 | 2655817.5496 | 1183053.2706
45 | 2655481.8502 | 1183144.1946 | 2655486.0455 | 1183147.0795 | 2655492.1029 | 1183148.3918 | 2655501.2733 | 1183146.6313 | 2655525.6699 | 1183137.1852 | 2655533.1187 | 1183135.8312 | 2655552.6614 | 1183134.4226 | 2655563.3622 | 1183135.589 | 2655573.5755 | 1183138.274 | 2655575.3473 | 1183139.2709
46 | 2655593.1047 | 1183187.7385 | 2655591.6738 | 1183185.5903 | 2655589.68 | 1183179.9576 | 2655586.7229 | 1183160.4638 | 2655583.4624 | 1183149.8165 | 2655579.4101 | 1183142.2192 | 2655576.6895 | 1183140.0261 | 2655575.3473 | 1183139.2709
47 | 2655481.8502 | 1183144.1946 | 2655482.0077 | 1183142.0171 | 2655483.3332 | 1183131.6236 | 2655486.4967 | 1183122.6629
48 | 2655481.8502 | 1183144.1946 | 2655481.1037 | 1183149.7797 | 2655481.3848 | 1183173.0174 | 2655480.1994 | 1183183.957 | 2655477.9838 | 1183194.8537 | 2655478.4953 | 1183200.3249
49 | 2655629.1559 | 1183233.4231 | 2655613.1582 | 1183229.1582 | 2655596.5908 | 1183225.069 | 2655591.8433 | 1183221.6453 | 2655589.1557 | 1183218.3741 | 2655588.5603 | 1183214.2441 | 2655590.0195 | 1183209.1992 | 2655595.8362 | 1183201.8935 | 2655598.006 | 1183198.4339 | 2655597.3739 | 1183194.1479 | 2655593.1047 | 1183187.7385
50 | 2656036.9225 | 1183807.1577 | 2656036.8309 | 1183806.0461 | 2656035.1497 | 1183797.2477 | 2656030.4021 | 1183787.3756 | 2656028.5612 | 1183785.6588
51 | 2655972.4557 | 1183865.5335 | 2655980.7763 | 1183866.3783 | 2655986.3441 | 1183865.2741 | 2655991.583 | 1183862.5993 | 2656012.8777 | 1183841.7644 | 2656033.3016 | 1183820.1876 | 2656037.5234 | 1183814.4461 | 2656036.9225 | 1183807.1577
52 | 2655911.3501 | 1183762.0835 | 2655915.8837 | 1183785.1053 | 2655918.435 | 1183791.477 | 2655935.8228 | 1183819.5326 | 2655952.8462 | 1183838.3575 | 2655969.076 | 1183862.0333 | 2655972.4557 | 1183865.5335
53 | 2655818.9602 | 1183706.7474 | 2655815.8909 | 1183718.2586 | 2655805.4074 | 1183761.1071 | 2655795.2905 | 1183799.0229 | 2655804.3712 | 1183787.9346 | 2655812.7064 | 1183762.6425 | 2655817.6747 | 1183745.5793 | 2655820.0313 | 1183745.012 | 2655823.8894 | 1183743.8806 | 2655827.5542 | 1183743.8258 | 2655830.4251 | 1183745.409 | 2655837.51 | 1183762.5512 | 2655842.9543 | 1183774.7087 | 2655847.6354 | 1183781.9118 | 2655852.1594 | 1183786.3231 | 2655858.7108 | 1183789.4414 | 2655868.0667 | 1183792.2524 | 2655875.439 | 1183772.0098 | 2655878.2163 | 1183764.7983 | 2655880.6566 | 1183760.9745 | 2655883.0677 | 1183759.4739 | 2655887.1879 | 1183759.7013 | 2655899.5998 | 1183760.6287 | 2655911.3501 | 1183762.0835
54 | 2655911.3501 | 1183762.0835 | 2655904.8018 | 1183733.273 | 2655904.5077 | 1183726.3331 | 2655905.6016 | 1183719.5506 | 2655909.5755 | 1183710.9162 | 2655912.9653 | 1183706.79 | 2655917.4616 | 1183703.5412 | 2655925.8744 | 1183696.9827 | 2655926.0253 | 1183695.5388 | 2655925.1343 | 1183692.8512 | 2655921.596 | 1183683.4352 | 2655921.1296 | 1183681.0629 | 2655921.9483 | 1183677.5908 | 2655922.1244 | 1183673.4457 | 2655922.009 | 1183667.8081 | 2655922.2311 | 1183662.8297 | 2655923.7328 | 1183651.6152 | 2655927.6319 | 1183642.0018 | 2655936.3252 | 1183624.2174 | 2655944.2462 | 1183605.7588
55 | 2655818.9602 | 1183706.7474 | 2655826.3949 | 1183681.4358 | 2655833.0717 | 1183662.0872 | 2655841.2556 | 1183637.4942 | 2655849.3798 | 1183616.8584 | 2655862.3795 | 1183587.5076 | 2655875.5772 | 1183560.6823 | 2655898.044 | 1183517.985
56 | 2655944.2462 | 1183605.7588 | 2655944.2462 | 1183605.7588 | 2655940.4913 | 1183593.3724 | 2655936.9271 | 1183585.0901 | 2655931.277 | 1183582.725 | 2655919.3666 | 1183577.1108 | 2655909.1657 | 1183569.0889 | 2655887.8841 | 1183558.1734 | 2655873.3553 | 1183551.7121 | 2655868.052 | 1183546.5376 | 2655865.8999 | 1183539.0801 | 2655862.0445 | 1183534.9974 | 2655850.7184 | 1183525.6534 | 2655839.8916 | 1183520.8832 | 2655831.5109 | 1183519.8824 | 2655822.3814 | 1183518.9413 | 2655820.1812 | 1183516.6529 | 2655819.8882 | 1183513.6819 | 2655818.1724 | 1183511.8315 | 2655811.8687 | 1183506.6811 | 2655809.1023 | 1183504.5208 | 2655805.7116 | 1183502.1768 | 2655796.3768 | 1183499.4996 | 2655793.5633 | 1183488.4673 | 2655790.7316 | 1183484.2941 | 2655787.0109 | 1183481.3134 | 2655776.5743 | 1183477.2585 | 2655772.374 | 1183474.9515 | 2655765.7303 | 1183469.4088 | 2655761.1836 | 1183468.2215 | 2655757.5601 | 1183467.9209 | 2655747.5835 | 1183464.4818 | 2655742.0714 | 1183464.4861 | 2655735.7447 | 1183464.2605 | 2655728.9853 | 1183463.7641 | 2655718.4162 | 1183459.9971 | 2655710.0875 | 1183454.2054 | 2655707.1284 | 1183443.2051 | 2655705.1211 | 1183430.0013 | 2655706.658 | 1183418.5756
57 | 2655706.658 | 1183418.5756 | 2655706.9746 | 1183416.222 | 2655711.3792 | 1183404.7676 | 2655687.6623 | 1183401.1342 | 2655671.8193 | 1183398.0187 | 2655658.7651 | 1183392.1831 | 2655647.1802 | 1183382.6926 | 2655637.92 | 1183376.0696 | 2655630.7808 | 1183373.7132 | 2655622.9809 | 1183370.9726 | 2655615.6026 | 1183367.2243 | 2655615.6026 | 1183367.2243
58 | 2655615.6026 | 1183367.2243 | 2655608.4586 | 1183362.9112 | 2655602.0019 | 1183356.9258 | 2655596.3396 | 1183350.9033 | 2655590.9664 | 1183344.9835 | 2655586.9862 | 1183341.9672 | 2655582.7576 | 1183339.4043 | 2655564.2841 | 1183329.3053 | 2655556.1066 | 1183325.2939 | 2655547.7773 | 1183322.0038 | 2655540.2233 | 1183318.254 | 2655534.656 | 1183314.3225 | 2655531.2911 | 1183311.6454 | 2655525.896 | 1183307.2485 | 2655519.6965 | 1183303.1555 | 2655510.4022 | 1183299.3673 | 2655501.2264 | 1183295.9694 | 2655495.0139 | 1183292.4544 | 2655489.838 | 1183286.6366 | 2655485.3628 | 1183280.1916 | 2655481.0211 | 1183271.6912 | 2655478.3986 | 1183263.8514 | 2655476.9013 | 1183253.2317 | 2655478.5481 | 1183239.1934
59 | 2655478.5481 | 1183239.1934 | 2655480.3743 | 1183223.6251 | 2655481.4086 | 1183214.1628 | 2655478.609 | 1183201.541 | 2655478.4953 | 1183200.3249
60 | 2655749.0887 | 1183278.2729 | 2655752.7517 | 1183279.8605 | 2655756.5807 | 1183282.2094
61 | 2655749.0887 | 1183278.2729 | 2655742.0302 | 1183275.2138 | 2655730.7339 | 1183272.4405 | 2655719.4087 | 1183271.1346 | 2655709.2096 | 1183271.8736 | 2655697.349 | 1183272.3081 | 2655691.0231 | 1183271.1487 | 2655683.7277 | 1183267.5122 | 2655666.2207 | 1183253.6308 | 2655649.5997 | 1183242.1702 | 2655631.002 | 1183233.9153 | 2655629.1559 | 1183233.4231
62 | 2655516.9228 | 1183084.0016 | 2655516.0934 | 1183086.3461 | 2655509.0816 | 1183093.2739 | 2655493.89 | 1183107.9303 | 2655489.0096 | 1183115.5449 | 2655486.4967 | 1183122.6629
63 | 2655516.9228 | 1183084.0016 | 2655518.0378 | 1183080.8499 | 2655518.3826 | 1183078.8276
64 | 2655433.0849 | 1183130.6662 | 2655449.9011 | 1183113.4042 | 2655475.5007 | 1183079.5777 | 2655481.6667 | 1183070.4169
65 | 2655423.7866 | 1183140.211 | 2655433.0849 | 1183130.6662
66 | 2655340.5501 | 1183033.754 | 2655337.6016 | 1183029.8315 | 2655334.0262 | 1183010.6757
67 | 2655340.5501 | 1183033.754 | 2655341.2369 | 1183034.6678 | 2655346.4323 | 1183036.7502 | 2655352.1367 | 1183036.6361 | 2655355.9893 | 1183035.6484
68 | 2655334.0262 | 1183010.6757 | 2655331.8397 | 1182998.9612 | 2655331.8397 | 1182998.9612
69 | 2655355.9893 | 1183035.6484 | 2655363.731 | 1183033.6637 | 2655366.9627 | 1183032.1043
70 | 2655330.518 | 1182989.1325 | 2655331.8397 | 1182998.9612
71 | 2655379.3069 | 1183026.1478 | 2655366.9627 | 1183032.1043

## bus_geodata
| x | y | coords
0 | 2655404.9939 | 1182703.905
1 | 2655408.8418 | 1182689.0643
2 | 2655397.3689 | 1182729.8279
3 | 2655402.8378 | 1182769.4387
4 | 2655389.1679 | 1182726.6059
5 | 2655429.4728 | 1182796.6451
6 | 2655388.0863 | 1182812.9154
7 | 2655483.5091 | 1182963.3428
8 | 2655388.5355 | 1182832.2142
9 | 2655383.8845 | 1182822.0644
10 | 2655384.1269 | 1182831.7177
11 | 2655482.3297 | 1182991.8083
12 | 2655495.2194 | 1182994.3208
13 | 2655389.4968 | 1182878.0785
14 | 2655481.8574 | 1183003.2052
15 | 2655504.7298 | 1183032.2664
16 | 2655511.9511 | 1183040.649
17 | 2655497.2759 | 1183047.2265
18 | 2655514.0971 | 1183061.6591
19 | 2655513.6969 | 1183034.0131
20 | 2655484.3527 | 1183066.4263
21 | 2655174.9544 | 1183008.3876
22 | 2655370.4829 | 1182832.0165
23 | 2655383.1167 | 1182957.3658
24 | 2655284.2437 | 1183253.0899
25 | 2654568.1147 | 1182976.6646
26 | 2655380.8947 | 1182960.7229
27 | 2655324.1194 | 1183305.9605
28 | 2654567.8858 | 1182978.3939
29 | 2655356.8279 | 1182980.9105
30 | 2655556.8481 | 1182721.0626
31 | 2655543.2924 | 1182856.9149
32 | 2655693.1116 | 1182942.8744
33 | 2655692.7327 | 1182946.1393
34 | 2655736.0162 | 1183040.1903
35 | 2655691.5501 | 1182967.968
36 | 2655687.7731 | 1182998.1111
37 | 2655675.7234 | 1183002.4016
38 | 2655667.6391 | 1183006.3954
39 | 2655664.1192 | 1183019.5701
40 | 2655518.456 | 1183075.523
41 | 2655862.0124 | 1183127.2813
42 | 2655817.5496 | 1183053.2706
43 | 2655575.3473 | 1183139.2709
44 | 2655481.8502 | 1183144.1946
45 | 2655593.1047 | 1183187.7385
46 | 2656036.9225 | 1183807.1577
47 | 2656028.5612 | 1183785.6588
48 | 2655972.4557 | 1183865.5335
49 | 2655911.3501 | 1183762.0835
50 | 2655818.9602 | 1183706.7474
51 | 2655944.2462 | 1183605.7588
52 | 2655898.044 | 1183517.985
53 | 2655706.658 | 1183418.5756
54 | 2655615.6026 | 1183367.2243
55 | 2655478.5481 | 1183239.1934
56 | 2655478.4953 | 1183200.3249
57 | 2655749.0887 | 1183278.2729
58 | 2655756.5807 | 1183282.2094
59 | 2655629.1559 | 1183233.4231
60 | 2655486.4967 | 1183122.6629
61 | 2655516.9228 | 1183084.0016
62 | 2655518.3826 | 1183078.8276
63 | 2655433.0849 | 1183130.6662
64 | 2655481.6667 | 1183070.4169
65 | 2655423.7866 | 1183140.211
66 | 2655340.5501 | 1183033.754
67 | 2655334.0262 | 1183010.6757
68 | 2655355.9893 | 1183035.6484
69 | 2655331.8397 | 1182998.9612
70 | 2655366.9627 | 1183032.1043
71 | 2655330.518 | 1182989.1325
72 | 2655379.3069 | 1183026.1478
73 | 2655330.518 | 1182989.1325

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98313 | -0.11881 | 0.0024438 | 0.00061248
1 | 0.9831 | -0.11902 | 0.0013442 | 0.00033688
2 | 0.98328 | -0.11775 | 0 | 0
3 | 0.98209 | -0.12626 | 0.0018136 | 0.00045454
4 | 0.98356 | -0.11574 | 0 | 0
5 | 0.98105 | -0.13368 | 0.0025775 | 0.00064597
6 | 0.98625 | -0.096585 | 0.0068803 | 0.0017244
7 | 0.9764 | -0.16725 | 0 | 0
8 | 0.98694 | -0.091639 | 0 | 0
9 | 0.98685 | -0.092284 | 0.0017579 | 0.00044058
10 | 0.98688 | -0.09211 | 0 | 0
11 | 0.97623 | -0.16848 | 0.0013282 | 0.00033289
12 | 0.97566 | -0.17261 | 0.00090639 | 0.00022716
13 | 0.98894 | -0.077482 | 0.0014856 | 0.00037232
14 | 0.97618 | -0.16881 | 0.0027836 | 0.00069765
15 | 0.97475 | -0.1792 | 0 | 0
16 | 0.97455 | -0.18067 | 0 | 0
17 | 0.97463 | -0.18008 | 0.0012142 | 0.00030432
18 | 0.97416 | -0.18351 | 0.00053037 | 0.00013292
19 | 0.97455 | -0.18073 | 0.00075552 | 0.00018935
20 | 0.97451 | -0.18099 | 0.0007295 | 0.00018283
21 | 0.98312 | -0.11912 | 0 | 0
22 | 0.98685 | -0.092266 | 0.0011114 | 0.00027855
23 | 0.99253 | -0.052149 | 0.001282 | 0.00032129
24 | 0.98163 | -0.12976 | 0.0022537 | 0.00056482
25 | 0.97981 | -0.14288 | 0.0016918 | 0.000424
26 | 0.99271 | -0.050862 | 0.0017901 | 0.00044865
27 | 0.9815 | -0.13072 | 0.0013925 | 0.00034899
28 | 0.9798 | -0.14291 | 0.0020533 | 0.0005146
29 | 0.9942 | -0.040401 | 0.001308 | 0.00032781
30 | 0.97001 | -0.21391 | 0.0016538 | 0.00041447
31 | 0.97018 | -0.2127 | 0.00079663 | 0.00019965
32 | 0.97049 | -0.21042 | 0 | 0
33 | 0.9705 | -0.21034 | 0.0005575 | 0.00013972
34 | 0.97035 | -0.21142 | 0.00099555 | 0.00024951
35 | 0.97057 | -0.2098 | 0.00048118 | 0.00012059
36 | 0.97069 | -0.20896 | 0.0010703 | 0.00026825
37 | 0.97075 | -0.20852 | 0.00039577 | 9.9189e-05
38 | 0.97079 | -0.2082 | 0.0004772 | 0.0001196
39 | 0.97086 | -0.20767 | 0.0013844 | 0.00034697
40 | 0.97391 | -0.18533 | 0.0003838 | 9.6189e-05
41 | 0.97021 | -0.21247 | 0 | 0
42 | 0.97013 | -0.21307 | 0.00061102 | 0.00015314
43 | 0.97178 | -0.20093 | 0.00069028 | 0.000173
44 | 0.97267 | -0.19446 | 0 | 0
45 | 0.97153 | -0.2028 | 0.0018982 | 0.00047573
46 | 0.97025 | -0.21272 | 0.00083713 | 0.0002098
47 | 0.97024 | -0.21279 | 0.00028142 | 7.053e-05
48 | 0.9704 | -0.2116 | 0 | 0
49 | 0.9706 | -0.21013 | 0 | 0
50 | 0.97038 | -0.21182 | 0 | 0
51 | 0.97101 | -0.20704 | 0.00035338 | 8.8565e-05
52 | 0.97023 | -0.21294 | 0.00050644 | 0.00012692
53 | 0.97149 | -0.20334 | 0.00052147 | 0.00013069
54 | 0.97171 | -0.20166 | 0.00045556 | 0.00011417
55 | 0.97215 | -0.19832 | 0.0040567 | 0.0010167
56 | 0.97235 | -0.19682 | 0.00069356 | 0.00017382
57 | 0.97118 | -0.20535 | 0.00052183 | 0.00013078
58 | 0.97117 | -0.20539 | 0.00044698 | 0.00011202
59 | 0.97136 | -0.20398 | 0.00044142 | 0.00011063
60 | 0.973 | -0.19206 | 0.0010293 | 0.00025798
61 | 0.97377 | -0.18637 | 0.0006156 | 0.00015428
62 | 0.97386 | -0.18574 | 0.00095634 | 0.00023968
63 | 0.97422 | -0.18302 | 0.001199 | 0.00030051
64 | 0.97449 | -0.18114 | 0.00070415 | 0.00017648
65 | 0.9742 | -0.18318 | 0.0011048 | 0.00027689
66 | 0.9978 | -0.015279 | 0.0025122 | 0.00062961
67 | 0.99658 | -0.023756 | 0.0010035 | 0.0002515
68 | 0.99865 | -0.0093769 | 0.0015953 | 0.00039981
69 | 0.996 | -0.027844 | 0.001978 | 0.00049573
70 | 0.99926 | -0.0051286 | 0.0015646 | 0.00039211
71 | 0.99553 | -0.031152 | 0 | 0
72 | 1 | 0 | -0.076424 | -0.019046
73 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0013442 | 0.0003367 | -0.0013442 | -0.00033688 | 3.9599e-08 | -1.7917e-07 | 0.0020345 | 0.0020345 | 0.0020345 | 0.98313 | -0.11881 | 0.9831 | -0.11902 | 0.75354
1 | -0.0037881 | -0.00094919 | 0.0037886 | 0.00094906 | 5.5553e-07 | -1.2982e-07 | 0.0057333 | 0.0057332 | 0.0057333 | 0.98313 | -0.11881 | 0.98328 | -0.11775 | 2.1235
2 | 0.039132 | 0.0097879 | -0.039086 | -0.0097714 | 4.5911e-05 | 1.6595e-05 | 0.059212 | 0.059213 | 0.059213 | 0.98328 | -0.11775 | 0.98209 | -0.12626 | 10.9653
3 | -0.04292 | -0.010737 | 0.042932 | 0.010741 | 1.1902e-05 | 4.3481e-06 | 0.064945 | 0.064945 | 0.064945 | 0.98328 | -0.11775 | 0.98356 | -0.11574 | 12.0269
4 | 0.037272 | 0.0093168 | -0.037234 | -0.0093031 | 3.8051e-05 | 1.3668e-05 | 0.056465 | 0.056465 | 0.056465 | 0.98209 | -0.12626 | 0.98105 | -0.13368 | 10.4565
5 | -0.042932 | -0.010741 | 0.043046 | 0.010783 | 0.00011372 | 4.1539e-05 | 0.064945 | 0.064945 | 0.064945 | 0.98356 | -0.11574 | 0.98625 | -0.096585 | 12.0269
6 | 0.034657 | 0.0086572 | -0.034497 | -0.0086005 | 0.00015933 | 5.6635e-05 | 0.052556 | 0.052557 | 0.052557 | 0.98105 | -0.13368 | 0.9764 | -0.16725 | 9.7328
7 | -0.049926 | -0.012507 | 0.049961 | 0.01252 | 3.4173e-05 | 1.265e-05 | 0.075325 | 0.075325 | 0.075325 | 0.98625 | -0.096585 | 0.98694 | -0.091639 | 13.9491
8 | 0.0041127 | 0.0010304 | -0.004112 | -0.0010304 | 6.9836e-07 | -8.7669e-08 | 0.0062676 | 0.0062677 | 0.0062677 | 0.9764 | -0.16725 | 0.97623 | -0.16848 | 2.3214
9 | 0.030385 | 0.0075702 | -0.030362 | -0.0075625 | 2.2261e-05 | 7.7296e-06 | 0.04629 | 0.04629 | 0.04629 | 0.9764 | -0.16725 | 0.97566 | -0.17261 | 8.5722
10 | 0.010307 | 0.0025723 | -0.010306 | -0.0025721 | 6.6626e-07 | 1.9972e-07 | 0.015535 | 0.015535 | 0.015535 | 0.98694 | -0.091639 | 0.98688 | -0.09211 | 5.7539
11 | -0.060267 | -0.015092 | 0.060385 | 0.015136 | 0.00011816 | 4.4272e-05 | 0.090861 | 0.09086 | 0.090861 | 0.98694 | -0.091639 | 0.98894 | -0.077482 | 16.826
12 | -0.0017579 | -0.00044058 | 0.001758 | 0.00044047 | 4.2336e-08 | -1.0709e-07 | 0.0026507 | 0.0026506 | 0.0026507 | 0.98685 | -0.092284 | 0.98688 | -0.09211 | 0.98174
13 | 0.0074364 | 0.0018533 | -0.007409 | -0.0018472 | 2.7456e-05 | 6.103e-06 | 0.011209 | 0.011211 | 0.011211 | 0.98688 | -0.09211 | 0.98312 | -0.11912 | 4.152
14 | 0.0011115 | 0.00027839 | -0.0011114 | -0.00027855 | 2.3916e-08 | -1.6517e-07 | 0.0016758 | 0.0016759 | 0.0016759 | 0.98688 | -0.09211 | 0.98685 | -0.092266 | 0.62069
15 | 0.0027838 | 0.00069755 | -0.0027836 | -0.00069765 | 1.2815e-07 | -9.3322e-08 | 0.0042431 | 0.0042432 | 0.0042432 | 0.97623 | -0.16848 | 0.97618 | -0.16881 | 1.5715
16 | 0.029456 | 0.0073353 | -0.02943 | -0.0073261 | 2.6531e-05 | 9.1522e-06 | 0.044908 | 0.044908 | 0.044908 | 0.97566 | -0.17261 | 0.97475 | -0.1792 | 8.3163
17 | -0.061871 | -0.015509 | 0.062089 | 0.015591 | 0.00021781 | 8.17e-05 | 0.093095 | 0.093095 | 0.093095 | 0.98894 | -0.077482 | 0.99253 | -0.052149 | 17.2399
18 | 0.024476 | 0.0060861 | -0.024471 | -0.0060845 | 4.9009e-06 | 1.6043e-06 | 0.037347 | 0.037347 | 0.037347 | 0.97475 | -0.1792 | 0.97455 | -0.18067 | 6.9161
19 | 0.0049535 | 0.00124 | -0.0049529 | -0.00124 | 5.9843e-07 | 2.1099e-08 | 0.0075613 | 0.0075613 | 0.0075613 | 0.97475 | -0.1792 | 0.97463 | -0.18008 | 2.8005
20 | 0.023716 | 0.0058953 | -0.023706 | -0.0058923 | 9.1665e-06 | 2.9669e-06 | 0.036193 | 0.036193 | 0.036193 | 0.97455 | -0.18067 | 0.97416 | -0.18351 | 6.7025
21 | 0.00075552 | 0.00018927 | -0.00075552 | -0.00018935 | 5.7005e-09 | -8.3344e-08 | 0.0011536 | 0.0011536 | 0.0011536 | 0.97455 | -0.18067 | 0.97455 | -0.18073 | 0.42725
22 | 0.0037387 | 0.00093567 | -0.0037382 | -0.00093578 | 4.7046e-07 | -1.0744e-07 | 0.0057075 | 0.0057076 | 0.0057076 | 0.97463 | -0.18008 | 0.97451 | -0.18099 | 2.1139
23 | 0.023176 | 0.0057594 | -0.02317 | -0.0057575 | 5.7551e-06 | 1.8467e-06 | 0.035383 | 0.035383 | 0.035383 | 0.97416 | -0.18351 | 0.97391 | -0.18533 | 6.5525
24 | 0.0030087 | 0.00075295 | -0.0030086 | -0.00075298 | 6.3342e-08 | -3.5568e-08 | 0.0045937 | 0.0045937 | 0.0045937 | 0.97451 | -0.18099 | 0.97449 | -0.18114 | 1.7014
25 | 0.0036517 | 0.00091154 | -0.0036463 | -0.00091304 | 5.3508e-06 | -1.4968e-06 | 0.0055257 | 0.005527 | 0.005527 | 0.98312 | -0.11912 | 0.98163 | -0.12976 | 2.047
26 | 0.0037573 | 0.00093561 | -0.003745 | -0.00093858 | 1.226e-05 | -2.964e-06 | 0.0056848 | 0.0056875 | 0.0056875 | 0.98312 | -0.11912 | 0.97981 | -0.14288 | 2.1065
27 | -0.063371 | -0.015912 | 0.063382 | 0.015916 | 1.134e-05 | 4.2574e-06 | 0.095017 | 0.095017 | 0.095017 | 0.99253 | -0.052149 | 0.99271 | -0.050862 | 17.5957
28 | 0.0013927 | 0.00034822 | -0.0013925 | -0.00034899 | 1.8432e-07 | -7.6698e-07 | 0.0021108 | 0.0021111 | 0.0021111 | 0.98163 | -0.12976 | 0.9815 | -0.13072 | 0.78188
29 | 0.0020533 | 0.00051458 | -0.0020533 | -0.0005146 | 1.0584e-08 | -1.79e-08 | 0.0031183 | 0.0031183 | 0.0031183 | 0.97981 | -0.14288 | 0.9798 | -0.14291 | 1.1549
30 | -0.065172 | -0.016365 | 0.065267 | 0.0164 | 9.4876e-05 | 3.5666e-05 | 0.0977 | 0.0977 | 0.0977 | 0.99271 | -0.050862 | 0.9942 | -0.040401 | 18.0926
31 | -0.066575 | -0.016728 | 0.066661 | 0.01676 | 8.5795e-05 | 3.2279e-05 | 0.099657 | 0.099657 | 0.099657 | 0.9942 | -0.040401 | 0.99553 | -0.031152 | 18.455
32 | -0.0016538 | -0.00041447 | 0.001654 | 0.0004112 | 2.7476e-07 | -3.2747e-06 | 0.0025369 | 0.0025357 | 0.0025369 | 0.97001 | -0.21391 | 0.97018 | -0.2127 | 0.4698
33 | -0.0024507 | -0.00061085 | 0.0024514 | 0.00060688 | 7.6058e-07 | -3.9747e-06 | 0.0037575 | 0.003756 | 0.0037575 | 0.97018 | -0.2127 | 0.97049 | -0.21042 | 0.69584
34 | -0.0040584 | -0.0010037 | 0.0040584 | 0.0010037 | 3.9644e-08 | -6.5978e-08 | 0.0062177 | 0.0062177 | 0.0062177 | 0.97049 | -0.21042 | 0.9705 | -0.21034 | 1.1514
35 | 0.0016069 | 0.00039685 | -0.0016067 | -0.00039961 | 2.1787e-07 | -2.7623e-06 | 0.0024617 | 0.0024627 | 0.0024627 | 0.97049 | -0.21042 | 0.97035 | -0.21142 | 0.45606
36 | -0.0046159 | -0.0011434 | 0.0046162 | 0.001143 | 3.4153e-07 | -4.0953e-07 | 0.0070725 | 0.0070723 | 0.0070725 | 0.9705 | -0.21034 | 0.97057 | -0.2098 | 1.3097
37 | 0.00061116 | 0.0001501 | -0.00061107 | -0.00015202 | 8.632e-08 | -1.9152e-06 | 0.0009361 | 0.0009368 | 0.0009368 | 0.97035 | -0.21142 | 0.97021 | -0.21247 | 0.34696
38 | -0.0050974 | -0.0012636 | 0.005098 | 0.001263 | 5.8004e-07 | -5.3037e-07 | 0.00781 | 0.0078097 | 0.00781 | 0.97057 | -0.2098 | 0.97069 | -0.20896 | 1.4463
39 | -0.0061683 | -0.0015313 | 0.0061687 | 0.0015311 | 3.6936e-07 | -1.8567e-07 | 0.0094505 | 0.0094504 | 0.0094505 | 0.97069 | -0.20896 | 0.97075 | -0.20852 | 1.7501
40 | -0.0065645 | -0.0016303 | 0.0065648 | 0.0016302 | 2.8455e-07 | -1.1352e-07 | 0.010057 | 0.010057 | 0.010057 | 0.97075 | -0.20852 | 0.97079 | -0.2082 | 1.8624
41 | -0.007042 | -0.0017498 | 0.0070425 | 0.0017496 | 5.018e-07 | -1.4874e-07 | 0.010788 | 0.010788 | 0.010788 | 0.97079 | -0.2082 | 0.97086 | -0.20767 | 1.9979
42 | -0.0084269 | -0.0020966 | 0.0084347 | 0.0020959 | 7.7488e-06 | -7.0886e-07 | 0.01291 | 0.012909 | 0.01291 | 0.97086 | -0.20767 | 0.97178 | -0.20093 | 2.3908
43 | 0.022787 | 0.0056613 | -0.022785 | -0.0056609 | 1.2501e-06 | 3.9845e-07 | 0.034797 | 0.034797 | 0.034797 | 0.97391 | -0.18533 | 0.97386 | -0.18574 | 6.4439
44 | 0.00061107 | 0.00015202 | -0.00061102 | -0.00015314 | 5.0409e-08 | -1.1168e-06 | 0.0009368 | 0.00093721 | 0.00093721 | 0.97021 | -0.21247 | 0.97013 | -0.21307 | 0.34711
45 | -0.012435 | -0.0030952 | 0.012446 | 0.003097 | 1.0997e-05 | 1.8163e-06 | 0.019033 | 0.019032 | 0.019033 | 0.97178 | -0.20093 | 0.97267 | -0.19446 | 3.5245
46 | 0.0033097 | 0.00082628 | -0.0033088 | -0.00082661 | 8.4991e-07 | -3.3024e-07 | 0.0050667 | 0.005067 | 0.005067 | 0.97178 | -0.20093 | 0.97153 | -0.2028 | 1.8766
47 | -0.020159 | -0.0050014 | 0.020166 | 0.0050033 | 6.5691e-06 | 1.9762e-06 | 0.030822 | 0.030822 | 0.030822 | 0.97267 | -0.19446 | 0.973 | -0.19206 | 5.7077
48 | 0.0077135 | 0.0019044 | -0.0077111 | -0.0019048 | 2.4502e-06 | -4.5954e-07 | 0.01179 | 0.011791 | 0.011791 | 0.97267 | -0.19446 | 0.97235 | -0.19682 | 2.1834
49 | 0.0014106 | 0.00035088 | -0.0014104 | -0.00035177 | 2.2875e-07 | -8.8499e-07 | 0.0021596 | 0.00216 | 0.00216 | 0.97153 | -0.2028 | 0.97136 | -0.20398 | 0.79999
50 | 0.00028142 | 7.024e-05 | -0.00028142 | -7.053e-05 | 2.7361e-09 | -2.8973e-07 | 0.00043149 | 0.0004316 | 0.0004316 | 0.97025 | -0.21272 | 0.97024 | -0.21279 | 0.15985
51 | -0.0011186 | -0.00028004 | 0.0011187 | 0.00027895 | 1.723e-07 | -1.0932e-06 | 0.0017154 | 0.0017149 | 0.0017154 | 0.97025 | -0.21272 | 0.9704 | -0.2116 | 0.63532
52 | -0.0011187 | -0.00027895 | 0.0011189 | 0.00027753 | 2.2435e-07 | -1.4248e-06 | 0.0017149 | 0.0017144 | 0.0017149 | 0.9704 | -0.2116 | 0.9706 | -0.21013 | 0.63516
53 | 0.00050662 | 0.0001208 | -0.00050651 | -0.00012442 | 1.1108e-07 | -3.6179e-06 | 0.00077452 | 0.0007758 | 0.0007758 | 0.9706 | -0.21013 | 0.97038 | -0.21182 | 0.28733
54 | -0.0016256 | -0.00039833 | 0.0016262 | 0.00039647 | 6.6114e-07 | -1.8611e-06 | 0.0024889 | 0.0024881 | 0.0024889 | 0.9706 | -0.21013 | 0.97101 | -0.20704 | 0.92181
55 | 0.00050651 | 0.00012442 | -0.00050644 | -0.00012692 | 7.7152e-08 | -2.5048e-06 | 0.0007758 | 0.00077671 | 0.00077671 | 0.97038 | -0.21182 | 0.97023 | -0.21294 | 0.28767
56 | -0.0019796 | -0.00048503 | 0.0019806 | 0.00047713 | 9.5594e-07 | -7.9023e-06 | 0.0030297 | 0.0030268 | 0.0030297 | 0.97101 | -0.20704 | 0.97149 | -0.20334 | 0.56105
57 | -0.002502 | -0.00060782 | 0.0025026 | 0.00060507 | 5.4551e-07 | -2.7504e-06 | 0.0038255 | 0.0038244 | 0.0038255 | 0.97149 | -0.20334 | 0.97171 | -0.20166 | 0.70842
58 | -0.0029581 | -0.00071925 | 0.0029594 | 0.00071474 | 1.2861e-06 | -4.5039e-06 | 0.004522 | 0.0045203 | 0.004522 | 0.97171 | -0.20166 | 0.97215 | -0.19832 | 0.83741
59 | -0.0070161 | -0.0017314 | 0.0070175 | 0.001731 | 1.4131e-06 | -4.3232e-07 | 0.01073 | 0.010729 | 0.01073 | 0.97215 | -0.19832 | 0.97235 | -0.19682 | 1.9869
60 | 0.00044698 | 0.00011192 | -0.00044698 | -0.00011202 | 2.483e-09 | -1.0403e-07 | 0.00068481 | 0.00068485 | 0.00068485 | 0.97118 | -0.20535 | 0.97117 | -0.20539 | 0.25365
61 | -0.00096881 | -0.0002427 | 0.00096899 | 0.00024114 | 1.8167e-07 | -1.5662e-06 | 0.0014844 | 0.0014838 | 0.0014844 | 0.97118 | -0.20535 | 0.97136 | -0.20398 | 0.54976
62 | -0.021195 | -0.0052613 | 0.021211 | 0.0052664 | 1.6387e-05 | 5.0584e-06 | 0.032396 | 0.032395 | 0.032396 | 0.973 | -0.19206 | 0.97377 | -0.18637 | 5.9992
63 | -0.021827 | -0.0054207 | 0.021829 | 0.0054213 | 1.8704e-06 | 5.8516e-07 | 0.033336 | 0.033336 | 0.033336 | 0.97377 | -0.18637 | 0.97386 | -0.18574 | 6.1733
64 | -0.0023039 | -0.00057724 | 0.0023045 | 0.00057651 | 5.9924e-07 | -7.3557e-07 | 0.0035189 | 0.0035185 | 0.0035189 | 0.97422 | -0.18302 | 0.97449 | -0.18114 | 1.3033
65 | 0.0011048 | 0.00027674 | -0.0011048 | -0.00027689 | 2.3678e-08 | -1.5681e-07 | 0.0016875 | 0.0016875 | 0.0016875 | 0.97422 | -0.18302 | 0.9742 | -0.18318 | 0.62501
66 | 0.069795 | 0.017565 | -0.069712 | -0.017534 | 8.2493e-05 | 3.1092e-05 | 0.10411 | 0.10411 | 0.10411 | 0.9978 | -0.015279 | 0.99658 | -0.023756 | 19.2797
67 | -0.072307 | -0.018195 | 0.072366 | 0.018217 | 5.9607e-05 | 2.2496e-05 | 0.10786 | 0.10786 | 0.10786 | 0.9978 | -0.015279 | 0.99865 | -0.0093769 | 19.9734
68 | 0.068709 | 0.017283 | -0.068669 | -0.017268 | 3.9148e-05 | 1.4746e-05 | 0.10261 | 0.10261 | 0.10261 | 0.99658 | -0.023756 | 0.996 | -0.027844 | 19.0022
69 | -0.073962 | -0.018617 | 0.074005 | 0.018634 | 4.3903e-05 | 1.6583e-05 | 0.11023 | 0.11023 | 0.11023 | 0.99865 | -0.0093769 | 0.99926 | -0.0051286 | 20.4136
70 | 0.066691 | 0.016772 | -0.066661 | -0.01676 | 3.073e-05 | 1.1561e-05 | 0.099657 | 0.099657 | 0.099657 | 0.996 | -0.027844 | 0.99553 | -0.031152 | 18.455
71 | -0.07557 | -0.019026 | 0.075624 | 0.019046 | 5.4183e-05 | 2.048e-05 | 0.11256 | 0.11256 | 0.11256 | 0.99926 | -0.0051286 | 1 | 0 | 20.845

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.08099 | 0.020191

## res_load
| p_mw | q_mvar
0 | 0.0024438 | 0.00061248
1 | 0.0013442 | 0.00033688
2 | 0.0018136 | 0.00045454
3 | 0.0025775 | 0.00064597
4 | 0.0068803 | 0.0017244
5 | 0.0017579 | 0.00044058
6 | 0.0013282 | 0.00033289
7 | 0.00090639 | 0.00022716
8 | 0.0014856 | 0.00037232
9 | 0.0027836 | 0.00069765
10 | 0.0012142 | 0.00030432
11 | 0.00053037 | 0.00013292
12 | 0.00075552 | 0.00018935
13 | 0.0007295 | 0.00018283
14 | 0.0011114 | 0.00027855
15 | 0.001282 | 0.00032129
16 | 0.0022537 | 0.00056482
17 | 0.0016918 | 0.000424
18 | 0.0017901 | 0.00044865
19 | 0.0013925 | 0.00034899
20 | 0.0020533 | 0.0005146
21 | 0.001308 | 0.00032781
22 | 0.0016538 | 0.00041447
23 | 0.00079663 | 0.00019965
24 | 0.0005575 | 0.00013972
25 | 0.00099555 | 0.00024951
26 | 0.00048118 | 0.00012059
27 | 0.0010703 | 0.00026825
28 | 0.00039577 | 9.9189e-05
29 | 0.0004772 | 0.0001196
30 | 0.0013844 | 0.00034697
31 | 0.0003838 | 9.6189e-05
32 | 0.00061102 | 0.00015314
33 | 0.00069028 | 0.000173
34 | 0.0018982 | 0.00047573
35 | 0.00083713 | 0.0002098
36 | 0.00028142 | 7.053e-05
37 | 0.00035338 | 8.8565e-05
38 | 0.00050644 | 0.00012692
39 | 0.00052147 | 0.00013069
40 | 0.00045556 | 0.00011417
41 | 0.0040567 | 0.0010167
42 | 0.00069356 | 0.00017382
43 | 0.00052183 | 0.00013078
44 | 0.00044698 | 0.00011202
45 | 0.00044142 | 0.00011063
46 | 0.0010293 | 0.00025798
47 | 0.0006156 | 0.00015428
48 | 0.00095634 | 0.00023968
49 | 0.001199 | 0.00030051
50 | 0.00070415 | 0.00017648
51 | 0.0011048 | 0.00027689
52 | 0.0025122 | 0.00062961
53 | 0.0010035 | 0.0002515
54 | 0.0015953 | 0.00039981
55 | 0.001978 | 0.00049573
56 | 0.0015646 | 0.00039211
57 | 0.0045656 | 0.0011442

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1