## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1405-1_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1405-1_0_4_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_1405-1_0_4_node_4 | 0.4 | n |  | TRUE
3 | bus_LV_1405-1_0_4_node_39 | 0.4 | n |  | TRUE
4 | bus_LV_1405-1_0_4_node_29 | 0.4 | n |  | TRUE
5 | bus_LV_1405-1_0_4_node_38 | 0.4 | n |  | TRUE
6 | bus_LV_1405-1_0_4_node_28 | 0.4 | n |  | TRUE
7 | bus_LV_1405-1_0_4_node_27 | 0.4 | n |  | TRUE
8 | bus_LV_1405-1_0_4_node_16 | 0.4 | n |  | TRUE
9 | bus_LV_1405-1_0_4_node_35 | 0.4 | n |  | TRUE
10 | bus_LV_1405-1_0_4_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_1405-1_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1405-1_0_4_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_1405-1_0_4_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_1405-1_0_4_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_1405-1_0_4_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_1405-1_0_4_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_1405-1_0_4_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_1405-1_0_4_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_1405-1_0_4_node_18 | 0.4 | n |  | TRUE
20 | bus_LV_1405-1_0_4_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_1405-1_0_4_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_1405-1_0_4_node_21 | 0.4 | n |  | TRUE
23 | bus_LV_1405-1_0_4_node_22 | 0.4 | n |  | TRUE
24 | bus_LV_1405-1_0_4_node_23 | 0.4 | n |  | TRUE
25 | bus_LV_1405-1_0_4_node_24 | 0.4 | n |  | TRUE
26 | bus_LV_1405-1_0_4_node_26 | 0.4 | n |  | TRUE
27 | bus_LV_1405-1_0_4_node_37 | 0.4 | n |  | TRUE
28 | bus_LV_1405-1_0_4_node_40 | 0.4 | n |  | TRUE
29 | bus_LV_1405-1_0_4_node_30 | 0.4 | n |  | TRUE
30 | bus_LV_1405-1_0_4_node_34 | 0.4 | n |  | TRUE
31 | bus_LV_1405-1_0_4_node_32 | 0.4 | n |  | TRUE
32 | bus_LV_1405-1_0_4_node_31 | 0.4 | n |  | TRUE
33 | bus_LV_1405-1_0_4_node_33 | 0.4 | n |  | TRUE
34 | bus_LV_1405-1_0_4_node_36 | 0.4 | n |  | TRUE
35 | bus_MV_138_2_node_77 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1405-1_0_4_load_0 | 0 | 0.0046235 | 0.0011588 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1405-1_0_4_load_38 | 5 | 0.0028207 | 0.00070694 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1405-1_0_4_load_28 | 6 | 0.0077371 | 0.0019391 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1405-1_0_4_load_27 | 7 | 0.002229 | 0.00055863 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1405-1_0_4_load_16 | 8 | 0.00028159 | 7.0573e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1405-1_0_4_load_35 | 9 | 0.018 | 0.0045111 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1405-1_0_4_load_5 | 10 | 0.028605 | 0.007169 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1405-1_0_4_load_9 | 12 | 0.0476 | 0.01193 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1405-1_0_4_load_10 | 13 | 0.00082752 | 0.0002074 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1405-1_0_4_load_8 | 14 | 0.00046157 | 0.00011568 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1405-1_0_4_load_12 | 16 | 0.032658 | 0.0081849 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1405-1_0_4_load_11 | 18 | 0.0049314 | 0.0012359 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1405-1_0_4_load_18 | 19 | 0.019042 | 0.0047723 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1405-1_0_4_load_19 | 20 | 0.023385 | 0.0058609 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1405-1_0_4_load_20 | 21 | 0.0019505 | 0.00048883 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1405-1_0_4_load_21 | 22 | 0.0016688 | 0.00041825 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1405-1_0_4_load_24 | 25 | 0.0017568 | 0.00044031 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1405-1_0_4_load_26 | 26 | 0.0013168 | 0.00033003 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1405-1_0_4_load_40 | 28 | 0.001868 | 0.00046817 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1405-1_0_4_load_34 | 30 | 0.014377 | 0.0036033 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1405-1_0_4_load_32 | 31 | 0.0018278 | 0.00045809 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1405-1_0_4_load_31 | 32 | 0.002059 | 0.00051602 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1405-1_0_4_load_36 | 34 | 0.0032125 | 0.00080512 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 13 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1405-1_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.039945 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1405-1_0_4_line_1 | NAYY 4x150 SE | 1 | 2 | 0.082857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1405-1_0_4_line_2 | NAYY 4x150 SE | 2 | 3 | 0.12017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
3 | LV_1405-1_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.062925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1405-1_0_4_line_4 | NAYY 4x150 SE | 2 | 5 | 0.047275 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
5 | LV_1405-1_0_4_line_5 | NAYY 4x150 SE | 3 | 8 | 0.072763 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
6 | LV_1405-1_0_4_line_6 | NAYY 4x150 SE | 4 | 7 | 0.010062 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1405-1_0_4_line_7 | NAYY 4x150 SE | 5 | 9 | 0.048957 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1405-1_0_4_line_8 | NAYY 4x150 SE | 6 | 7 | 0.031216 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1405-1_0_4_line_9 | NAYY 4x150 SE | 8 | 15 | 0.072983 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
10 | LV_1405-1_0_4_line_10 | NAYY 4x150 SE | 9 | 33 | 0.017378 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1405-1_0_4_line_11 | NAYY 4x150 SE | 10 | 11 | 0.02201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1405-1_0_4_line_12 | NAYY 4x150 SE | 11 | 12 | 0.057141 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1405-1_0_4_line_13 | NAYY 4x150 SE | 11 | 13 | 0.02856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
14 | LV_1405-1_0_4_line_14 | NAYY 4x150 SE | 12 | 16 | 0.078491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1405-1_0_4_line_15 | NAYY 4x150 SE | 13 | 17 | 0.00028752 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
16 | LV_1405-1_0_4_line_16 | NAYY 4x150 SE | 14 | 15 | 0.036724 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1405-1_0_4_line_17 | NAYY 4x150 SE | 15 | 17 | 0.036104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
18 | LV_1405-1_0_4_line_18 | NAYY 4x150 SE | 16 | 18 | 0.014978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1405-1_0_4_line_19 | NAYY 4x150 SE | 17 | 19 | 0.12402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1405-1_0_4_line_20 | NAYY 4x150 SE | 19 | 20 | 0.040188 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1405-1_0_4_line_21 | NAYY 4x150 SE | 21 | 22 | 0.017177 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1405-1_0_4_line_22 | NAYY 4x150 SE | 21 | 23 | 0.032179 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1405-1_0_4_line_23 | NAYY 4x150 SE | 22 | 24 | 0.021951 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1405-1_0_4_line_24 | NAYY 4x150 SE | 23 | 25 | 0.013442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1405-1_0_4_line_25 | NAYY 4x150 SE | 24 | 26 | 0.10383 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1405-1_0_4_line_26 | NAYY 4x150 SE | 26 | 27 | 0.04043 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1405-1_0_4_line_27 | NAYY 4x150 SE | 27 | 28 | 0.017172 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1405-1_0_4_line_28 | NAYY 4x150 SE | 27 | 29 | 0.059593 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1405-1_0_4_line_29 | NAYY 4x150 SE | 29 | 30 | 0.035178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1405-1_0_4_line_30 | NAYY 4x150 SE | 30 | 31 | 0.023958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1405-1_0_4_line_31 | NAYY 4x150 SE | 31 | 32 | 0.066974 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1405-1_0_4_line_32 | NAYY 4x150 SE | 32 | 33 | 0.056158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1405-1_0_4_line_33 | NAYY 4x150 SE | 33 | 34 | 0.025477 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1405-1_0_4_trafo_10 | 0.25 MVA 20/0.4 kV | 35 | 13 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2655011.0826 | 1181524.4599 | 2655019.6782 | 1181523.1714 | 2655015.4995 | 1181492.1984
1 | 2655024.4829 | 1181602.0925 | 2655006.0704 | 1181533.052 | 2655009.9741 | 1181531.2424 | 2655011.4416 | 1181527.7873 | 2655011.0826 | 1181524.4599
2 | 2654951.9369 | 1181533.4783 | 2654994.678 | 1181587.8112 | 2655008.6206 | 1181608.0058 | 2655012.1717 | 1181611.3291 | 2655016.551 | 1181611.7917 | 2655014.7429 | 1181604.938 | 2655024.4829 | 1181602.0925
3 | 2655070.6193 | 1181559.3589 | 2655054.5509 | 1181576.8878 | 2655024.4829 | 1181602.0925
4 | 2655024.4829 | 1181602.0925 | 2655071.3965 | 1181607.9268
5 | 2654951.9369 | 1181533.4783 | 2654907.8615 | 1181475.4982
6 | 2655070.6193 | 1181559.3589 | 2655071.8652 | 1181549.3743
7 | 2655071.3965 | 1181607.9268 | 2655119.9794 | 1181613.9687
8 | 2655071.8652 | 1181549.3743 | 2655074.1971 | 1181530.687 | 2655073.0926 | 1181526.2188 | 2655070.839 | 1181522.1403 | 2655068.8183 | 1181519.7614
9 | 2654863.657 | 1181417.3393 | 2654907.8615 | 1181475.4982
10 | 2655137.2244 | 1181616.1133 | 2655119.9794 | 1181613.9687
11 | 2654850.0853 | 1181353.9913 | 2654835.223 | 1181363.2494 | 2654831.6786 | 1181366.0227
12 | 2654850.0853 | 1181353.9913 | 2654839.3191 | 1181317.8729 | 2654829.6641 | 1181300.9858
13 | 2654850.0853 | 1181353.9913 | 2654858.2426 | 1181381.3619
14 | 2654784.4324 | 1181237.2617 | 2654786.2183 | 1181240.1892 | 2654812.2208 | 1181270.4768 | 2654829.6641 | 1181300.9858
15 | 2654858.3247 | 1181381.6375 | 2654858.2426 | 1181381.3619
16 | 2654863.657 | 1181417.3393 | 2654852.698 | 1181409.8238 | 2654840.269 | 1181404.385 | 2654830.9892 | 1181402.8104 | 2654830.5389 | 1181402.7341
17 | 2654858.3247 | 1181381.6375 | 2654863.657 | 1181417.3393
18 | 2654776.6322 | 1181224.4752 | 2654784.4324 | 1181237.2617
19 | 2654858.3247 | 1181381.6375 | 2654861.2314 | 1181371.9476 | 2654848.5187 | 1181283.1489 | 2654845.917 | 1181260.3236 | 2654845.6305 | 1181259.1353
20 | 2654835.2646 | 1181220.3337 | 2654839.2066 | 1181232.4914 | 2654845.6305 | 1181259.1353
21 | 2655168.3482 | 1181268.3151 | 2655168.9009 | 1181262.6423 | 2655169.2197 | 1181260.3662 | 2655171.3752 | 1181258.5072 | 2655177.5221 | 1181256.9833
22 | 2655200.2435 | 1181270.1348 | 2655193.4545 | 1181256.8205 | 2655190.918 | 1181254.4403 | 2655188.8431 | 1181254.1766 | 2655177.5221 | 1181256.9833
23 | 2655172.1046 | 1181289.6312 | 2655168.1823 | 1181277.6662 | 2655168.1672 | 1181270.1731 | 2655168.3482 | 1181268.3151
24 | 2655200.2435 | 1181270.1348 | 2655211.4448 | 1181262.7035
25 | 2655172.1046 | 1181289.6312 | 2655175.4261 | 1181297.1659 | 2655186.9067 | 1181317.6828 | 2655195.4793 | 1181330.5466 | 2655196.654 | 1181334.0149 | 2655197.2259 | 1181338.2558 | 2655196.7225 | 1181345.6553 | 2655194.2348 | 1181362.0304 | 2655189.4605 | 1181386.2667
26 | 2655178.0962 | 1181424.4275 | 2655182.8055 | 1181418.0896 | 2655183.7399 | 1181415.3077 | 2655189.4605 | 1181386.2667
27 | 2655178.0962 | 1181424.4275 | 2655177.1586 | 1181422.5845 | 2655178.3868 | 1181412.7682 | 2655177.9207 | 1181407.5778
28 | 2655178.0962 | 1181424.4275 | 2655141.8509 | 1181471.7982
29 | 2655141.8509 | 1181471.7982 | 2655169.6548 | 1181493.3486
30 | 2655188.5911 | 1181508.0259 | 2655169.6548 | 1181493.3486
31 | 2655155.1685 | 1181564.8498 | 2655157.3473 | 1181553.0078 | 2655161.9409 | 1181543.4559 | 2655188.5911 | 1181508.0259 | 2655188.5911 | 1181508.0259
32 | 2655137.2244 | 1181616.1133 | 2655149.9244 | 1181599.4986 | 2655153.7694 | 1181585.8042 | 2655154.6865 | 1181567.4691 | 2655155.1685 | 1181564.8498
33 | 2655137.2244 | 1181616.1133 | 2655157.7208 | 1181618.6587 | 2655162.5403 | 1181618.8344

## bus_geodata
| x | y | coords
0 | 2655015.4995 | 1181492.1984
1 | 2655011.0826 | 1181524.4599
2 | 2655024.4829 | 1181602.0925
3 | 2654951.9369 | 1181533.4783
4 | 2655070.6193 | 1181559.3589
5 | 2655071.3965 | 1181607.9268
6 | 2655068.8183 | 1181519.7614
7 | 2655071.8652 | 1181549.3743
8 | 2654907.8615 | 1181475.4982
9 | 2655119.9794 | 1181613.9687
10 | 2654831.6786 | 1181366.0227
11 | 2654850.0853 | 1181353.9913
12 | 2654829.6641 | 1181300.9858
13 | 2654858.2426 | 1181381.3619
14 | 2654830.5389 | 1181402.7341
15 | 2654863.657 | 1181417.3393
16 | 2654784.4324 | 1181237.2617
17 | 2654858.3247 | 1181381.6375
18 | 2654776.6322 | 1181224.4752
19 | 2654845.6305 | 1181259.1353
20 | 2654835.2646 | 1181220.3337
21 | 2655177.5221 | 1181256.9833
22 | 2655168.3482 | 1181268.3151
23 | 2655200.2435 | 1181270.1348
24 | 2655172.1046 | 1181289.6312
25 | 2655211.4448 | 1181262.7035
26 | 2655189.4605 | 1181386.2667
27 | 2655178.0962 | 1181424.4275
28 | 2655177.9207 | 1181407.5778
29 | 2655141.8509 | 1181471.7982
30 | 2655169.6548 | 1181493.3486
31 | 2655188.5911 | 1181508.0259
32 | 2655155.1685 | 1181564.8498
33 | 2655137.2244 | 1181616.1133
34 | 2655162.5403 | 1181618.8344
35 | 2654858.3937 | 1181381.4073

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98473 | -0.1065 | 0.0046235 | 0.0011588
1 | 0.98499 | -0.1046 | 0 | 0
2 | 0.98555 | -0.10066 | 0 | 0
3 | 0.99128 | -0.060425 | 0 | 0
4 | 0.98464 | -0.10711 | 0 | 0
5 | 0.98379 | -0.11305 | 0.0028207 | 0.00070694
6 | 0.98414 | -0.11063 | 0.0077371 | 0.0019391
7 | 0.98449 | -0.10814 | 0.002229 | 0.00055863
8 | 0.99474 | -0.036283 | 0.00028159 | 7.0573e-05
9 | 0.98036 | -0.13741 | 0.018 | 0.0045111
10 | 0.99676 | -0.022578 | 0.028605 | 0.007169
11 | 0.99766 | -0.016259 | 0 | 0
12 | 0.99064 | -0.065422 | 0.0476 | 0.01193
13 | 1 | 0 | -0.22597 | -0.056779
14 | 0.99821 | -0.012299 | 0.00046157 | 0.00011568
15 | 0.99824 | -0.012128 | 0 | 0
16 | 0.98638 | -0.095561 | 0.032658 | 0.0081849
17 | 0.99998 | -0.00015608 | 0 | 0
18 | 0.98627 | -0.096319 | 0.0049314 | 0.0012359
19 | 0.99241 | -0.053084 | 0.019042 | 0.0047723
20 | 0.99106 | -0.062621 | 0.023385 | 0.0058609
21 | 0.97149 | -0.20101 | 0.0019505 | 0.00048883
22 | 0.97158 | -0.20034 | 0.0016688 | 0.00041825
23 | 0.9714 | -0.20161 | 0 | 0
24 | 0.97175 | -0.19909 | 0 | 0
25 | 0.97137 | -0.20186 | 0.0017568 | 0.00044031
26 | 0.97257 | -0.19318 | 0.0013168 | 0.00033003
27 | 0.97297 | -0.19032 | 0 | 0
28 | 0.97292 | -0.19066 | 0.001868 | 0.00046817
29 | 0.97372 | -0.18493 | 0 | 0
30 | 0.97416 | -0.18175 | 0.014377 | 0.0036033
31 | 0.97496 | -0.17597 | 0.0018278 | 0.00045809
32 | 0.97739 | -0.15857 | 0.002059 | 0.00051602
33 | 0.9796 | -0.14284 | 0 | 0
34 | 0.97948 | -0.14369 | 0.0032125 | 0.00080512
35 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0046235 | -0.0011588 | 0.0046247 | 0.0011587 | 1.2167e-06 | -4.0357e-08 | 0.0069866 | 0.0069864 | 0.0069866 | 0.98473 | -0.1065 | 0.98499 | -0.1046 | 2.5876
1 | -0.0046247 | -0.0011587 | 0.0046273 | 0.0011586 | 2.5235e-06 | -8.4668e-08 | 0.0069864 | 0.006986 | 0.0069864 | 0.98499 | -0.1046 | 0.98555 | -0.10066 | 2.5876
2 | -0.065895 | -0.016564 | 0.066267 | 0.016703 | 0.00037126 | 0.00013971 | 0.099509 | 0.099508 | 0.099509 | 0.98555 | -0.10066 | 0.99128 | -0.060425 | 18.4275
3 | 0.009979 | 0.0025014 | -0.0099701 | -0.0024988 | 8.9138e-06 | 2.6273e-06 | 0.015067 | 0.015067 | 0.015067 | 0.98555 | -0.10066 | 0.98464 | -0.10711 | 5.5804
4 | 0.051289 | 0.012904 | -0.051201 | -0.012871 | 8.8491e-05 | 3.2832e-05 | 0.077456 | 0.077456 | 0.077456 | 0.98555 | -0.10066 | 0.98379 | -0.11305 | 14.3438
5 | -0.066267 | -0.016703 | 0.066491 | 0.016788 | 0.00022479 | 8.4575e-05 | 0.099508 | 0.099507 | 0.099508 | 0.99128 | -0.060425 | 0.99474 | -0.036283 | 18.4273
6 | 0.0099701 | 0.0024988 | -0.0099687 | -0.0024983 | 1.4254e-06 | 4.2026e-07 | 0.015067 | 0.015067 | 0.015067 | 0.98464 | -0.10711 | 0.98449 | -0.10814 | 5.5804
7 | 0.04838 | 0.012164 | -0.048216 | -0.012102 | 0.00016365 | 6.2321e-05 | 0.07319 | 0.07319 | 0.07319 | 0.98379 | -0.11305 | 0.98036 | -0.13741 | 27.1074
8 | -0.0077371 | -0.0019391 | 0.0077397 | 0.0019397 | 2.6657e-06 | 6.2847e-07 | 0.011698 | 0.011698 | 0.011698 | 0.98414 | -0.11063 | 0.98449 | -0.10814 | 4.3327
9 | -0.066773 | -0.016859 | 0.067 | 0.016944 | 0.00022738 | 8.5552e-05 | 0.099928 | 0.099928 | 0.099928 | 0.99474 | -0.036283 | 0.99824 | -0.012128 | 18.5052
10 | 0.030217 | 0.0075904 | -0.030194 | -0.0075819 | 2.2816e-05 | 8.5564e-06 | 0.04587 | 0.04587 | 0.04587 | 0.98036 | -0.13741 | 0.9796 | -0.14284 | 16.9889
11 | -0.028605 | -0.007169 | 0.02863 | 0.0071783 | 2.5045e-05 | 9.3454e-06 | 0.042702 | 0.042702 | 0.042702 | 0.99676 | -0.022578 | 0.99766 | -0.016259 | 15.8157
12 | 0.085933 | 0.021635 | -0.085347 | -0.02141 | 0.00058606 | 0.00022467 | 0.1282 | 0.1282 | 0.1282 | 0.99766 | -0.016259 | 0.99064 | -0.065422 | 47.4832
13 | -0.11456 | -0.028813 | 0.11482 | 0.028912 | 0.00026028 | 9.9359e-05 | 0.17091 | 0.17091 | 0.17091 | 0.99766 | -0.016259 | 1 | 0 | 31.6494
14 | 0.037748 | 0.0094804 | -0.03759 | -0.0094209 | 0.0001575 | 5.957e-05 | 0.056707 | 0.056707 | 0.056707 | 0.99064 | -0.065422 | 0.98638 | -0.095561 | 21.0026
15 | 0.11035 | 0.027867 | -0.11035 | -0.027866 | 2.4208e-06 | 9.2355e-07 | 0.16428 | 0.16428 | 0.16428 | 1 | 0 | 0.99998 | -0.00015608 | 30.4216
16 | -0.00046157 | -0.00011568 | 0.00046158 | 0.0001152 | 1.0846e-08 | -4.7592e-07 | 0.00068806 | 0.00068789 | 0.00068806 | 0.99821 | -0.012299 | 0.99824 | -0.012128 | 0.25484
17 | -0.067462 | -0.017059 | 0.067576 | 0.017102 | 0.00011403 | 4.2914e-05 | 0.10062 | 0.10062 | 0.10062 | 0.99824 | -0.012128 | 0.99998 | -0.00015608 | 18.6325
18 | 0.0049319 | 0.0012359 | -0.0049314 | -0.0012359 | 5.1735e-07 | 7.8192e-09 | 0.00744 | 0.0074401 | 0.0074401 | 0.98638 | -0.095561 | 0.98627 | -0.096319 | 2.7556
19 | 0.042772 | 0.010764 | -0.042458 | -0.010645 | 0.00031363 | 0.00011901 | 0.063662 | 0.063662 | 0.063662 | 0.99998 | -0.00015608 | 0.99241 | -0.053084 | 23.5786
20 | 0.023416 | 0.0058723 | -0.023385 | -0.0058609 | 3.0916e-05 | 1.1372e-05 | 0.035111 | 0.035112 | 0.035112 | 0.99241 | -0.053084 | 0.99106 | -0.062621 | 13.0043
21 | -0.0037075 | -0.00092865 | 0.0037079 | 0.00092857 | 3.4563e-07 | -7.9773e-08 | 0.0056786 | 0.0056785 | 0.0056786 | 0.97149 | -0.20101 | 0.97158 | -0.20034 | 2.1032
22 | 0.001757 | 0.00043982 | -0.0017569 | -0.00044016 | 1.4542e-07 | -3.4247e-07 | 0.0026911 | 0.0026912 | 0.0026912 | 0.97149 | -0.20101 | 0.9714 | -0.20161 | 0.99674
23 | -0.0053767 | -0.0013468 | 0.0053776 | 0.0013469 | 9.2876e-07 | 8.5316e-08 | 0.0082344 | 0.0082343 | 0.0082344 | 0.97158 | -0.20034 | 0.97175 | -0.19909 | 3.0498
24 | 0.0017569 | 0.00044016 | -0.0017568 | -0.00044031 | 6.0752e-08 | -1.4304e-07 | 0.0026912 | 0.0026913 | 0.0026913 | 0.9714 | -0.20161 | 0.97137 | -0.20186 | 0.99676
25 | -0.0053776 | -0.0013469 | 0.005382 | 0.0013473 | 4.3926e-06 | 4.021e-07 | 0.0082343 | 0.0082338 | 0.0082343 | 0.97175 | -0.19909 | 0.97257 | -0.19318 | 3.0497
26 | -0.0066988 | -0.0016773 | 0.0067015 | 0.0016779 | 2.6497e-06 | 5.1721e-07 | 0.010249 | 0.010248 | 0.010249 | 0.97257 | -0.19318 | 0.97297 | -0.19032 | 3.7958
27 | 0.0018681 | 0.00046799 | -0.001868 | -0.00046817 | 8.746e-08 | -1.7962e-07 | 0.0028569 | 0.002857 | 0.002857 | 0.97297 | -0.19032 | 0.97292 | -0.19066 | 1.0581
28 | -0.0085696 | -0.0021458 | 0.008576 | 0.0021476 | 6.3865e-06 | 1.7157e-06 | 0.013105 | 0.013105 | 0.013105 | 0.97297 | -0.19032 | 0.97372 | -0.18493 | 4.8538
29 | -0.008576 | -0.0021476 | 0.0085798 | 0.0021486 | 3.7698e-06 | 1.0122e-06 | 0.013105 | 0.013105 | 0.013105 | 0.97372 | -0.18493 | 0.97416 | -0.18175 | 4.8537
30 | -0.022957 | -0.0057519 | 0.022976 | 0.0057587 | 1.8383e-05 | 6.7719e-06 | 0.035066 | 0.035066 | 0.035066 | 0.97416 | -0.18175 | 0.97496 | -0.17597 | 12.9875
31 | -0.024803 | -0.0062168 | 0.024863 | 0.006239 | 5.989e-05 | 2.2197e-05 | 0.037856 | 0.037855 | 0.037856 | 0.97496 | -0.17597 | 0.97739 | -0.15857 | 14.0206
32 | -0.026922 | -0.006755 | 0.026981 | 0.0067769 | 5.8877e-05 | 2.194e-05 | 0.04099 | 0.04099 | 0.04099 | 0.97739 | -0.15857 | 0.9796 | -0.14284 | 15.1815
33 | 0.0032129 | 0.00080495 | -0.0032125 | -0.00080512 | 3.7864e-07 | -1.7507e-07 | 0.0048803 | 0.0048804 | 0.0048804 | 0.9796 | -0.14284 | 0.97948 | -0.14369 | 1.8075

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.2268 | 0.056987

## res_load
| p_mw | q_mvar
0 | 0.0046235 | 0.0011588
1 | 0.0028207 | 0.00070694
2 | 0.0077371 | 0.0019391
3 | 0.002229 | 0.00055863
4 | 0.00028159 | 7.0573e-05
5 | 0.018 | 0.0045111
6 | 0.028605 | 0.007169
7 | 0.0476 | 0.01193
8 | 0.00082752 | 0.0002074
9 | 0.00046157 | 0.00011568
10 | 0.032658 | 0.0081849
11 | 0.0049314 | 0.0012359
12 | 0.019042 | 0.0047723
13 | 0.023385 | 0.0058609
14 | 0.0019505 | 0.00048883
15 | 0.0016688 | 0.00041825
16 | 0.0017568 | 0.00044031
17 | 0.0013168 | 0.00033003
18 | 0.001868 | 0.00046817
19 | 0.014377 | 0.0036033
20 | 0.0018278 | 0.00045809
21 | 0.002059 | 0.00051602
22 | 0.0032125 | 0.00080512

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1