## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1405-20_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1405-20_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1405-20_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1405-20_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1405-20_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1405-20_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1405-20_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1405-20_0_3_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_1405-20_0_3_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_1405-20_0_3_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_1405-20_0_3_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_1405-20_0_3_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_1405-20_0_3_node_23 | 0.4 | n |  | TRUE
13 | bus_LV_1405-20_0_3_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_1405-20_0_3_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_1405-20_0_3_node_20 | 0.4 | n |  | TRUE
16 | bus_LV_1405-20_0_3_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_1405-20_0_3_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_1405-20_0_3_node_34 | 0.4 | n |  | TRUE
19 | bus_LV_1405-20_0_3_node_35 | 0.4 | n |  | TRUE
20 | bus_LV_1405-20_0_3_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_1405-20_0_3_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_1405-20_0_3_node_21 | 0.4 | n |  | TRUE
23 | bus_LV_1405-20_0_3_node_22 | 0.4 | n |  | TRUE
24 | bus_LV_1405-20_0_3_node_27 | 0.4 | n |  | TRUE
25 | bus_LV_1405-20_0_3_node_25 | 0.4 | n |  | TRUE
26 | bus_LV_1405-20_0_3_node_24 | 0.4 | n |  | TRUE
27 | bus_LV_1405-20_0_3_node_26 | 0.4 | n |  | TRUE
28 | bus_LV_1405-20_0_3_node_28 | 0.4 | n |  | TRUE
29 | bus_LV_1405-20_0_3_node_30 | 0.4 | n |  | TRUE
30 | bus_LV_1405-20_0_3_node_29 | 0.4 | n |  | TRUE
31 | bus_LV_1405-20_0_3_node_31 | 0.4 | n |  | TRUE
32 | bus_LV_1405-20_0_3_node_33 | 0.4 | n |  | TRUE
33 | bus_LV_1405-20_0_3_node_32 | 0.4 | n |  | TRUE
34 | bus_LV_1405-20_0_3_node_40 | 0.4 | n |  | TRUE
35 | bus_LV_1405-20_0_3_node_36 | 0.4 | n |  | TRUE
36 | bus_LV_1405-20_0_3_node_39 | 0.4 | n |  | TRUE
37 | bus_LV_1405-20_0_3_node_37 | 0.4 | n |  | TRUE
38 | bus_MV_138_2_node_83 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1405-20_0_3_load_0 | 0 | 0.0033766 | 0.00084627 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1405-20_0_3_load_3 | 3 | 0.0047342 | 0.0011865 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1405-20_0_3_load_4 | 4 | 0.0057704 | 0.0014462 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1405-20_0_3_load_5 | 5 | 0.0060317 | 0.0015117 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1405-20_0_3_load_6 | 6 | 0.0031431 | 0.00078773 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1405-20_0_3_load_8 | 7 | 0.0056119 | 0.0014065 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1405-20_0_3_load_7 | 8 | 0.010438 | 0.0026161 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1405-20_0_3_load_9 | 9 | 0.006311 | 0.0015817 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1405-20_0_3_load_23 | 12 | 0.0056335 | 0.0014119 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1405-20_0_3_load_14 | 13 | 0.0032381 | 0.00081155 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1405-20_0_3_load_11 | 14 | 0.0073205 | 0.0018347 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1405-20_0_3_load_13 | 16 | 0.003709 | 0.00092955 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1405-20_0_3_load_15 | 17 | 0.0098553 | 0.00247 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1405-20_0_3_load_34 | 18 | 0.0023426 | 0.0005871 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1405-20_0_3_load_35 | 19 | 0.0029088 | 0.000729 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1405-20_0_3_load_18 | 20 | 0.0055377 | 0.0013879 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1405-20_0_3_load_21 | 22 | 0.017182 | 0.0043063 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1405-20_0_3_load_22 | 23 | 0.0032871 | 0.00082382 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1405-20_0_3_load_27 | 24 | 0.0092495 | 0.0023181 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1405-20_0_3_load_25 | 25 | 0.0050813 | 0.0012735 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1405-20_0_3_load_24 | 26 | 0.0027246 | 0.00068286 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1405-20_0_3_load_26 | 27 | 0.0014591 | 0.0003657 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1405-20_0_3_load_28 | 28 | 0.0055037 | 0.0013794 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1405-20_0_3_load_30 | 29 | 0.0014893 | 0.00037325 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1405-20_0_3_load_29 | 30 | 0.004976 | 0.0012471 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1405-20_0_3_load_40 | 34 | 0.0071955 | 0.0018034 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1405-20_0_3_load_36 | 35 | 0.0032996 | 0.00082695 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1405-20_0_3_load_37 | 37 | 0.0031616 | 0.00079237 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 20 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1405-20_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.099743 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1405-20_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0038123 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1405-20_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.083269 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1405-20_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.020215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1405-20_0_3_line_4 | NAYY 4x150 SE | 4 | 5 | 0.0055213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1405-20_0_3_line_5 | NAYY 4x150 SE | 5 | 6 | 0.0067828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1405-20_0_3_line_6 | NAYY 4x150 SE | 6 | 7 | 0.018834 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1405-20_0_3_line_7 | NAYY 4x150 SE | 7 | 8 | 0.0049714 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1405-20_0_3_line_8 | NAYY 4x150 SE | 8 | 9 | 0.016344 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1405-20_0_3_line_9 | NAYY 4x150 SE | 9 | 10 | 0.0052212 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1405-20_0_3_line_10 | NAYY 4x150 SE | 10 | 11 | 0.07728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1405-20_0_3_line_11 | NAYY 4x150 SE | 10 | 12 | 0.0051378 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1405-20_0_3_line_12 | NAYY 4x150 SE | 11 | 13 | 0.013199 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1405-20_0_3_line_13 | NAYY 4x150 SE | 11 | 14 | 0.01259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1405-20_0_3_line_14 | NAYY 4x150 SE | 12 | 15 | 0.023645 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1405-20_0_3_line_15 | NAYY 4x150 SE | 13 | 17 | 0.0014005 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1405-20_0_3_line_16 | NAYY 4x150 SE | 14 | 16 | 0.0037999 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1405-20_0_3_line_17 | NAYY 4x150 SE | 15 | 23 | 0.0031669 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1405-20_0_3_line_18 | NAYY 4x150 SE | 15 | 20 | 0.013064 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
19 | LV_1405-20_0_3_line_19 | NAYY 4x150 SE | 18 | 19 | 0.003352 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1405-20_0_3_line_20 | NAYY 4x150 SE | 19 | 35 | 0.024355 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1405-20_0_3_line_21 | NAYY 4x150 SE | 20 | 21 | 0.027386 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1405-20_0_3_line_22 | NAYY 4x150 SE | 21 | 22 | 0.013304 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1405-20_0_3_line_23 | NAYY 4x150 SE | 23 | 24 | 0.015325 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1405-20_0_3_line_24 | NAYY 4x150 SE | 24 | 25 | 0.017702 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1405-20_0_3_line_25 | NAYY 4x150 SE | 25 | 26 | 0.015316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1405-20_0_3_line_26 | NAYY 4x150 SE | 26 | 27 | 0.0029944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1405-20_0_3_line_27 | NAYY 4x150 SE | 27 | 28 | 0.015864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1405-20_0_3_line_28 | NAYY 4x150 SE | 28 | 29 | 0.00011831 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1405-20_0_3_line_29 | NAYY 4x150 SE | 29 | 30 | 0.0033432 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1405-20_0_3_line_30 | NAYY 4x150 SE | 30 | 31 | 0.0019545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1405-20_0_3_line_31 | NAYY 4x150 SE | 31 | 32 | 0.019752 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1405-20_0_3_line_32 | NAYY 4x150 SE | 32 | 35 | 0.012168 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1405-20_0_3_line_33 | NAYY 4x150 SE | 32 | 33 | 0.003921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1405-20_0_3_line_34 | NAYY 4x150 SE | 33 | 34 | 0.032278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1405-20_0_3_line_35 | NAYY 4x150 SE | 34 | 36 | 0.038787 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1405-20_0_3_line_36 | NAYY 4x150 SE | 36 | 37 | 0.034954 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1405-20_0_3_trafo_18 | 0.25 MVA 20/0.4 kV | 38 | 20 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2655072.9227 | 1181951.1858 | 2655075.3545 | 1181964.938 | 2655077.3276 | 1181977.0851 | 2655089.911 | 1182049.4706
1 | 2655090.5639 | 1182053.2266 | 2655089.911 | 1182049.4706
2 | 2655072.9227 | 1181951.1858 | 2655077.5719 | 1181950.4948 | 2655081.2547 | 1181951.0956 | 2655088.6362 | 1181954.721 | 2655097.6346 | 1181962.7081 | 2655109.2778 | 1181981.2142 | 2655108.3193 | 1181983.3065 | 2655111.1057 | 1181990.0358 | 2655119.7914 | 1182003.7899 | 2655123.84 | 1182009.4525
3 | 2655090.5639 | 1182053.2266 | 2655094.0354 | 1182073.1415
4 | 2655094.0354 | 1182073.1415 | 2655094.9835 | 1182078.5807
5 | 2655094.9835 | 1182078.5807 | 2655096.1483 | 1182085.2627
6 | 2655099.3826 | 1182103.8165 | 2655096.1483 | 1182085.2627
7 | 2655099.3826 | 1182103.8165 | 2655100.2363 | 1182108.7141
8 | 2655103.0429 | 1182124.815 | 2655100.2363 | 1182108.7141
9 | 2655103.9395 | 1182129.9586 | 2655103.0429 | 1182124.815
10 | 2655103.9395 | 1182129.9586 | 2655122.5522 | 1182127.9063 | 2655133.8441 | 1182124.775 | 2655138.1267 | 1182123.2469 | 2655140.7484 | 1182119.6579 | 2655141.0291 | 1182115.7027 | 2655139.5112 | 1182109.7077 | 2655138.1167 | 1182104.4141 | 2655137.885 | 1182102.2108 | 2655138.8276 | 1182099.3512 | 2655141.3554 | 1182097.6624 | 2655153.9594 | 1182091.3637
11 | 2655103.9395 | 1182129.9586 | 2655104.8486 | 1182135.0154
12 | 2655153.9594 | 1182091.3637 | 2655159.9751 | 1182103.1116
13 | 2655153.9594 | 1182091.3637 | 2655148.833 | 1182079.8646
14 | 2655109.032 | 1182158.2878 | 2655104.8486 | 1182135.0154
15 | 2655160.6135 | 1182104.3582 | 2655159.9751 | 1182103.1116
16 | 2655147.2858 | 1182076.394 | 2655148.833 | 1182079.8646
17 | 2655109.032 | 1182158.2878 | 2655109.5927 | 1182161.4046
18 | 2655109.032 | 1182158.2878 | 2655121.8877 | 1182155.9631
19 | 2655163.1936 | 1182239.0563 | 2655160.0635 | 1182240.2556
20 | 2655137.3209 | 1182248.9694 | 2655160.0635 | 1182240.2556
21 | 2655148.7386 | 1182155.0287 | 2655147.8615 | 1182154.9095 | 2655142.9575 | 1182153.4413 | 2655138.8696 | 1182152.8924 | 2655121.8877 | 1182155.9631
22 | 2655162.0021 | 1182154.228 | 2655151.2402 | 1182155.3519 | 2655148.7386 | 1182155.0287
23 | 2655112.3061 | 1182176.4879 | 2655109.5927 | 1182161.4046
24 | 2655115.4402 | 1182193.91 | 2655112.3061 | 1182176.4879
25 | 2655118.1519 | 1182208.9838 | 2655115.4402 | 1182193.91
26 | 2655118.1519 | 1182208.9838 | 2655118.6821 | 1182211.9309
27 | 2655121.4908 | 1182227.5442 | 2655118.6821 | 1182211.9309
28 | 2655121.4908 | 1182227.5442 | 2655121.5118 | 1182227.6606
29 | 2655122.1037 | 1182230.951 | 2655121.5118 | 1182227.6606
30 | 2655122.4497 | 1182232.8746 | 2655122.1037 | 1182230.951
31 | 2655125.6685 | 1182252.3595 | 2655122.4497 | 1182232.8746
32 | 2655125.6685 | 1182252.3595 | 2655132.3177 | 1182250.8864 | 2655137.3209 | 1182248.9694
33 | 2655121.857 | 1182253.325 | 2655125.6685 | 1182252.3595
34 | 2655121.857 | 1182253.325 | 2655128.0345 | 1182285.0067
35 | 2655137.5689 | 1182322.5188 | 2655132.2698 | 1182306.728 | 2655128.0345 | 1182285.0067
36 | 2655137.5689 | 1182322.5188 | 2655114.5452 | 1182324.3749 | 2655103.8697 | 1182319.2184

## bus_geodata
| x | y | coords
0 | 2655089.911 | 1182049.4706
1 | 2655072.9227 | 1181951.1858
2 | 2655090.5639 | 1182053.2266
3 | 2655123.84 | 1182009.4525
4 | 2655094.0354 | 1182073.1415
5 | 2655094.9835 | 1182078.5807
6 | 2655096.1483 | 1182085.2627
7 | 2655099.3825 | 1182103.8165
8 | 2655100.2363 | 1182108.7141
9 | 2655103.0429 | 1182124.815
10 | 2655103.9395 | 1182129.9586
11 | 2655153.9594 | 1182091.3637
12 | 2655104.8486 | 1182135.0154
13 | 2655159.9751 | 1182103.1116
14 | 2655148.833 | 1182079.8646
15 | 2655109.032 | 1182158.2878
16 | 2655147.2858 | 1182076.394
17 | 2655160.6135 | 1182104.3582
18 | 2655163.1936 | 1182239.0563
19 | 2655160.0635 | 1182240.2556
20 | 2655121.8877 | 1182155.9631
21 | 2655148.7386 | 1182155.0287
22 | 2655162.0021 | 1182154.228
23 | 2655109.5927 | 1182161.4046
24 | 2655112.3061 | 1182176.4879
25 | 2655115.4402 | 1182193.91
26 | 2655118.1519 | 1182208.9838
27 | 2655118.6821 | 1182211.9309
28 | 2655121.4908 | 1182227.5442
29 | 2655121.5118 | 1182227.6606
30 | 2655122.1037 | 1182230.951
31 | 2655122.4497 | 1182232.8746
32 | 2655125.6685 | 1182252.3595
33 | 2655121.857 | 1182253.325
34 | 2655128.0345 | 1182285.0067
35 | 2655137.3209 | 1182248.9694
36 | 2655137.5689 | 1182322.5188
37 | 2655103.8697 | 1182319.2184
38 | 2655109.032 | 1182158.2878

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99307 | -0.048569 | 0.0033766 | 0.00084627
1 | 0.99239 | -0.053364 | 0 | 0
2 | 0.99312 | -0.048256 | 0 | 0
3 | 0.99183 | -0.057365 | 0.0047342 | 0.0011865
4 | 0.99335 | -0.046593 | 0.0057704 | 0.0014462
5 | 0.99346 | -0.045817 | 0.0060317 | 0.0015117
6 | 0.99366 | -0.04445 | 0.0031431 | 0.00078773
7 | 0.99428 | -0.040059 | 0.0056119 | 0.0014065
8 | 0.99448 | -0.03862 | 0.010438 | 0.0026161
9 | 0.9954 | -0.032172 | 0.006311 | 0.0015817
10 | 0.99574 | -0.029783 | 0 | 0
11 | 0.99306 | -0.048604 | 0 | 0
12 | 0.99625 | -0.026186 | 0.0056335 | 0.0014119
13 | 0.99282 | -0.050353 | 0.0032381 | 0.00081155
14 | 0.99286 | -0.050009 | 0.0073205 | 0.0018347
15 | 0.9988 | -0.0083492 | 0 | 0
16 | 0.99284 | -0.050152 | 0.003709 | 0.00092955
17 | 0.9928 | -0.050493 | 0.0098553 | 0.00247
18 | 0.9938 | -0.04347 | 0.0023426 | 0.0005871
19 | 0.99381 | -0.04339 | 0.0029088 | 0.000729
20 | 1 | 0 | -0.14655 | -0.036616
21 | 0.99933 | -0.0047002 | 0 | 0
22 | 0.999 | -0.0069855 | 0.017182 | 0.0043063
23 | 0.99856 | -0.010019 | 0.0032871 | 0.00082382
24 | 0.99748 | -0.017607 | 0.0092495 | 0.0023181
25 | 0.99646 | -0.024746 | 0.0050813 | 0.0012735
26 | 0.99569 | -0.030151 | 0.0027246 | 0.00068286
27 | 0.99555 | -0.031126 | 0.0014591 | 0.0003657
28 | 0.99485 | -0.036065 | 0.0055037 | 0.0013794
29 | 0.99485 | -0.036095 | 0.0014893 | 0.00037325
30 | 0.99473 | -0.036901 | 0.004976 | 0.0012471
31 | 0.99468 | -0.037274 | 0 | 0
32 | 0.99414 | -0.041047 | 0 | 0
33 | 0.99408 | -0.041457 | 0 | 0
34 | 0.99361 | -0.044838 | 0.0071955 | 0.0018034
35 | 0.99399 | -0.042098 | 0.0032996 | 0.00082695
36 | 0.99343 | -0.04608 | 0 | 0
37 | 0.99327 | -0.047198 | 0.0031616 | 0.00079237
38 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0047399 | 0.0011863 | -0.0047368 | -0.0011864 | 3.1392e-06 | -8.2208e-08 | 0.0071017 | 0.0071022 | 0.0071022 | 0.99307 | -0.048569 | 0.99239 | -0.053364 | 2.6304
1 | -0.0081166 | -0.0020326 | 0.0081169 | 0.0020327 | 3.5183e-07 | 8.5991e-08 | 0.012161 | 0.012161 | 0.012161 | 0.99307 | -0.048569 | 0.99312 | -0.048256 | 4.5042
2 | 0.0047368 | 0.0011864 | -0.0047342 | -0.0011865 | 2.6211e-06 | -6.7162e-08 | 0.0071022 | 0.0071026 | 0.0071026 | 0.99239 | -0.053364 | 0.99183 | -0.057365 | 2.6306
3 | -0.0081169 | -0.0020327 | 0.0081188 | 0.0020332 | 1.8656e-06 | 4.559e-07 | 0.012161 | 0.012161 | 0.012161 | 0.99312 | -0.048256 | 0.99335 | -0.046593 | 4.5042
4 | -0.013889 | -0.0034793 | 0.013891 | 0.0034798 | 1.4913e-06 | 5.0208e-07 | 0.020805 | 0.020805 | 0.020805 | 0.99335 | -0.046593 | 0.99346 | -0.045817 | 7.7056
5 | -0.019922 | -0.0049915 | 0.019926 | 0.0049929 | 3.7685e-06 | 1.3616e-06 | 0.029839 | 0.029839 | 0.029839 | 0.99346 | -0.045817 | 0.99366 | -0.04445 | 11.0516
6 | -0.023069 | -0.0057806 | 0.023083 | 0.0057858 | 1.4025e-05 | 5.1502e-06 | 0.034546 | 0.034546 | 0.034546 | 0.99366 | -0.04445 | 0.99428 | -0.040059 | 12.7948
7 | -0.028695 | -0.0071922 | 0.028701 | 0.0071944 | 5.7211e-06 | 2.136e-06 | 0.042945 | 0.042945 | 0.042945 | 0.99428 | -0.040059 | 0.99448 | -0.03862 | 15.9054
8 | -0.039139 | -0.0098105 | 0.039174 | 0.0098237 | 3.4977e-05 | 1.3241e-05 | 0.058563 | 0.058563 | 0.058563 | 0.99448 | -0.03862 | 0.9954 | -0.032172 | 21.6901
9 | -0.045485 | -0.011405 | 0.0455 | 0.011411 | 1.5064e-05 | 5.726e-06 | 0.067997 | 0.067997 | 0.067997 | 0.9954 | -0.032172 | 0.99574 | -0.029783 | 25.1843
10 | 0.024192 | 0.0060708 | -0.024129 | -0.0060475 | 6.3034e-05 | 2.3241e-05 | 0.036154 | 0.036154 | 0.036154 | 0.99574 | -0.029783 | 0.99306 | -0.048604 | 13.3905
11 | -0.069692 | -0.017482 | 0.069727 | 0.017495 | 3.4777e-05 | 1.3309e-05 | 0.10415 | 0.10415 | 0.10415 | 0.99574 | -0.029783 | 0.99625 | -0.026186 | 38.5747
12 | 0.013097 | 0.0032826 | -0.013094 | -0.0032816 | 3.1718e-06 | 1.0492e-06 | 0.019624 | 0.019625 | 0.019625 | 0.99306 | -0.048604 | 0.99282 | -0.050353 | 7.2683
13 | 0.011032 | 0.0027649 | -0.01103 | -0.0027642 | 2.1466e-06 | 6.6278e-07 | 0.01653 | 0.01653 | 0.01653 | 0.99306 | -0.048604 | 0.99286 | -0.050009 | 6.1223
14 | -0.07536 | -0.018907 | 0.075547 | 0.018979 | 0.00018696 | 7.1598e-05 | 0.11257 | 0.11257 | 0.11257 | 0.99625 | -0.026186 | 0.9988 | -0.0083492 | 41.691
15 | 0.0098555 | 0.00247 | -0.0098553 | -0.00247 | 1.9068e-07 | 5.5227e-08 | 0.014771 | 0.014771 | 0.014771 | 0.99282 | -0.050353 | 0.9928 | -0.050493 | 5.4708
16 | 0.003709 | 0.00092953 | -0.003709 | -0.00092955 | 7.3267e-08 | -2.0962e-08 | 0.0055587 | 0.0055588 | 0.0055588 | 0.99286 | -0.050009 | 0.99284 | -0.050152 | 2.0588
17 | 0.052857 | 0.013268 | -0.052845 | -0.013263 | 1.2256e-05 | 4.6725e-06 | 0.078754 | 0.078754 | 0.078754 | 0.9988 | -0.0083492 | 0.99856 | -0.010019 | 29.1681
18 | -0.1284 | -0.032247 | 0.12855 | 0.032304 | 0.0001492 | 5.7041e-05 | 0.19132 | 0.19132 | 0.19132 | 0.9988 | -0.0083492 | 1 | 0 | 35.4295
19 | -0.0023426 | -0.0005871 | 0.0023426 | 0.00058707 | 2.5733e-08 | -3.3535e-08 | 0.0035075 | 0.0035075 | 0.0035075 | 0.9938 | -0.04347 | 0.99381 | -0.04339 | 1.2991
20 | -0.0052513 | -0.0013161 | 0.0052523 | 0.0013161 | 9.3953e-07 | 4.5725e-08 | 0.0078627 | 0.0078626 | 0.0078627 | 0.99381 | -0.04339 | 0.99399 | -0.042098 | 2.9121
21 | 0.017199 | 0.0043122 | -0.017188 | -0.0043082 | 1.1193e-05 | 3.9461e-06 | 0.025593 | 0.025593 | 0.025593 | 1 | 0 | 0.99933 | -0.0047002 | 9.4789
22 | 0.017188 | 0.0043082 | -0.017182 | -0.0043063 | 5.4377e-06 | 1.9172e-06 | 0.025593 | 0.025593 | 0.025593 | 0.99933 | -0.0047002 | 0.999 | -0.0069855 | 9.479
23 | 0.049558 | 0.012439 | -0.049506 | -0.01242 | 5.2163e-05 | 1.9862e-05 | 0.073856 | 0.073856 | 0.073856 | 0.99856 | -0.010019 | 0.99748 | -0.017607 | 27.3539
24 | 0.040256 | 0.010101 | -0.040216 | -0.010086 | 3.9841e-05 | 1.5093e-05 | 0.060057 | 0.060057 | 0.060057 | 0.99748 | -0.017607 | 0.99646 | -0.024746 | 22.2435
25 | 0.035135 | 0.0088129 | -0.035109 | -0.0088029 | 2.6311e-05 | 9.9203e-06 | 0.05247 | 0.05247 | 0.05247 | 0.99646 | -0.024746 | 0.99569 | -0.030151 | 19.4332
26 | 0.032384 | 0.0081201 | -0.03238 | -0.0081184 | 4.3767e-06 | 1.6444e-06 | 0.048398 | 0.048398 | 0.048398 | 0.99569 | -0.030151 | 0.99555 | -0.031126 | 17.9251
27 | 0.03092 | 0.0077527 | -0.030899 | -0.0077448 | 2.1144e-05 | 7.9263e-06 | 0.046217 | 0.046217 | 0.046217 | 0.99555 | -0.031126 | 0.99485 | -0.036065 | 17.1174
28 | 0.025396 | 0.0063655 | -0.025395 | -0.0063654 | 1.0652e-07 | 3.9434e-08 | 0.037985 | 0.037985 | 0.037985 | 0.99485 | -0.036065 | 0.99485 | -0.036095 | 14.0685
29 | 0.023906 | 0.0059922 | -0.023904 | -0.0059912 | 2.6673e-06 | 9.8249e-07 | 0.035757 | 0.035757 | 0.035757 | 0.99485 | -0.036095 | 0.99473 | -0.036901 | 13.2435
30 | 0.018928 | 0.0047441 | -0.018927 | -0.0047437 | 9.7774e-07 | 3.5068e-07 | 0.028314 | 0.028314 | 0.028314 | 0.99473 | -0.036901 | 0.99468 | -0.037274 | 10.4866
31 | 0.018927 | 0.0047437 | -0.018917 | -0.0047402 | 9.8809e-06 | 3.5441e-06 | 0.028314 | 0.028314 | 0.028314 | 0.99468 | -0.037274 | 0.99414 | -0.041047 | 10.4866
32 | 0.0085531 | 0.0021434 | -0.0085519 | -0.0021431 | 1.2445e-06 | 3.2088e-07 | 0.012802 | 0.012802 | 0.012802 | 0.99414 | -0.041047 | 0.99399 | -0.042098 | 4.7415
33 | 0.010364 | 0.0025968 | -0.010363 | -0.0025966 | 5.8872e-07 | 1.7559e-07 | 0.015512 | 0.015512 | 0.015512 | 0.99414 | -0.041047 | 0.99408 | -0.041457 | 5.7451
34 | 0.010363 | 0.0025966 | -0.010358 | -0.0025952 | 4.8465e-06 | 1.4458e-06 | 0.015512 | 0.015512 | 0.015512 | 0.99408 | -0.041457 | 0.99361 | -0.044838 | 5.7452
35 | 0.0031626 | 0.00079181 | -0.0031621 | -0.0007921 | 5.4289e-07 | -2.9347e-07 | 0.004736 | 0.0047362 | 0.0047362 | 0.99361 | -0.044838 | 0.99343 | -0.04608 | 1.7542
36 | 0.0031621 | 0.0007921 | -0.0031616 | -0.00079237 | 4.8928e-07 | -2.6431e-07 | 0.0047362 | 0.0047364 | 0.0047364 | 0.99343 | -0.04608 | 0.99327 | -0.047198 | 1.7542

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.15209 | 0.038004

## res_load
| p_mw | q_mvar
0 | 0.0033766 | 0.00084627
1 | 0.0047342 | 0.0011865
2 | 0.0057704 | 0.0014462
3 | 0.0060317 | 0.0015117
4 | 0.0031431 | 0.00078773
5 | 0.0056119 | 0.0014065
6 | 0.010438 | 0.0026161
7 | 0.006311 | 0.0015817
8 | 0.0056335 | 0.0014119
9 | 0.0032381 | 0.00081155
10 | 0.0073205 | 0.0018347
11 | 0.003709 | 0.00092955
12 | 0.0098553 | 0.00247
13 | 0.0023426 | 0.0005871
14 | 0.0029088 | 0.000729
15 | 0.0055377 | 0.0013879
16 | 0.017182 | 0.0043063
17 | 0.0032871 | 0.00082382
18 | 0.0092495 | 0.0023181
19 | 0.0050813 | 0.0012735
20 | 0.0027246 | 0.00068286
21 | 0.0014591 | 0.0003657
22 | 0.0055037 | 0.0013794
23 | 0.0014893 | 0.00037325
24 | 0.004976 | 0.0012471
25 | 0.0071955 | 0.0018034
26 | 0.0032996 | 0.00082695
27 | 0.0031616 | 0.00079237

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1