## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1406-18_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1406-18_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1406-18_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1406-18_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1406-18_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1406-18_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1406-18_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1406-18_0_3_node_51 | 0.4 | n |  | TRUE
8 | bus_LV_1406-18_0_3_node_12 | 0.4 | n |  | TRUE
9 | bus_LV_1406-18_0_3_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_1406-18_0_3_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1406-18_0_3_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_1406-18_0_3_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_1406-18_0_3_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_1406-18_0_3_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_1406-18_0_3_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_1406-18_0_3_node_62 | 0.4 | n |  | TRUE
17 | bus_LV_1406-18_0_3_node_95 | 0.4 | n |  | TRUE
18 | bus_LV_1406-18_0_3_node_50 | 0.4 | n |  | TRUE
19 | bus_LV_1406-18_0_3_node_52 | 0.4 | n |  | TRUE
20 | bus_LV_1406-18_0_3_node_53 | 0.4 | n |  | TRUE
21 | bus_LV_1406-18_0_3_node_57 | 0.4 | n |  | TRUE
22 | bus_LV_1406-18_0_3_node_54 | 0.4 | n |  | TRUE
23 | bus_LV_1406-18_0_3_node_55 | 0.4 | n |  | TRUE
24 | bus_LV_1406-18_0_3_node_56 | 0.4 | n |  | TRUE
25 | bus_LV_1406-18_0_3_node_61 | 0.4 | n |  | TRUE
26 | bus_LV_1406-18_0_3_node_58 | 0.4 | n |  | TRUE
27 | bus_LV_1406-18_0_3_node_59 | 0.4 | n |  | TRUE
28 | bus_LV_1406-18_0_3_node_60 | 0.4 | n |  | TRUE
29 | bus_LV_1406-18_0_3_node_63 | 0.4 | n |  | TRUE
30 | bus_LV_1406-18_0_3_node_107 | 0.4 | n |  | TRUE
31 | bus_LV_1406-18_0_3_node_102 | 0.4 | n |  | TRUE
32 | bus_LV_1406-18_0_3_node_103 | 0.4 | n |  | TRUE
33 | bus_LV_1406-18_0_3_node_104 | 0.4 | n |  | TRUE
34 | bus_LV_1406-18_0_3_node_105 | 0.4 | n |  | TRUE
35 | bus_LV_1406-18_0_3_node_106 | 0.4 | n |  | TRUE
36 | bus_MV_138_3_node_126 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1406-18_0_3_load_0 | 0 | 0.00062129 | 0.00015571 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1406-18_0_3_load_1 | 1 | 0.00014777 | 3.7034e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1406-18_0_3_load_3 | 3 | 0.00013139 | 3.2929e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1406-18_0_3_load_5 | 5 | 0.0068403 | 0.0017143 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1406-18_0_3_load_6 | 6 | 0.00086629 | 0.00021711 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1406-18_0_3_load_51 | 7 | 0.00065262 | 0.00016356 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1406-18_0_3_load_7 | 9 | 0.0011637 | 0.00029166 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1406-18_0_3_load_8 | 10 | 0.0015515 | 0.00038885 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1406-18_0_3_load_14 | 13 | 0.0017795 | 0.00044598 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1406-18_0_3_load_11 | 14 | 0.0027504 | 0.00068931 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1406-18_0_3_load_13 | 15 | 0.0049496 | 0.0012405 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1406-18_0_3_load_62 | 16 | 0.00092557 | 0.00023197 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1406-18_0_3_load_95 | 17 | 0.0044476 | 0.0011147 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1406-18_0_3_load_50 | 18 | 0.00153 | 0.00038346 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1406-18_0_3_load_57 | 21 | 0.0026304 | 0.00065923 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1406-18_0_3_load_54 | 22 | 0.0094089 | 0.0023581 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1406-18_0_3_load_55 | 23 | 0.00080225 | 0.00020106 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1406-18_0_3_load_56 | 24 | 0.010457 | 0.0026208 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1406-18_0_3_load_61 | 25 | 0.0087489 | 0.0021927 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1406-18_0_3_load_59 | 27 | 0.0018633 | 0.00046699 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1406-18_0_3_load_60 | 28 | 0.0018289 | 0.00045836 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1406-18_0_3_load_63 | 29 | 0.0012779 | 0.00032027 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1406-18_0_3_load_102 | 31 | 0.0037675 | 0.00094423 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1406-18_0_3_load_103 | 32 | 0.00069455 | 0.00017407 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1406-18_0_3_load_104 | 33 | 0.002013 | 0.00050451 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1406-18_0_3_load_105 | 34 | 0.0010991 | 0.00027546 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1406-18_0_3_load_106 | 35 | 0.0050057 | 0.0012545 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 29 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1406-18_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.00090388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1406-18_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0164 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1406-18_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.005449 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1406-18_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.025812 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
4 | LV_1406-18_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.0224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
5 | LV_1406-18_0_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.10413 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1406-18_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.019537 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
7 | LV_1406-18_0_3_line_7 | NAYY 4x150 SE | 5 | 8 | 0.045365 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_1406-18_0_3_line_8 | NAYY 4x150 SE | 7 | 18 | 0.078802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
9 | LV_1406-18_0_3_line_9 | NAYY 4x150 SE | 8 | 14 | 0.16218 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
10 | LV_1406-18_0_3_line_10 | NAYY 4x150 SE | 9 | 10 | 0.019967 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1406-18_0_3_line_11 | NAYY 4x150 SE | 10 | 11 | 0.031129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1406-18_0_3_line_12 | NAYY 4x150 SE | 11 | 12 | 0.036255 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1406-18_0_3_line_13 | NAYY 4x150 SE | 12 | 13 | 0.064607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1406-18_0_3_line_14 | NAYY 4x150 SE | 12 | 14 | 0.013343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1406-18_0_3_line_15 | NAYY 4x150 SE | 13 | 17 | 0.024629 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1406-18_0_3_line_16 | NAYY 4x150 SE | 15 | 16 | 0.0015854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1406-18_0_3_line_17 | NAYY 4x150 SE | 16 | 29 | 0.016419 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1406-18_0_3_line_18 | NAYY 4x150 SE | 17 | 30 | 0.086071 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1406-18_0_3_line_19 | NAYY 4x150 SE | 18 | 19 | 0.057978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
20 | LV_1406-18_0_3_line_20 | NAYY 4x150 SE | 19 | 20 | 0.089968 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
21 | LV_1406-18_0_3_line_21 | NAYY 4x150 SE | 20 | 21 | 0.025409 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1406-18_0_3_line_22 | NAYY 4x150 SE | 20 | 22 | 0.018454 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
23 | LV_1406-18_0_3_line_23 | NAYY 4x150 SE | 21 | 26 | 0.067863 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1406-18_0_3_line_24 | NAYY 4x150 SE | 22 | 23 | 0.058657 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
25 | LV_1406-18_0_3_line_25 | NAYY 4x150 SE | 23 | 24 | 0.043873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
26 | LV_1406-18_0_3_line_26 | NAYY 4x150 SE | 24 | 25 | 0.029981 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
27 | LV_1406-18_0_3_line_27 | NAYY 4x150 SE | 25 | 29 | 0.023334 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
28 | LV_1406-18_0_3_line_28 | NAYY 4x150 SE | 26 | 27 | 0.050454 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1406-18_0_3_line_29 | NAYY 4x150 SE | 27 | 28 | 0.029458 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1406-18_0_3_line_30 | NAYY 4x150 SE | 30 | 35 | 0.081224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1406-18_0_3_line_31 | NAYY 4x150 SE | 31 | 32 | 0.098426 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1406-18_0_3_line_32 | NAYY 4x150 SE | 32 | 33 | 0.096606 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1406-18_0_3_line_33 | NAYY 4x150 SE | 33 | 34 | 0.21427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1406-18_0_3_line_34 | NAYY 4x150 SE | 34 | 35 | 0.04442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1406-18_0_3_trafo_63 | 0.25 MVA 20/0.4 kV | 36 | 29 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18
0 | 2659502.1782 | 1189994.8657 | 2659502.1782 | 1189994.8657 | 2659502.7363 | 1189994.1547
1 | 2659510.7616 | 1189979.8868 | 2659504.1092 | 1189992.4057 | 2659502.7363 | 1189994.1547
2 | 2659497.3873 | 1189997.3417 | 2659500.0351 | 1189996.4119 | 2659502.1782 | 1189994.8657
3 | 2659533.8518 | 1189991.5563 | 2659510.7616 | 1189979.8868
4 | 2659510.7616 | 1189979.8868 | 2659490.5828 | 1189970.1608
5 | 2659408.9784 | 1190018.0315 | 2659409.346 | 1190007.8849 | 2659409.4677 | 1190004.8399 | 2659410.3925 | 1190002.3365 | 2659411.5819 | 1190000.8252 | 2659413.9303 | 1189999.3255 | 2659417.4372 | 1189998.671 | 2659493.9742 | 1189997.7636 | 2659497.3873 | 1189997.3417
6 | 2659533.8518 | 1189991.5563 | 2659546.0281 | 1189976.2784
7 | 2659449.7169 | 1189950.4638 | 2659490.5828 | 1189970.1608
8 | 2659612.4459 | 1189986.7973 | 2659605.0771 | 1189980.3361 | 2659602.5819 | 1189978.9549 | 2659600.4786 | 1189978.8005 | 2659595.8626 | 1189979.0214 | 2659593.3593 | 1189978.4517 | 2659591.1988 | 1189977.1517 | 2659585.0667 | 1189972.6215 | 2659580.6047 | 1189971.154 | 2659572.888 | 1189969.5319 | 2659569.8487 | 1189968.4121 | 2659566.6711 | 1189966.6239 | 2659563.4406 | 1189964.0237 | 2659561.2817 | 1189963.324 | 2659559.3817 | 1189963.4385 | 2659557.4006 | 1189964.0303 | 2659555.2909 | 1189965.2878 | 2659553.2354 | 1189967.2351 | 2659546.0281 | 1189976.2784
9 | 2659449.7169 | 1189950.4638 | 2659321.8432 | 1189850.7083
10 | 2659254.4123 | 1189844.6301 | 2659270.9227 | 1189833.4012
11 | 2659291.8461 | 1189811.2639 | 2659284.4398 | 1189816.7604 | 2659282.775 | 1189818.5338 | 2659281.7286 | 1189820.2356 | 2659280.0879 | 1189824.1882 | 2659278.4586 | 1189826.9959 | 2659276.1215 | 1189829.6521 | 2659273.7238 | 1189831.4961 | 2659270.9227 | 1189833.4012
12 | 2659291.8461 | 1189811.2639 | 2659304.6526 | 1189830.3127 | 2659313.0918 | 1189840.6355
13 | 2659313.0918 | 1189840.6355 | 2659319.8194 | 1189828.2061 | 2659331.2555 | 1189812.3882 | 2659337.4464 | 1189804.0892 | 2659339.3678 | 1189800.295 | 2659340.1788 | 1189797.7237 | 2659340.3907 | 1189795.5802 | 2659340.2106 | 1189793.744 | 2659338.9773 | 1189791.2192 | 2659335.0328 | 1189785.6279
14 | 2659313.0918 | 1189840.6355 | 2659321.8432 | 1189850.7083
15 | 2659333.4037 | 1189762.7735 | 2659332.3496 | 1189765.8613 | 2659331.0427 | 1189770.7623 | 2659330.3601 | 1189776.5366 | 2659330.4173 | 1189778.4605 | 2659331.1106 | 1189780.0683 | 2659335.0328 | 1189785.6279
16 | 2659512.3746 | 1189875.7484 | 2659513.4269 | 1189874.5627
17 | 2659525.8949 | 1189864.5492 | 2659520.4671 | 1189866.6297 | 2659513.4269 | 1189874.5627
18 | 2659333.4037 | 1189762.7735 | 2659302.4184 | 1189682.4729
19 | 2659599.7493 | 1190035.1922 | 2659619.2336 | 1190009.9606 | 2659620.0663 | 1190008.279 | 2659620.564 | 1190005.7825 | 2659620.5998 | 1190002.1919 | 2659619.9635 | 1189997.9276 | 2659619.0516 | 1189994.5388 | 2659617.6499 | 1189992.0901 | 2659615.2984 | 1189989.2985 | 2659612.4459 | 1189986.7973
20 | 2659599.7493 | 1190035.1922 | 2659602.5249 | 1190037.5211 | 2659606.4863 | 1190041.007 | 2659636.6911 | 1190003.6975 | 2659656.5763 | 1189977.2804
21 | 2659656.5763 | 1189977.2804 | 2659673.3182 | 1189958.1675
22 | 2659656.5763 | 1189977.2804 | 2659642.5724 | 1189965.2616
23 | 2659718.0337 | 1189907.1195 | 2659673.3182 | 1189958.1675
24 | 2659642.5724 | 1189965.2616 | 2659621.5968 | 1189947.2594 | 2659604.21 | 1189926.4967 | 2659601.2252 | 1189923.9332
25 | 2659601.2252 | 1189923.9332 | 2659567.9423 | 1189895.3483
26 | 2659545.1983 | 1189875.8147 | 2659567.9423 | 1189895.3483
27 | 2659545.1983 | 1189875.8147 | 2659533.8038 | 1189866.0286 | 2659529.8257 | 1189864.2214 | 2659525.8949 | 1189864.5492 | 2659525.8949 | 1189864.5492
28 | 2659718.0337 | 1189907.1195 | 2659713.9016 | 1189900.8747 | 2659704.1695 | 1189891.8058 | 2659694.8323 | 1189885.1868 | 2659687.6923 | 1189883.0811 | 2659679.9443 | 1189880.7581 | 2659677.7383 | 1189879.2268
29 | 2659670.9434 | 1189855.7114 | 2659669.8999 | 1189861.6916 | 2659666.9753 | 1189868.1884 | 2659667.3545 | 1189871.4607 | 2659675.4757 | 1189877.6562 | 2659677.7383 | 1189879.2268
30 | 2659302.4184 | 1189682.4729 | 2659320.5046 | 1189669.7893 | 2659331.8474 | 1189662.642 | 2659343.3716 | 1189661.8223 | 2659365.7224 | 1189658.9978 | 2659377.2235 | 1189660.5126 | 2659377.2636 | 1189660.5326
31 | 2659625.9757 | 1189458.8662 | 2659625.2685 | 1189470.6685 | 2659621.36 | 1189483.2812 | 2659620.1642 | 1189495.3762 | 2659621.5718 | 1189516.3799 | 2659620.1149 | 1189527.1271 | 2659614.1096 | 1189534.327 | 2659594.6255 | 1189538.7134
32 | 2659616.5982 | 1189614.1229 | 2659599.5384 | 1189615.1837 | 2659605.833 | 1189578.9145 | 2659605.1103 | 1189570.3024 | 2659593.5154 | 1189542.2044 | 2659594.6255 | 1189538.7134 | 2659594.6255 | 1189538.7134
33 | 2659616.5982 | 1189614.1229 | 2659404.6041 | 1189645.2792
34 | 2659404.6041 | 1189645.2792 | 2659407.3949 | 1189651.2065 | 2659403.7804 | 1189659.6088 | 2659396.6901 | 1189663.9854 | 2659385.4046 | 1189664.5738 | 2659377.2636 | 1189660.5326

## bus_geodata
| x | y | coords
0 | 2659502.7363 | 1189994.1547
1 | 2659502.1782 | 1189994.8657
2 | 2659510.7616 | 1189979.8868
3 | 2659497.3873 | 1189997.3417
4 | 2659533.8518 | 1189991.5563
5 | 2659490.5828 | 1189970.1608
6 | 2659408.9784 | 1190018.0315
7 | 2659546.0281 | 1189976.2784
8 | 2659449.7169 | 1189950.4638
9 | 2659254.4123 | 1189844.6301
10 | 2659270.9227 | 1189833.4012
11 | 2659291.8461 | 1189811.2639
12 | 2659313.0918 | 1189840.6355
13 | 2659335.0328 | 1189785.6279
14 | 2659321.8432 | 1189850.7083
15 | 2659512.3746 | 1189875.7484
16 | 2659513.4269 | 1189874.5627
17 | 2659333.4037 | 1189762.7735
18 | 2659612.4459 | 1189986.7973
19 | 2659599.7493 | 1190035.1922
20 | 2659656.5763 | 1189977.2804
21 | 2659673.3182 | 1189958.1675
22 | 2659642.5724 | 1189965.2616
23 | 2659601.2252 | 1189923.9332
24 | 2659567.9423 | 1189895.3483
25 | 2659545.1983 | 1189875.8147
26 | 2659718.0337 | 1189907.1195
27 | 2659677.7383 | 1189879.2269
28 | 2659670.9434 | 1189855.7114
29 | 2659525.8949 | 1189864.5492
30 | 2659302.4184 | 1189682.4729
31 | 2659625.9757 | 1189458.8662
32 | 2659594.6255 | 1189538.7134
33 | 2659616.5982 | 1189614.1229
34 | 2659404.6041 | 1189645.2792
35 | 2659377.2636 | 1189660.5326
36 | 2659449.7169 | 1189950.4638

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98629 | -0.096023 | 0.00062129 | 0.00015571
1 | 0.98629 | -0.096034 | 0.00014777 | 3.7034e-05
2 | 0.98634 | -0.095724 | 0 | 0
3 | 0.98629 | -0.09609 | 0.00013139 | 3.2929e-05
4 | 0.98695 | -0.091356 | 0 | 0
5 | 0.98583 | -0.099314 | 0.0068403 | 0.0017143
6 | 0.98616 | -0.097021 | 0.00086629 | 0.00021711
7 | 0.98742 | -0.088053 | 0.00065262 | 0.00016356
8 | 0.98503 | -0.105 | 0 | 0
9 | 0.98144 | -0.1305 | 0.0011637 | 0.00029166
10 | 0.98147 | -0.13026 | 0.0015515 | 0.00038885
11 | 0.98159 | -0.12938 | 0 | 0
12 | 0.98174 | -0.12836 | 0 | 0
13 | 0.97996 | -0.14101 | 0.0017795 | 0.00044598
14 | 0.98216 | -0.12538 | 0.0027504 | 0.00068931
15 | 0.99985 | -0.0010414 | 0.0049496 | 0.0012405
16 | 0.99986 | -0.00096305 | 0.00092557 | 0.00023197
17 | 0.97935 | -0.14539 | 0.0044476 | 0.0011147
18 | 0.98934 | -0.074495 | 0.00153 | 0.00038346
19 | 0.99082 | -0.064099 | 0 | 0
20 | 0.99311 | -0.048022 | 0 | 0
21 | 0.99288 | -0.049652 | 0.0026304 | 0.00065923
22 | 0.99367 | -0.044141 | 0.0094089 | 0.0023581
23 | 0.99583 | -0.029054 | 0.00080225 | 0.00020106
24 | 0.99746 | -0.017633 | 0.010457 | 0.0026208
25 | 0.99881 | -0.0082811 | 0.0087489 | 0.0021927
26 | 0.99252 | -0.052197 | 0 | 0
27 | 0.99226 | -0.054088 | 0.0018633 | 0.00046699
28 | 0.99218 | -0.054634 | 0.0018289 | 0.00045836
29 | 1 | 0 | -0.078308 | -0.019505
30 | 0.97777 | -0.15672 | 0 | 0
31 | 0.97257 | -0.19409 | 0.0037675 | 0.00094423
32 | 0.97312 | -0.19017 | 0.00069455 | 0.00017407
33 | 0.97375 | -0.18562 | 0.002013 | 0.00050451
34 | 0.97578 | -0.17098 | 0.0010991 | 0.00027546
35 | 0.97627 | -0.16744 | 0.0050057 | 0.0012545
36 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0011456 | 0.00028571 | -0.0011456 | -0.00028572 | 1.6837e-09 | -1.0888e-08 | 0.0017278 | 0.0017278 | 0.0017278 | 0.98629 | -0.096023 | 0.98629 | -0.096034 | 0.63993
1 | -0.0017669 | -0.00044142 | 0.0017669 | 0.00044124 | 7.2688e-08 | -1.8135e-07 | 0.0026652 | 0.0026651 | 0.0026652 | 0.98629 | -0.096023 | 0.98634 | -0.095724 | 0.98709
2 | 0.0009978 | 0.00024869 | -0.00099779 | -0.00024876 | 7.7004e-09 | -6.6579e-08 | 0.0015049 | 0.0015049 | 0.0015049 | 0.98629 | -0.096034 | 0.98629 | -0.09609 | 0.55737
3 | -0.033097 | -0.0083065 | 0.033117 | 0.0083135 | 2.0081e-05 | 7.0643e-06 | 0.049936 | 0.049935 | 0.049936 | 0.98634 | -0.095724 | 0.98695 | -0.091356 | 9.2473
4 | 0.03133 | 0.0078652 | -0.031315 | -0.0078598 | 1.5617e-05 | 5.4349e-06 | 0.04727 | 0.047271 | 0.047271 | 0.98634 | -0.095724 | 0.98583 | -0.099314 | 8.7538
5 | 0.0008664 | 0.00021583 | -0.00086629 | -0.00021711 | 1.1098e-07 | -1.286e-06 | 0.0013067 | 0.0013072 | 0.0013072 | 0.98629 | -0.09609 | 0.98616 | -0.097021 | 0.48413
6 | -0.033117 | -0.0083135 | 0.033132 | 0.0083189 | 1.5199e-05 | 5.3462e-06 | 0.049935 | 0.049935 | 0.049935 | 0.98695 | -0.091356 | 0.98742 | -0.088053 | 9.2473
7 | 0.024474 | 0.0061455 | -0.024455 | -0.0061392 | 1.932e-05 | 6.275e-06 | 0.036946 | 0.036946 | 0.036946 | 0.98583 | -0.099314 | 0.98503 | -0.105 | 6.8419
8 | -0.033785 | -0.0084825 | 0.033849 | 0.008505 | 6.3744e-05 | 2.2497e-05 | 0.050919 | 0.050918 | 0.050919 | 0.98742 | -0.088053 | 0.98934 | -0.074495 | 9.4294
9 | 0.024455 | 0.0061392 | -0.024386 | -0.0061167 | 6.9074e-05 | 2.245e-05 | 0.036946 | 0.036948 | 0.036948 | 0.98503 | -0.105 | 0.98216 | -0.12538 | 6.8422
10 | -0.0011637 | -0.00029166 | 0.0011638 | 0.00029142 | 3.8786e-08 | -2.3741e-07 | 0.0017644 | 0.0017643 | 0.0017644 | 0.98144 | -0.1305 | 0.98147 | -0.13026 | 0.65349
11 | -0.0027153 | -0.00068027 | 0.0027156 | 0.00068 | 3.2917e-07 | -2.6685e-07 | 0.0041166 | 0.0041165 | 0.0041166 | 0.98147 | -0.13026 | 0.98159 | -0.12938 | 1.5247
12 | -0.0027156 | -0.00068 | 0.002716 | 0.00067969 | 3.8334e-07 | -3.1092e-07 | 0.0041165 | 0.0041163 | 0.0041165 | 0.98159 | -0.12938 | 0.98174 | -0.12836 | 1.5246
13 | 0.018911 | 0.0047445 | -0.018878 | -0.0047325 | 3.3125e-05 | 1.1925e-05 | 0.028665 | 0.028665 | 0.028665 | 0.98174 | -0.12836 | 0.97996 | -0.14101 | 10.6166
14 | -0.021627 | -0.0054242 | 0.021636 | 0.0054274 | 8.9473e-06 | 3.2725e-06 | 0.032781 | 0.032781 | 0.032781 | 0.98174 | -0.12836 | 0.98216 | -0.12538 | 12.1411
15 | 0.017098 | 0.0042866 | -0.017088 | -0.0042829 | 1.0359e-05 | 3.6743e-06 | 0.025963 | 0.025963 | 0.025963 | 0.97996 | -0.14101 | 0.97935 | -0.14539 | 9.6159
16 | -0.0049496 | -0.0012405 | 0.0049497 | 0.0012405 | 5.368e-08 | -1.4721e-10 | 0.0073662 | 0.0073662 | 0.0073662 | 0.99985 | -0.0010414 | 0.99986 | -0.00096305 | 2.7282
17 | -0.0058752 | -0.0014725 | 0.005876 | 0.0014725 | 7.8329e-07 | 8.5885e-08 | 0.0087437 | 0.0087436 | 0.0087437 | 0.99986 | -0.00096305 | 1 | 0 | 3.2384
18 | 0.01264 | 0.0031682 | -0.01262 | -0.0031617 | 1.981e-05 | 6.5381e-06 | 0.019205 | 0.019206 | 0.019206 | 0.97935 | -0.14539 | 0.97777 | -0.15672 | 7.1132
19 | -0.035379 | -0.0088884 | 0.03543 | 0.0089066 | 5.1233e-05 | 1.8214e-05 | 0.053219 | 0.053219 | 0.053219 | 0.98934 | -0.074495 | 0.99082 | -0.064099 | 9.8554
20 | -0.03543 | -0.0089066 | 0.03551 | 0.0089349 | 7.9499e-05 | 2.8254e-05 | 0.053219 | 0.053218 | 0.053219 | 0.99082 | -0.064099 | 0.99311 | -0.048022 | 9.8553
21 | 0.0063264 | 0.0015838 | -0.0063249 | -0.0015836 | 1.4244e-06 | 2.1916e-07 | 0.0094784 | 0.0094785 | 0.0094785 | 0.99311 | -0.048022 | 0.99288 | -0.049652 | 3.5106
22 | -0.041836 | -0.010519 | 0.041859 | 0.010527 | 2.2633e-05 | 8.227e-06 | 0.062696 | 0.062696 | 0.062696 | 0.99311 | -0.048022 | 0.99367 | -0.044141 | 11.6104
23 | 0.0036946 | 0.00092436 | -0.0036933 | -0.00092474 | 1.2981e-06 | -3.7811e-07 | 0.0055364 | 0.0055368 | 0.0055368 | 0.99288 | -0.049652 | 0.99252 | -0.052197 | 2.0506
24 | -0.051267 | -0.012885 | 0.051375 | 0.012925 | 0.0001079 | 3.9978e-05 | 0.076786 | 0.076785 | 0.076786 | 0.99367 | -0.044141 | 0.99583 | -0.029054 | 14.2196
25 | -0.052178 | -0.013126 | 0.052261 | 0.013157 | 8.3246e-05 | 3.0874e-05 | 0.077984 | 0.077984 | 0.077984 | 0.99583 | -0.029054 | 0.99746 | -0.017633 | 14.4415
26 | -0.062718 | -0.015778 | 0.0628 | 0.015808 | 8.1921e-05 | 3.0724e-05 | 0.093584 | 0.093583 | 0.093584 | 0.99746 | -0.017633 | 0.99881 | -0.0082811 | 17.3303
27 | -0.071549 | -0.018001 | 0.071632 | 0.018032 | 8.2755e-05 | 3.1218e-05 | 0.10662 | 0.10662 | 0.10662 | 0.99881 | -0.0082811 | 1 | 0 | 19.7439
28 | 0.0036933 | 0.00092474 | -0.0036923 | -0.00092502 | 9.6518e-07 | -2.8066e-07 | 0.0055368 | 0.005537 | 0.005537 | 0.99252 | -0.052197 | 0.99226 | -0.054088 | 2.0507
29 | 0.001829 | 0.00045803 | -0.0018289 | -0.00045836 | 1.3829e-07 | -3.2729e-07 | 0.0027427 | 0.0027428 | 0.0027428 | 0.99226 | -0.054088 | 0.99218 | -0.054634 | 1.0159
30 | 0.01262 | 0.0031617 | -0.012602 | -0.0031555 | 1.8696e-05 | 6.1734e-06 | 0.019206 | 0.019206 | 0.019206 | 0.97777 | -0.15672 | 0.97627 | -0.16744 | 7.1133
31 | -0.0037675 | -0.00094423 | 0.0037696 | 0.00094379 | 2.0405e-06 | -4.3728e-07 | 0.0057642 | 0.0057638 | 0.0057642 | 0.97257 | -0.19409 | 0.97312 | -0.19017 | 2.1349
32 | -0.0044641 | -0.0011179 | 0.0044669 | 0.0011177 | 2.8085e-06 | -1.2076e-07 | 0.0068258 | 0.0068254 | 0.0068258 | 0.97312 | -0.19017 | 0.97375 | -0.18562 | 2.5281
33 | -0.0064799 | -0.0016223 | 0.006493 | 0.0016246 | 1.3107e-05 | 2.3703e-06 | 0.0099016 | 0.0099006 | 0.0099016 | 0.97375 | -0.18562 | 0.97578 | -0.17098 | 3.6672
34 | -0.0075922 | -0.0019001 | 0.0075959 | 0.001901 | 3.7147e-06 | 8.7358e-07 | 0.011577 | 0.011576 | 0.011577 | 0.97578 | -0.17098 | 0.97627 | -0.16744 | 4.2877

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.079585 | 0.019825

## res_load
| p_mw | q_mvar
0 | 0.00062129 | 0.00015571
1 | 0.00014777 | 3.7034e-05
2 | 0.00013139 | 3.2929e-05
3 | 0.0068403 | 0.0017143
4 | 0.00086629 | 0.00021711
5 | 0.00065262 | 0.00016356
6 | 0.0011637 | 0.00029166
7 | 0.0015515 | 0.00038885
8 | 0.0017795 | 0.00044598
9 | 0.0027504 | 0.00068931
10 | 0.0049496 | 0.0012405
11 | 0.00092557 | 0.00023197
12 | 0.0044476 | 0.0011147
13 | 0.00153 | 0.00038346
14 | 0.0026304 | 0.00065923
15 | 0.0094089 | 0.0023581
16 | 0.00080225 | 0.00020106
17 | 0.010457 | 0.0026208
18 | 0.0087489 | 0.0021927
19 | 0.0018633 | 0.00046699
20 | 0.0018289 | 0.00045836
21 | 0.0012779 | 0.00032027
22 | 0.0037675 | 0.00094423
23 | 0.00069455 | 0.00017407
24 | 0.002013 | 0.00050451
25 | 0.0010991 | 0.00027546
26 | 0.0050057 | 0.0012545

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1