## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1406-26_1_3_node_129 | 0.4 | n |  | TRUE
1 | bus_LV_1406-26_1_3_node_130 | 0.4 | n |  | TRUE
2 | bus_LV_1406-26_1_3_node_132 | 0.4 | n |  | TRUE
3 | bus_LV_1406-26_1_3_node_134 | 0.4 | n |  | TRUE
4 | bus_LV_1406-26_1_3_node_133 | 0.4 | n |  | TRUE
5 | bus_LV_1406-26_1_3_node_137 | 0.4 | n |  | TRUE
6 | bus_LV_1406-26_1_3_node_139 | 0.4 | n |  | TRUE
7 | bus_LV_1406-26_1_3_node_123 | 0.4 | n |  | TRUE
8 | bus_LV_1406-26_1_3_node_135 | 0.4 | n |  | TRUE
9 | bus_LV_1406-26_1_3_node_136 | 0.4 | n |  | TRUE
10 | bus_LV_1406-26_1_3_node_138 | 0.4 | n |  | TRUE
11 | bus_LV_1406-26_1_3_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_1406-26_1_3_node_12 | 0.4 | n |  | TRUE
13 | bus_LV_1406-26_1_3_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_1406-26_1_3_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_1406-26_1_3_node_140 | 0.4 | n |  | TRUE
16 | bus_LV_1406-26_1_3_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_1406-26_1_3_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_1406-26_1_3_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_1406-26_1_3_node_18 | 0.4 | n |  | TRUE
20 | bus_LV_1406-26_1_3_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_1406-26_1_3_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_1406-26_1_3_node_100 | 0.4 | n |  | TRUE
23 | bus_LV_1406-26_1_3_node_141 | 0.4 | n |  | TRUE
24 | bus_LV_1406-26_1_3_node_142 | 0.4 | n |  | TRUE
25 | bus_LV_1406-26_1_3_node_122 | 0.4 | n |  | TRUE
26 | bus_LV_1406-26_1_3_node_144 | 0.4 | n |  | TRUE
27 | bus_LV_1406-26_1_3_node_145 | 0.4 | n |  | TRUE
28 | bus_LV_1406-26_1_3_node_101 | 0.4 | n |  | TRUE
29 | bus_LV_1406-26_1_3_node_97 | 0.4 | n |  | TRUE
30 | bus_LV_1406-26_1_3_node_98 | 0.4 | n |  | TRUE
31 | bus_LV_1406-26_1_3_node_119 | 0.4 | n |  | TRUE
32 | bus_LV_1406-26_1_3_node_120 | 0.4 | n |  | TRUE
33 | bus_LV_1406-26_1_3_node_121 | 0.4 | n |  | TRUE
34 | bus_MV_0_node_140 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1406-26_1_3_load_129 | 0 | 0.0060957 | 0.0015277 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1406-26_1_3_load_130 | 1 | 0.0035485 | 0.00088935 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1406-26_1_3_load_137 | 5 | 0.0042569 | 0.0010669 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1406-26_1_3_load_139 | 6 | 0.0052532 | 0.0013166 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1406-26_1_3_load_123 | 7 | 0.0023449 | 0.00058769 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1406-26_1_3_load_135 | 8 | 0.0025688 | 0.0006438 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1406-26_1_3_load_136 | 9 | 0.0028754 | 0.00072065 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1406-26_1_3_load_138 | 10 | 0.0028629 | 0.00071752 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1406-26_1_3_load_11 | 11 | 0.0049621 | 0.0012436 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1406-26_1_3_load_12 | 12 | 0.00070922 | 0.00017775 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1406-26_1_3_load_14 | 14 | 0.0043286 | 0.0010849 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1406-26_1_3_load_140 | 15 | 0.0020083 | 0.00050333 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1406-26_1_3_load_15 | 16 | 0.0051276 | 0.0012851 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1406-26_1_3_load_18 | 19 | 0.0011877 | 0.00029766 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1406-26_1_3_load_19 | 20 | 0.0006303 | 0.00015797 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1406-26_1_3_load_20 | 21 | 0.00041233 | 0.00010334 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1406-26_1_3_load_100 | 22 | 0.00045943 | 0.00011514 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1406-26_1_3_load_142 | 24 | 0.0044122 | 0.0011058 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1406-26_1_3_load_122 | 25 | 0.00061913 | 0.00015517 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1406-26_1_3_load_145 | 27 | 0.0029867 | 0.00074853 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1406-26_1_3_load_101 | 28 | 0.00042877 | 0.00010746 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1406-26_1_3_load_97 | 29 | 0.0007157 | 0.00017937 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1406-26_1_3_load_119 | 31 | 0.0017742 | 0.00044467 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1406-26_1_3_load_120 | 32 | 0.0036916 | 0.0009252 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 15 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1406-26_1_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0025962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1406-26_1_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.017067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1406-26_1_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.041317 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1406-26_1_3_line_3 | NAYY 4x150 SE | 3 | 7 | 0.047996 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1406-26_1_3_line_4 | NAYY 4x150 SE | 3 | 8 | 0.013099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1406-26_1_3_line_5 | NAYY 4x150 SE | 4 | 5 | 0.034763 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1406-26_1_3_line_6 | NAYY 4x150 SE | 4 | 6 | 0.0039313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1406-26_1_3_line_7 | NAYY 4x150 SE | 5 | 9 | 0.035057 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1406-26_1_3_line_8 | NAYY 4x150 SE | 6 | 10 | 0.030612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1406-26_1_3_line_9 | NAYY 4x150 SE | 7 | 33 | 0.0021774 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1406-26_1_3_line_10 | NAYY 4x150 SE | 8 | 9 | 0.031102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1406-26_1_3_line_11 | NAYY 4x150 SE | 11 | 12 | 0.12568 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1406-26_1_3_line_12 | NAYY 4x150 SE | 11 | 13 | 0.018991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1406-26_1_3_line_13 | NAYY 4x150 SE | 12 | 14 | 0.32152 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1406-26_1_3_line_14 | NAYY 4x150 SE | 12 | 15 | 0.32929 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1406-26_1_3_line_15 | NAYY 4x150 SE | 13 | 16 | 0.047627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1406-26_1_3_line_16 | NAYY 4x150 SE | 15 | 23 | 0.019883 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1406-26_1_3_line_17 | NAYY 4x150 SE | 15 | 24 | 0.01909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1406-26_1_3_line_18 | NAYY 4x150 SE | 16 | 17 | 0.061581 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1406-26_1_3_line_19 | NAYY 4x150 SE | 17 | 21 | 0.12385 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1406-26_1_3_line_20 | NAYY 4x150 SE | 17 | 18 | 0.17484 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1406-26_1_3_line_21 | NAYY 4x150 SE | 18 | 19 | 0.014118 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1406-26_1_3_line_22 | NAYY 4x150 SE | 18 | 20 | 0.042832 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1406-26_1_3_line_23 | NAYY 4x150 SE | 20 | 22 | 0.030415 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1406-26_1_3_line_24 | NAYY 4x150 SE | 22 | 30 | 0.12908 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1406-26_1_3_line_25 | NAYY 4x150 SE | 23 | 25 | 0.0068584 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1406-26_1_3_line_26 | NAYY 4x150 SE | 25 | 33 | 0.057859 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1406-26_1_3_line_27 | NAYY 4x150 SE | 26 | 27 | 0.019796 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1406-26_1_3_line_28 | NAYY 4x150 SE | 26 | 28 | 0.15738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1406-26_1_3_line_29 | NAYY 4x150 SE | 28 | 30 | 0.090832 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1406-26_1_3_line_30 | NAYY 4x150 SE | 29 | 30 | 0.15609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1406-26_1_3_line_31 | NAYY 4x150 SE | 31 | 32 | 0.04236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1406-26_1_3_line_32 | NAYY 4x150 SE | 32 | 33 | 0.044894 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1406-26_1_3_trafo_140 | 0.25 MVA 20/0.4 kV | 34 | 15 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2661455.2988 | 1191827.6914 | 2661456.1755 | 1191830.1351
1 | 2661461.9388 | 1191846.1993 | 2661456.1755 | 1191830.1351
2 | 2661461.9388 | 1191846.1993 | 2661469.2392 | 1191866.5527 | 2661477.5562 | 1191884.415
3 | 2661477.5562 | 1191884.415 | 2661486.6453 | 1191902.8079 | 2661488.3434 | 1191905.2267 | 2661490.7421 | 1191906.9746 | 2661494.873 | 1191908.5735 | 2661498.7032 | 1191909.0131 | 2661503.0422 | 1191908.1683 | 2661506.9403 | 1191906.4518 | 2661510.9251 | 1191904.17
4 | 2661477.5562 | 1191884.415 | 2661490.4223 | 1191881.9559
5 | 2661509.231 | 1191791.1421 | 2661509.9356 | 1191803.4454 | 2661508.3992 | 1191825.8319
6 | 2661509.231 | 1191791.1421 | 2661509.0051 | 1191787.2173
7 | 2661508.3992 | 1191825.8319 | 2661505.9991 | 1191860.8064
8 | 2661505.1369 | 1191756.8794 | 2661508.5194 | 1191778.7833 | 2661509.0051 | 1191787.2173
9 | 2661512.8146 | 1191903.088 | 2661510.9251 | 1191904.17
10 | 2661490.4223 | 1191881.9559 | 2661500.2433 | 1191880.0789 | 2661504.3479 | 1191876.0743 | 2661505.47 | 1191868.5148 | 2661505.9991 | 1191860.8064
11 | 2661990.5102 | 1191887.5479 | 2661985.9895 | 1191888.3596 | 2661968.4744 | 1191895.3045 | 2661956.1954 | 1191900.9251 | 2661938.4124 | 1191912.3922 | 2661926.5905 | 1191920.9971 | 2661907.1867 | 1191938.8179 | 2661899.8215 | 1191946.2571 | 2661895.4893 | 1191952.3381 | 2661891.219 | 1191959.8093 | 2661891.2005 | 1191959.8793
12 | 2662009.3339 | 1191885.3774 | 2662000.4482 | 1191885.7634 | 2661990.5102 | 1191887.5479
13 | 2661891.2005 | 1191959.8793 | 2661889.7036 | 1191965.5414 | 2661888.0858 | 1191972.3286 | 2661887.9813 | 1191977.2748 | 2661888.7845 | 1191983.6424 | 2661891.3877 | 1191991.4071 | 2661900.9717 | 1192020.7787 | 2661903.9027 | 1192027.0682 | 2661907.9374 | 1192032.791 | 2661923.1165 | 1192048.2013 | 2661932.0989 | 1192058.3334 | 2661974.3317 | 1192105.5978 | 2662072.7887 | 1192213.0519
14 | 2661891.2005 | 1191959.8793 | 2661577.3039 | 1191860.3707
15 | 2662009.3339 | 1191885.3774 | 2662009.1452 | 1191891.0787 | 2662011.3574 | 1191894.6259 | 2662024.3739 | 1191903.1879 | 2662046.0168 | 1191907.9581
16 | 2661571.1487 | 1191878.9069 | 2661571.4504 | 1191872.5508 | 2661572.7791 | 1191869.3738 | 2661577.3039 | 1191860.3707
17 | 2661583.1576 | 1191842.465 | 2661581.9399 | 1191851.1464 | 2661577.3039 | 1191860.3707
18 | 2662104.7316 | 1191900.6528 | 2662094.7484 | 1191906.8862 | 2662084.0721 | 1191910.8556 | 2662071.7942 | 1191911.9511 | 2662050.1519 | 1191908.8694 | 2662046.0168 | 1191907.9581
19 | 2662104.7316 | 1191900.6528 | 2662132.1332 | 1191940.8603 | 2662171.8204 | 1192004.7227
20 | 2662234.4994 | 1191860.6883 | 2662224.2609 | 1191863.5947 | 2662215.3961 | 1191864.9033 | 2662094.3991 | 1191868.5493 | 2662095.0604 | 1191877.5614 | 2662096.2992 | 1191883.0774 | 2662104.7316 | 1191900.6528
21 | 2662234.4994 | 1191860.6883 | 2662236.97 | 1191856.2448 | 2662237.9569 | 1191852.9865 | 2662238.1525 | 1191847.3606
22 | 2662234.4994 | 1191860.6883 | 2662263.5241 | 1191879.6566 | 2662270.3983 | 1191884.0506
23 | 2662270.3983 | 1191884.0506 | 2662296.0257 | 1191900.4314
24 | 2662404.564 | 1191970.2997 | 2662339.6059 | 1191928.2876 | 2662296.0257 | 1191900.4314
25 | 2661571.1487 | 1191878.9069 | 2661568.0322 | 1191878.7415 | 2661565.0653 | 1191878.8666 | 2661564.3071 | 1191878.9885
26 | 2661512.8146 | 1191903.088 | 2661528.4734 | 1191890.5194 | 2661532.8582 | 1191888.1853 | 2661540.1974 | 1191885.4592 | 2661560.9722 | 1191879.5249 | 2661564.3071 | 1191878.9885
27 | 2662285.2444 | 1192187.2382 | 2662290.9191 | 1192199.4043 | 2662292.8779 | 1192205.4668
28 | 2662285.2444 | 1192187.2382 | 2662355.4941 | 1192064.3206 | 2662358.2135 | 1192052.8311 | 2662360.0658 | 1192049.2923
29 | 2662404.564 | 1191970.2997 | 2662393.5747 | 1191985.2716 | 2662360.0658 | 1192049.2923
30 | 2662404.564 | 1191970.2997 | 2662404.7436 | 1191963.3197 | 2662403.6355 | 1191956.2597 | 2662400.0198 | 1191951.3414 | 2662369.2592 | 1191922.7265 | 2662360.787 | 1191914.8893 | 2662356.4773 | 1191909.2634 | 2662348.1123 | 1191889.676 | 2662342.7797 | 1191875.3789 | 2662339.6382 | 1191867.386 | 2662338.6401 | 1191860.7384 | 2662340.3663 | 1191847.9824 | 2662343.5797 | 1191838.0157
31 | 2661504.128 | 1191989.707 | 2661504.0997 | 1191988.481 | 2661509.2181 | 1191947.6673
32 | 2661512.8146 | 1191903.088 | 2661513.4797 | 1191908.1088 | 2661513.5501 | 1191913.1235 | 2661509.2181 | 1191947.6673

## bus_geodata
| x | y | coords
0 | 2661455.2988 | 1191827.6914
1 | 2661456.1755 | 1191830.1351
2 | 2661461.9388 | 1191846.1993
3 | 2661477.5562 | 1191884.415
4 | 2661509.231 | 1191791.1421
5 | 2661508.3992 | 1191825.8319
6 | 2661509.0051 | 1191787.2173
7 | 2661510.9251 | 1191904.1699
8 | 2661490.4223 | 1191881.9559
9 | 2661505.9991 | 1191860.8064
10 | 2661505.1369 | 1191756.8794
11 | 2661990.5102 | 1191887.5479
12 | 2661891.2005 | 1191959.8793
13 | 2662009.3339 | 1191885.3774
14 | 2662072.7887 | 1192213.0519
15 | 2661577.3039 | 1191860.3707
16 | 2662046.0168 | 1191907.9581
17 | 2662104.7316 | 1191900.6528
18 | 2662234.4994 | 1191860.6883
19 | 2662238.1525 | 1191847.3606
20 | 2662270.3983 | 1191884.0506
21 | 2662171.8204 | 1192004.7227
22 | 2662296.0257 | 1191900.4314
23 | 2661571.1487 | 1191878.907
24 | 2661583.1576 | 1191842.465
25 | 2661564.3071 | 1191878.9885
26 | 2662285.2444 | 1192187.2382
27 | 2662292.8779 | 1192205.4668
28 | 2662360.0658 | 1192049.2923
29 | 2662343.5797 | 1191838.0157
30 | 2662404.564 | 1191970.2997
31 | 2661504.128 | 1191989.707
32 | 2661509.2181 | 1191947.6673
33 | 2661512.8146 | 1191903.088
34 | 2661577.3039 | 1191860.3707

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99288 | -0.049927 | 0.0060957 | 0.0015277
1 | 0.9929 | -0.049767 | 0.0035485 | 0.00088935
2 | 0.99314 | -0.048101 | 0 | 0
3 | 0.99371 | -0.04407 | 0 | 0
4 | 0.99166 | -0.058497 | 0 | 0
5 | 0.99207 | -0.055633 | 0.0042569 | 0.0010669
6 | 0.99162 | -0.058821 | 0.0052532 | 0.0013166
7 | 0.9956 | -0.030762 | 0.0023449 | 0.00058769
8 | 0.99337 | -0.046431 | 0.0025688 | 0.0006438
9 | 0.99269 | -0.051235 | 0.0028754 | 0.00072065
10 | 0.99149 | -0.059711 | 0.0028629 | 0.00071752
11 | 0.98647 | -0.095291 | 0.0049621 | 0.0012436
12 | 0.98954 | -0.073424 | 0.00070922 | 0.00017775
13 | 0.98614 | -0.097638 | 0 | 0
14 | 0.98754 | -0.087688 | 0.0043286 | 0.0010849
15 | 1 | 0 | -0.063616 | -0.015789
16 | 0.98531 | -0.10353 | 0.0051276 | 0.0012851
17 | 0.9847 | -0.10791 | 0 | 0
18 | 0.98308 | -0.11959 | 0 | 0
19 | 0.98305 | -0.11976 | 0.0011877 | 0.00029766
20 | 0.98275 | -0.12192 | 0.0006303 | 0.00015797
21 | 0.98463 | -0.10844 | 0.00041233 | 0.00010334
22 | 0.98255 | -0.12338 | 0.00045943 | 0.00011514
23 | 0.99898 | -0.0071377 | 0 | 0
24 | 0.99988 | -0.00084091 | 0.0044122 | 0.0011058
25 | 0.99862 | -0.009603 | 0.00061913 | 0.00015517
26 | 0.98064 | -0.13708 | 0 | 0
27 | 0.98056 | -0.1377 | 0.0029867 | 0.00074853
28 | 0.98133 | -0.13219 | 0.00042877 | 0.00010746
29 | 0.98161 | -0.13013 | 0.0007157 | 0.00017937
30 | 0.98178 | -0.12896 | 0 | 0
31 | 0.99523 | -0.03334 | 0.0017742 | 0.00044467
32 | 0.99534 | -0.032582 | 0.0036916 | 0.0009252
33 | 0.99569 | -0.030108 | 0 | 0
34 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0060957 | -0.0015277 | 0.0060959 | 0.0015278 | 1.3521e-07 | 1.8425e-08 | 0.0091356 | 0.0091356 | 0.0091356 | 0.99288 | -0.049927 | 0.9929 | -0.049767 | 3.3836
1 | -0.0096444 | -0.0024171 | 0.0096466 | 0.0024177 | 2.2248e-06 | 6.349e-07 | 0.014454 | 0.014454 | 0.014454 | 0.9929 | -0.049767 | 0.99314 | -0.048101 | 5.3532
2 | -0.0096466 | -0.0024177 | 0.009652 | 0.0024193 | 5.3859e-06 | 1.5366e-06 | 0.014454 | 0.014453 | 0.014454 | 0.99314 | -0.048101 | 0.99371 | -0.04407 | 5.3532
3 | -0.027497 | -0.0068933 | 0.027548 | 0.0069123 | 5.0777e-05 | 1.8906e-05 | 0.041175 | 0.041175 | 0.041175 | 0.99371 | -0.04407 | 0.9956 | -0.030762 | 15.2502
4 | 0.017845 | 0.0044741 | -0.017839 | -0.004472 | 5.8367e-06 | 2.0752e-06 | 0.026722 | 0.026722 | 0.026722 | 0.99371 | -0.04407 | 0.99337 | -0.046431 | 9.8971
5 | -0.0081169 | -0.0020339 | 0.0081201 | 0.0020347 | 3.2177e-06 | 7.8891e-07 | 0.012179 | 0.012179 | 0.012179 | 0.99166 | -0.058497 | 0.99207 | -0.055633 | 4.5109
6 | 0.0081169 | 0.0020339 | -0.0081165 | -0.0020338 | 3.639e-07 | 8.9243e-08 | 0.012179 | 0.012179 | 0.012179 | 0.99166 | -0.058497 | 0.99162 | -0.058821 | 4.5109
7 | -0.012377 | -0.0031016 | 0.012385 | 0.003104 | 7.5389e-06 | 2.4466e-06 | 0.018564 | 0.018564 | 0.018564 | 0.99207 | -0.055633 | 0.99269 | -0.051235 | 6.8757
8 | 0.0028633 | 0.00071726 | -0.0028629 | -0.00071752 | 3.5263e-07 | -2.5922e-07 | 0.0042965 | 0.0042966 | 0.0042966 | 0.99162 | -0.058821 | 0.99149 | -0.059711 | 1.5914
9 | -0.029892 | -0.0074999 | 0.029895 | 0.007501 | 2.7124e-06 | 1.0149e-06 | 0.04468 | 0.04468 | 0.04468 | 0.9956 | -0.030762 | 0.99569 | -0.030108 | 16.5481
10 | 0.01527 | 0.0038282 | -0.01526 | -0.0038247 | 1.0155e-05 | 3.5033e-06 | 0.022874 | 0.022874 | 0.022874 | 0.99337 | -0.046431 | 0.99269 | -0.051235 | 8.472
11 | -0.016948 | -0.0042392 | 0.016999 | 0.0042573 | 5.1243e-05 | 1.8099e-05 | 0.025562 | 0.025562 | 0.025562 | 0.98647 | -0.095291 | 0.98954 | -0.073424 | 9.4675
12 | 0.011986 | 0.0029955 | -0.011982 | -0.0029943 | 3.8726e-06 | 1.2471e-06 | 0.018077 | 0.018077 | 0.018077 | 0.98647 | -0.095291 | 0.98614 | -0.097638 | 6.6953
13 | 0.0043371 | 0.001084 | -0.0043286 | -0.0010849 | 8.533e-06 | -8.4008e-07 | 0.0065209 | 0.0065223 | 0.0065223 | 0.98954 | -0.073424 | 0.98754 | -0.087688 | 2.4157
14 | -0.022046 | -0.005519 | 0.022272 | 0.0056016 | 0.00022578 | 8.2564e-05 | 0.033149 | 0.033148 | 0.033149 | 0.98954 | -0.073424 | 1 | 0 | 12.2774
15 | 0.011982 | 0.0029943 | -0.011973 | -0.0029912 | 9.7122e-06 | 3.1283e-06 | 0.018077 | 0.018078 | 0.018078 | 0.98614 | -0.097638 | 0.98531 | -0.10353 | 6.6954
16 | 0.036131 | 0.0090819 | -0.036095 | -0.0090684 | 3.5876e-05 | 1.3538e-05 | 0.053773 | 0.053773 | 0.053773 | 1 | 0 | 0.99898 | -0.0071377 | 19.9161
17 | 0.0044127 | 0.0011057 | -0.0044122 | -0.0011058 | 5.1359e-07 | -5.2886e-08 | 0.0065661 | 0.0065662 | 0.0065662 | 1 | 0 | 0.99988 | -0.00084091 | 2.4319
18 | 0.006845 | 0.0017061 | -0.0068409 | -0.0017053 | 4.1037e-06 | 7.9449e-07 | 0.010334 | 0.010334 | 0.010334 | 0.98531 | -0.10353 | 0.9847 | -0.10791 | 3.8275
19 | 0.00041236 | 0.00010178 | -0.00041233 | -0.00010334 | 2.998e-08 | -1.5638e-06 | 0.00062257 | 0.00062313 | 0.00062313 | 0.9847 | -0.10791 | 0.98463 | -0.10844 | 0.23079
20 | 0.0064285 | 0.0016035 | -0.0064182 | -0.0016018 | 1.0291e-05 | 1.7375e-06 | 0.0097116 | 0.0097124 | 0.0097124 | 0.9847 | -0.10791 | 0.98308 | -0.11959 | 3.5972
21 | 0.0011877 | 0.0002975 | -0.0011877 | -0.00029766 | 2.8472e-08 | -1.6805e-07 | 0.0017977 | 0.0017978 | 0.0017978 | 0.98308 | -0.11959 | 0.98305 | -0.11976 | 0.66584
22 | 0.0052305 | 0.0013043 | -0.0052289 | -0.0013042 | 1.6743e-06 | 1.0107e-07 | 0.0079147 | 0.0079149 | 0.0079149 | 0.98308 | -0.11959 | 0.98275 | -0.12192 | 2.9314
23 | 0.0045985 | 0.0011462 | -0.0045976 | -0.0011462 | 9.1955e-07 | -3.1632e-08 | 0.0069606 | 0.0069607 | 0.0069607 | 0.98275 | -0.12192 | 0.98255 | -0.12338 | 2.578
24 | 0.0041382 | 0.0010311 | -0.004135 | -0.0010315 | 3.1617e-06 | -4.1755e-07 | 0.0062649 | 0.0062655 | 0.0062655 | 0.98255 | -0.12338 | 0.98178 | -0.12896 | 2.3206
25 | 0.036095 | 0.0090684 | -0.036083 | -0.0090637 | 1.2375e-05 | 4.6698e-06 | 0.053773 | 0.053773 | 0.053773 | 0.99898 | -0.0071377 | 0.99862 | -0.009603 | 19.9161
26 | 0.035464 | 0.0089085 | -0.035363 | -0.0088705 | 0.00010085 | 3.8032e-05 | 0.052851 | 0.052851 | 0.052851 | 0.99862 | -0.009603 | 0.99569 | -0.030108 | 19.5745
27 | 0.0029869 | 0.00074837 | -0.0029867 | -0.00074853 | 2.5374e-07 | -1.5213e-07 | 0.0045322 | 0.0045323 | 0.0045323 | 0.98064 | -0.13708 | 0.98056 | -0.1377 | 1.6786
28 | -0.0029869 | -0.00074837 | 0.0029889 | 0.00074716 | 2.0169e-06 | -1.2112e-06 | 0.0045322 | 0.0045315 | 0.0045322 | 0.98064 | -0.13708 | 0.98133 | -0.13219 | 1.6786
29 | -0.0034177 | -0.00085462 | 0.0034192 | 0.00085406 | 1.5217e-06 | -5.6281e-07 | 0.0051817 | 0.0051813 | 0.0051817 | 0.98133 | -0.13219 | 0.98178 | -0.12896 | 1.9191
30 | -0.0007157 | -0.00017937 | 0.00071581 | 0.00017744 | 1.1457e-07 | -1.9294e-06 | 0.0010849 | 0.0010842 | 0.0010849 | 0.98161 | -0.13013 | 0.98178 | -0.12896 | 0.40182
31 | -0.0017742 | -0.00044467 | 0.0017744 | 0.00044419 | 1.8599e-07 | -4.7897e-07 | 0.0026527 | 0.0026525 | 0.0026527 | 0.99523 | -0.03334 | 0.99534 | -0.032582 | 0.9825
32 | -0.005466 | -0.0013694 | 0.0054679 | 0.0013695 | 1.8705e-06 | 1.3571e-07 | 0.0081714 | 0.0081712 | 0.0081714 | 0.99534 | -0.032582 | 0.99569 | -0.030108 | 3.0264

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.065624 | 0.016293

## res_load
| p_mw | q_mvar
0 | 0.0060957 | 0.0015277
1 | 0.0035485 | 0.00088935
2 | 0.0042569 | 0.0010669
3 | 0.0052532 | 0.0013166
4 | 0.0023449 | 0.00058769
5 | 0.0025688 | 0.0006438
6 | 0.0028754 | 0.00072065
7 | 0.0028629 | 0.00071752
8 | 0.0049621 | 0.0012436
9 | 0.00070922 | 0.00017775
10 | 0.0043286 | 0.0010849
11 | 0.0020083 | 0.00050333
12 | 0.0051276 | 0.0012851
13 | 0.0011877 | 0.00029766
14 | 0.0006303 | 0.00015797
15 | 0.00041233 | 0.00010334
16 | 0.00045943 | 0.00011514
17 | 0.0044122 | 0.0011058
18 | 0.00061913 | 0.00015517
19 | 0.0029867 | 0.00074853
20 | 0.00042877 | 0.00010746
21 | 0.0007157 | 0.00017937
22 | 0.0017742 | 0.00044467
23 | 0.0036916 | 0.0009252

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1