## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1406-4_1_3_node_61 | 0.4 | n |  | TRUE
1 | bus_LV_1406-4_1_3_node_62 | 0.4 | n |  | TRUE
2 | bus_LV_1406-4_1_3_node_63 | 0.4 | n |  | TRUE
3 | bus_LV_1406-4_1_3_node_64 | 0.4 | n |  | TRUE
4 | bus_LV_1406-4_1_3_node_88 | 0.4 | n |  | TRUE
5 | bus_LV_1406-4_1_3_node_87 | 0.4 | n |  | TRUE
6 | bus_LV_1406-4_1_3_node_71 | 0.4 | n |  | TRUE
7 | bus_LV_1406-4_1_3_node_72 | 0.4 | n |  | TRUE
8 | bus_LV_1406-4_1_3_node_73 | 0.4 | n |  | TRUE
9 | bus_LV_1406-4_1_3_node_74 | 0.4 | n |  | TRUE
10 | bus_LV_1406-4_1_3_node_75 | 0.4 | n |  | TRUE
11 | bus_LV_1406-4_1_3_node_77 | 0.4 | n |  | TRUE
12 | bus_LV_1406-4_1_3_node_81 | 0.4 | n |  | TRUE
13 | bus_LV_1406-4_1_3_node_97 | 0.4 | n |  | TRUE
14 | bus_LV_1406-4_1_3_node_82 | 0.4 | n |  | TRUE
15 | bus_LV_1406-4_1_3_node_83 | 0.4 | n |  | TRUE
16 | bus_LV_1406-4_1_3_node_89 | 0.4 | n |  | TRUE
17 | bus_LV_1406-4_1_3_node_100 | 0.4 | n |  | TRUE
18 | bus_LV_1406-4_1_3_node_84 | 0.4 | n |  | TRUE
19 | bus_LV_1406-4_1_3_node_85 | 0.4 | n |  | TRUE
20 | bus_LV_1406-4_1_3_node_90 | 0.4 | n |  | TRUE
21 | bus_LV_1406-4_1_3_node_91 | 0.4 | n |  | TRUE
22 | bus_LV_1406-4_1_3_node_92 | 0.4 | n |  | TRUE
23 | bus_LV_1406-4_1_3_node_93 | 0.4 | n |  | TRUE
24 | bus_LV_1406-4_1_3_node_94 | 0.4 | n |  | TRUE
25 | bus_LV_1406-4_1_3_node_95 | 0.4 | n |  | TRUE
26 | bus_LV_1406-4_1_3_node_98 | 0.4 | n |  | TRUE
27 | bus_LV_1406-4_1_3_node_96 | 0.4 | n |  | TRUE
28 | bus_LV_1406-4_1_3_node_99 | 0.4 | n |  | TRUE
29 | bus_MV_0_node_92 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1406-4_1_3_load_61 | 0 | 0.00068043 | 0.00017053 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1406-4_1_3_load_63 | 2 | 0.0028662 | 0.00071834 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1406-4_1_3_load_88 | 4 | 0.00039616 | 9.9288e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1406-4_1_3_load_87 | 5 | 0.00051963 | 0.00013023 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1406-4_1_3_load_71 | 6 | 0.00037905 | 9.5e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1406-4_1_3_load_73 | 8 | 0.00044382 | 0.00011123 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1406-4_1_3_load_74 | 9 | 0.00053659 | 0.00013448 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1406-4_1_3_load_75 | 10 | 0.00032518 | 8.1497e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1406-4_1_3_load_77 | 11 | 0.00057863 | 0.00014502 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1406-4_1_3_load_81 | 12 | 0.00032419 | 8.125e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1406-4_1_3_load_97 | 13 | 0.0047961 | 0.001202 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1406-4_1_3_load_82 | 14 | 0.00050216 | 0.00012585 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1406-4_1_3_load_83 | 15 | 0.00047586 | 0.00011926 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1406-4_1_3_load_89 | 16 | 0.00023581 | 5.91e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1406-4_1_3_load_100 | 17 | 0.00022973 | 5.7576e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1406-4_1_3_load_84 | 18 | 0.00051504 | 0.00012908 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1406-4_1_3_load_85 | 19 | 0.0002231 | 5.5915e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1406-4_1_3_load_90 | 20 | 0.0036018 | 0.00090271 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1406-4_1_3_load_91 | 21 | 0.019377 | 0.0048564 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1406-4_1_3_load_94 | 24 | 0.0069459 | 0.0017408 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1406-4_1_3_load_95 | 25 | 0.0062571 | 0.0015682 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1406-4_1_3_load_98 | 26 | 0.0037008 | 0.00092752 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1406-4_1_3_load_96 | 27 | 0.003789 | 0.00094961 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1406-4_1_3_load_99 | 28 | 0.0054534 | 0.0013668 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 22 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1406-4_1_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.015669 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1406-4_1_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.035894 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1406-4_1_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0095176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1406-4_1_3_line_3 | NAYY 4x150 SE | 3 | 4 | 0.036831 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1406-4_1_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.037667 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1406-4_1_3_line_5 | NAYY 4x150 SE | 4 | 16 | 0.0047568 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1406-4_1_3_line_6 | NAYY 4x150 SE | 5 | 19 | 0.015021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1406-4_1_3_line_7 | NAYY 4x150 SE | 6 | 7 | 0.039078 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1406-4_1_3_line_8 | NAYY 4x150 SE | 6 | 8 | 0.023409 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1406-4_1_3_line_9 | NAYY 4x150 SE | 7 | 9 | 0.097179 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1406-4_1_3_line_10 | NAYY 4x150 SE | 9 | 10 | 0.043222 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1406-4_1_3_line_11 | NAYY 4x150 SE | 10 | 11 | 0.019036 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1406-4_1_3_line_12 | NAYY 4x150 SE | 11 | 12 | 0.10958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1406-4_1_3_line_13 | NAYY 4x150 SE | 12 | 13 | 0.15864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1406-4_1_3_line_14 | NAYY 4x150 SE | 13 | 27 | 0.017214 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1406-4_1_3_line_15 | NAYY 4x150 SE | 14 | 15 | 0.0092441 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1406-4_1_3_line_16 | NAYY 4x150 SE | 14 | 16 | 0.10275 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1406-4_1_3_line_17 | NAYY 4x150 SE | 15 | 17 | 0.19304 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1406-4_1_3_line_18 | NAYY 4x150 SE | 17 | 28 | 0.19571 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1406-4_1_3_line_19 | NAYY 4x150 SE | 18 | 19 | 0.019203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1406-4_1_3_line_20 | NAYY 4x150 SE | 20 | 21 | 0.027481 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1406-4_1_3_line_21 | NAYY 4x150 SE | 21 | 22 | 0.014448 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1406-4_1_3_line_22 | NAYY 4x150 SE | 22 | 23 | 0.034028 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1406-4_1_3_line_23 | NAYY 4x150 SE | 22 | 24 | 0.041834 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1406-4_1_3_line_24 | NAYY 4x150 SE | 23 | 25 | 0.021995 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1406-4_1_3_line_25 | NAYY 4x150 SE | 24 | 26 | 0.024893 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1406-4_1_3_line_26 | NAYY 4x150 SE | 25 | 27 | 0.021035 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1406-4_1_3_line_27 | NAYY 4x150 SE | 26 | 28 | 0.05284 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1406-4_1_3_trafo_92 | 0.25 MVA 20/0.4 kV | 29 | 22 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2662983.0023 | 1191676.2755 | 2662996.3156 | 1191668.0133
1 | 2662983.0023 | 1191676.2755 | 2662982.8252 | 1191671.3708 | 2662965.6498 | 1191645.5804
2 | 2662983.0023 | 1191676.2755 | 2662978.4767 | 1191682.4982 | 2662979.9754 | 1191683.5368
3 | 2662979.9754 | 1191683.5368 | 2662975.2299 | 1191690.3686 | 2662973.2589 | 1191697.9967 | 2662977.0513 | 1191718.2791
4 | 2662979.9754 | 1191683.5368 | 2663010.9541 | 1191704.9645
5 | 2662977.0513 | 1191718.2791 | 2662977.9256 | 1191722.9549
6 | 2663010.9541 | 1191704.9645 | 2663023.3077 | 1191713.5093
7 | 2662745.8258 | 1191322.8809 | 2662743.8112 | 1191336.1341 | 2662732.737 | 1191356.0962 | 2662733.2674 | 1191358.8903
8 | 2662742.224 | 1191379.8872 | 2662735.526 | 1191370.7895 | 2662733.2674 | 1191358.8903
9 | 2662837.5857 | 1191290.8832 | 2662745.8258 | 1191322.8809
10 | 2662837.5857 | 1191290.8832 | 2662847.2235 | 1191301.1539 | 2662858.6607 | 1191309.1008 | 2662871.955 | 1191316.4918
11 | 2662888.5927 | 1191325.7415 | 2662871.955 | 1191316.4918
12 | 2662888.5927 | 1191325.7415 | 2662870.301 | 1191433.7882
13 | 2662870.301 | 1191433.7882 | 2662792.5515 | 1191572.0711
14 | 2662800.7311 | 1191587.2174 | 2662792.5515 | 1191572.0711
15 | 2662924.6082 | 1191817.7879 | 2662933.6015 | 1191815.649
16 | 2662977.9256 | 1191722.9549 | 2662933.6015 | 1191815.649
17 | 2662924.6082 | 1191817.7879 | 2662772.2744 | 1191936.3574
18 | 2662774.2207 | 1191740.6535 | 2662772.2744 | 1191936.3574
19 | 2663039.449 | 1191723.9121 | 2663023.6026 | 1191713.7133 | 2663023.3077 | 1191713.5093
20 | 2662747.1012 | 1191638.416 | 2662764.0106 | 1191639.0543 | 2662774.5388 | 1191638.237
21 | 2662788.6743 | 1191635.4441 | 2662778.6455 | 1191637.9182 | 2662774.5388 | 1191638.237
22 | 2662788.6743 | 1191635.4441 | 2662821.1779 | 1191625.0791
23 | 2662788.6743 | 1191635.4441 | 2662795.415 | 1191657.1385 | 2662801.8669 | 1191675.1166 | 2662801.8746 | 1191675.1308
24 | 2662821.1779 | 1191625.0791 | 2662810.7262 | 1191605.7255
25 | 2662801.8746 | 1191675.1308 | 2662805.3667 | 1191681.6237 | 2662807.983 | 1191688.0438 | 2662808.2767 | 1191691.2932 | 2662807.1319 | 1191695.0389 | 2662805.1376 | 1191697.8029
26 | 2662810.7262 | 1191605.7255 | 2662800.7311 | 1191587.2174
27 | 2662774.2207 | 1191740.6535 | 2662805.1376 | 1191697.8029

## bus_geodata
| x | y | coords
0 | 2662996.3156 | 1191668.0133
1 | 2662983.0023 | 1191676.2755
2 | 2662965.6498 | 1191645.5804
3 | 2662979.9754 | 1191683.5368
4 | 2662977.0513 | 1191718.2791
5 | 2663010.9541 | 1191704.9645
6 | 2662733.2674 | 1191358.8903
7 | 2662745.8258 | 1191322.8809
8 | 2662742.224 | 1191379.8872
9 | 2662837.5857 | 1191290.8832
10 | 2662871.955 | 1191316.4918
11 | 2662888.5927 | 1191325.7415
12 | 2662870.301 | 1191433.7882
13 | 2662792.5515 | 1191572.0711
14 | 2662933.6015 | 1191815.649
15 | 2662924.6082 | 1191817.7879
16 | 2662977.9256 | 1191722.9549
17 | 2662772.2744 | 1191936.3574
18 | 2663039.449 | 1191723.9121
19 | 2663023.3077 | 1191713.5093
20 | 2662747.1012 | 1191638.416
21 | 2662774.5388 | 1191638.237
22 | 2662788.6743 | 1191635.4441
23 | 2662821.1779 | 1191625.0791
24 | 2662801.8746 | 1191675.1308
25 | 2662810.7262 | 1191605.7255
26 | 2662805.1376 | 1191697.8029
27 | 2662800.7311 | 1191587.2174
28 | 2662774.2207 | 1191740.6535
29 | 2662788.6743 | 1191635.4441

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99228 | -0.054432 | 0.00068043 | 0.00017053
1 | 0.9923 | -0.054324 | 0 | 0
2 | 0.99215 | -0.055368 | 0.0028662 | 0.00071834
3 | 0.99234 | -0.053981 | 0 | 0
4 | 0.9926 | -0.052183 | 0.00039616 | 9.9288e-05
5 | 0.99228 | -0.054464 | 0.00051963 | 0.00013023
6 | 0.99686 | -0.022192 | 0.00037905 | 9.5e-05
7 | 0.9969 | -0.021868 | 0 | 0
8 | 0.99684 | -0.022297 | 0.00044382 | 0.00011123
9 | 0.99702 | -0.021054 | 0.00053659 | 0.00013448
10 | 0.9971 | -0.020457 | 0.00032518 | 8.1497e-05
11 | 0.99715 | -0.020131 | 0.00057863 | 0.00014502
12 | 0.9975 | -0.017613 | 0.00032419 | 8.125e-05
13 | 0.99809 | -0.013434 | 0.0047961 | 0.001202
14 | 0.99344 | -0.046256 | 0.00050216 | 0.00012585
15 | 0.99352 | -0.045698 | 0.00047586 | 0.00011926
16 | 0.99263 | -0.051932 | 0.00023581 | 5.91e-05
17 | 0.99529 | -0.033129 | 0.00022973 | 5.7576e-05
18 | 0.99225 | -0.054677 | 0.00051504 | 0.00012908
19 | 0.99226 | -0.054576 | 0.0002231 | 5.5915e-05
20 | 0.99939 | -0.004305 | 0.0036018 | 0.00090271
21 | 0.99953 | -0.0033157 | 0.019377 | 0.0048564
22 | 1 | 0 | -0.064075 | -0.015856
23 | 0.99915 | -0.0059431 | 0 | 0
24 | 0.99864 | -0.0095405 | 0.0069459 | 0.0017408
25 | 0.99861 | -0.0097894 | 0.0062571 | 0.0015682
26 | 0.99808 | -0.013496 | 0.0037008 | 0.00092752
27 | 0.99827 | -0.012153 | 0.003789 | 0.00094961
28 | 0.99716 | -0.019942 | 0.0054534 | 0.0013668
29 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00068043 | -0.00017053 | 0.00068044 | 0.00017033 | 1.0179e-08 | -1.9849e-07 | 0.0010204 | 0.0010203 | 0.0010204 | 0.99228 | -0.054432 | 0.9923 | -0.054324 | 0.37791
1 | 0.0028666 | 0.00071804 | -0.0028662 | -0.00071834 | 4.1387e-07 | -3.0443e-07 | 0.0042986 | 0.0042987 | 0.0042987 | 0.9923 | -0.054324 | 0.99215 | -0.055368 | 1.5921
2 | -0.0035471 | -0.00088837 | 0.0035472 | 0.00088831 | 1.6801e-07 | -5.8333e-08 | 0.0053189 | 0.0053188 | 0.0053189 | 0.9923 | -0.054324 | 0.99234 | -0.053981 | 1.9699
3 | -0.0048051 | -0.0012026 | 0.0048063 | 0.0012026 | 1.1929e-06 | -1.7129e-08 | 0.0072047 | 0.0072045 | 0.0072047 | 0.99234 | -0.053981 | 0.9926 | -0.052183 | 2.6684
4 | 0.0012579 | 0.00031434 | -0.0012578 | -0.00031479 | 8.36e-08 | -4.5444e-07 | 0.0018859 | 0.001886 | 0.001886 | 0.99234 | -0.053981 | 0.99228 | -0.054464 | 0.69853
5 | -0.0052025 | -0.0013019 | 0.0052026 | 0.0013019 | 1.8051e-07 | 7.9404e-09 | 0.0077984 | 0.0077984 | 0.0077984 | 0.9926 | -0.052183 | 0.99263 | -0.051932 | 2.8883
6 | 0.00073816 | 0.00018456 | -0.00073815 | -0.00018475 | 1.1482e-08 | -1.8961e-07 | 0.0011068 | 0.0011069 | 0.0011069 | 0.99228 | -0.054464 | 0.99226 | -0.054576 | 0.40995
7 | -0.00082288 | -0.00020593 | 0.00082291 | 0.00020543 | 3.6778e-08 | -4.9533e-07 | 0.0012282 | 0.001228 | 0.0012282 | 0.99686 | -0.022192 | 0.9969 | -0.021868 | 0.45489
8 | 0.00044382 | 0.00011093 | -0.00044382 | -0.00011123 | 6.4101e-09 | -3.0271e-07 | 0.00066239 | 0.0006625 | 0.0006625 | 0.99686 | -0.022192 | 0.99684 | -0.022297 | 0.24537
9 | -0.00082291 | -0.00020543 | 0.000823 | 0.0002042 | 9.1415e-08 | -1.232e-06 | 0.001228 | 0.0012276 | 0.001228 | 0.9969 | -0.021868 | 0.99702 | -0.021054 | 0.45482
10 | -0.0013596 | -0.00033868 | 0.0013597 | 0.00033816 | 1.1096e-07 | -5.2104e-07 | 0.0020284 | 0.0020282 | 0.0020284 | 0.99702 | -0.021054 | 0.9971 | -0.020457 | 0.75127
11 | -0.0016849 | -0.00041966 | 0.001685 | 0.00041944 | 7.5042e-08 | -2.1944e-07 | 0.0025135 | 0.0025134 | 0.0025135 | 0.9971 | -0.020457 | 0.99715 | -0.020131 | 0.93093
12 | -0.0022636 | -0.00056446 | 0.0022644 | 0.00056333 | 7.7965e-07 | -1.1301e-06 | 0.0033769 | 0.0033764 | 0.0033769 | 0.99715 | -0.020131 | 0.9975 | -0.017613 | 1.2507
13 | -0.0025886 | -0.00064458 | 0.00259 | 0.00064307 | 1.4747e-06 | -1.5049e-06 | 0.00386 | 0.0038593 | 0.00386 | 0.9975 | -0.017613 | 0.99809 | -0.013434 | 1.4296
14 | -0.0073861 | -0.0018451 | 0.0073874 | 0.0018454 | 1.302e-06 | 2.7574e-07 | 0.01101 | 0.011009 | 0.01101 | 0.99809 | -0.013434 | 0.99827 | -0.012153 | 4.0776
15 | -0.0059449 | -0.0014872 | 0.0059453 | 0.0014872 | 4.5727e-07 | 5.6175e-08 | 0.0089035 | 0.0089035 | 0.0089035 | 0.99344 | -0.046256 | 0.99352 | -0.045698 | 3.2976
16 | 0.0054427 | 0.0013613 | -0.0054385 | -0.001361 | 4.2603e-06 | 3.0933e-07 | 0.0081514 | 0.0081519 | 0.0081519 | 0.99344 | -0.046256 | 0.99263 | -0.051932 | 3.0192
17 | -0.0064212 | -0.0016065 | 0.0064323 | 0.0016083 | 1.1138e-05 | 1.7795e-06 | 0.0096162 | 0.0096153 | 0.0096162 | 0.99352 | -0.045698 | 0.99529 | -0.033129 | 3.5616
18 | -0.0066621 | -0.0016659 | 0.0066742 | 0.001668 | 1.2111e-05 | 2.1098e-06 | 0.0099588 | 0.0099579 | 0.0099588 | 0.99529 | -0.033129 | 0.99716 | -0.019942 | 3.6884
19 | -0.00051504 | -0.00012908 | 0.00051505 | 0.00012884 | 7.1477e-09 | -2.453e-07 | 0.00077238 | 0.00077229 | 0.00077238 | 0.99225 | -0.054677 | 0.99226 | -0.054576 | 0.28607
20 | -0.0036018 | -0.00090271 | 0.0036023 | 0.00090254 | 4.9319e-07 | -1.7046e-07 | 0.0053629 | 0.0053628 | 0.0053629 | 0.99939 | -0.004305 | 0.99953 | -0.0033157 | 1.9863
21 | -0.02298 | -0.005759 | 0.02299 | 0.0057628 | 1.0552e-05 | 3.8689e-06 | 0.03421 | 0.03421 | 0.03421 | 0.99953 | -0.0033157 | 1 | 0 | 12.6705
22 | 0.017461 | 0.0043726 | -0.017446 | -0.0043675 | 1.4333e-05 | 5.0665e-06 | 0.025981 | 0.025981 | 0.025981 | 1 | 0 | 0.99915 | -0.0059431 | 9.6225
23 | 0.022824 | 0.0057205 | -0.022794 | -0.0057095 | 3.011e-05 | 1.1033e-05 | 0.033962 | 0.033963 | 0.033963 | 1 | 0 | 0.99864 | -0.0095405 | 12.5787
24 | 0.017446 | 0.0043675 | -0.017437 | -0.0043643 | 9.2646e-06 | 3.2754e-06 | 0.025981 | 0.025981 | 0.025981 | 0.99915 | -0.0059431 | 0.99861 | -0.0097894 | 9.6226
25 | 0.015848 | 0.0039687 | -0.015839 | -0.0039657 | 8.6609e-06 | 3.0056e-06 | 0.023613 | 0.023613 | 0.023613 | 0.99864 | -0.0095405 | 0.99808 | -0.013496 | 8.7456
26 | 0.01118 | 0.0027961 | -0.011176 | -0.002795 | 3.6419e-06 | 1.1256e-06 | 0.016657 | 0.016657 | 0.016657 | 0.99861 | -0.0097894 | 0.99827 | -0.012153 | 6.1694
27 | 0.012138 | 0.0030382 | -0.012128 | -0.0030347 | 1.0797e-05 | 3.4627e-06 | 0.018096 | 0.018096 | 0.018096 | 0.99808 | -0.013496 | 0.99716 | -0.019942 | 6.7021

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.064075 | 0.015856

## res_load
| p_mw | q_mvar
0 | 0.00068043 | 0.00017053
1 | 0.0028662 | 0.00071834
2 | 0.00039616 | 9.9288e-05
3 | 0.00051963 | 0.00013023
4 | 0.00037905 | 9.5e-05
5 | 0.00044382 | 0.00011123
6 | 0.00053659 | 0.00013448
7 | 0.00032518 | 8.1497e-05
8 | 0.00057863 | 0.00014502
9 | 0.00032419 | 8.125e-05
10 | 0.0047961 | 0.001202
11 | 0.00050216 | 0.00012585
12 | 0.00047586 | 0.00011926
13 | 0.00023581 | 5.91e-05
14 | 0.00022973 | 5.7576e-05
15 | 0.00051504 | 0.00012908
16 | 0.0002231 | 5.5915e-05
17 | 0.0036018 | 0.00090271
18 | 0.019377 | 0.0048564
19 | 0.0069459 | 0.0017408
20 | 0.0062571 | 0.0015682
21 | 0.0037008 | 0.00092752
22 | 0.003789 | 0.00094961
23 | 0.0054534 | 0.0013668

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1