## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1501-18_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1501-18_0_2_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_1501-18_0_2_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1501-18_0_2_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1501-18_0_2_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_1501-18_0_2_node_20 | 0.4 | n |  | TRUE
6 | bus_LV_1501-18_0_2_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_1501-18_0_2_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_1501-18_0_2_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1501-18_0_2_node_19 | 0.4 | n |  | TRUE
10 | bus_LV_1501-18_0_2_node_30 | 0.4 | n |  | TRUE
11 | bus_LV_1501-18_0_2_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_1501-18_0_2_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_1501-18_0_2_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_1501-18_0_2_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_1501-18_0_2_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_1501-18_0_2_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_1501-18_0_2_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_1501-18_0_2_node_29 | 0.4 | n |  | TRUE
19 | bus_LV_1501-18_0_2_node_18 | 0.4 | n |  | TRUE
20 | bus_LV_1501-18_0_2_node_27 | 0.4 | n |  | TRUE
21 | bus_LV_1501-18_0_2_node_22 | 0.4 | n |  | TRUE
22 | bus_LV_1501-18_0_2_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_1501-18_0_2_node_25 | 0.4 | n |  | TRUE
24 | bus_LV_1501-18_0_2_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_1501-18_0_2_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_1501-18_0_2_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_1501-18_0_2_node_32 | 0.4 | n |  | TRUE
28 | bus_LV_1501-18_0_2_node_31 | 0.4 | n |  | TRUE
29 | bus_LV_1501-18_0_2_node_24 | 0.4 | n |  | TRUE
30 | bus_MV_142_0_node_31 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1501-18_0_2_load_0 | 0 | 0.0090501 | 0.0022682 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1501-18_0_2_load_4 | 3 | 0.0022023 | 0.00055194 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1501-18_0_2_load_20 | 5 | 0.0078178 | 0.0019593 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1501-18_0_2_load_7 | 6 | 0.0068754 | 0.0017231 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1501-18_0_2_load_8 | 7 | 0.0083635 | 0.0020961 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1501-18_0_2_load_5 | 8 | 0.0040101 | 0.001005 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1501-18_0_2_load_19 | 9 | 0.0035925 | 0.00090037 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1501-18_0_2_load_30 | 10 | 0.017983 | 0.004507 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1501-18_0_2_load_9 | 11 | 0.0068975 | 0.0017287 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1501-18_0_2_load_10 | 12 | 0.0075893 | 0.0019021 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1501-18_0_2_load_12 | 14 | 0.0045804 | 0.001148 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1501-18_0_2_load_13 | 15 | 0.0045151 | 0.0011316 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1501-18_0_2_load_14 | 16 | 0.0051697 | 0.0012956 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1501-18_0_2_load_15 | 17 | 0.0067747 | 0.0016979 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1501-18_0_2_load_29 | 18 | 0.0051414 | 0.0012886 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1501-18_0_2_load_18 | 19 | 0.0045601 | 0.0011429 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1501-18_0_2_load_27 | 20 | 0.0078226 | 0.0019605 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1501-18_0_2_load_22 | 21 | 0.0048347 | 0.0012117 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1501-18_0_2_load_17 | 22 | 0.0021606 | 0.00054151 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1501-18_0_2_load_25 | 23 | 0.007525 | 0.0018859 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1501-18_0_2_load_16 | 24 | 0.0022199 | 0.00055635 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1501-18_0_2_load_23 | 26 | 0.0022754 | 0.00057027 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1501-18_0_2_load_32 | 27 | 0.012159 | 0.0030473 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1501-18_0_2_load_31 | 28 | 0.011013 | 0.0027602 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1501-18_0_2_load_24 | 29 | 0.01249 | 0.0031302 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 15 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1501-18_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.026092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1501-18_0_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.006758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1501-18_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.034031 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1501-18_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.05961 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1501-18_0_2_line_4 | NAYY 4x150 SE | 2 | 5 | 0.017264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1501-18_0_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.044907 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1501-18_0_2_line_6 | NAYY 4x150 SE | 4 | 7 | 0.010004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1501-18_0_2_line_7 | NAYY 4x150 SE | 4 | 8 | 0.029909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1501-18_0_2_line_8 | NAYY 4x150 SE | 5 | 9 | 0.035386 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1501-18_0_2_line_9 | NAYY 4x150 SE | 7 | 10 | 0.021576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1501-18_0_2_line_10 | NAYY 4x150 SE | 9 | 25 | 0.023504 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1501-18_0_2_line_11 | NAYY 4x150 SE | 11 | 12 | 0.010419 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1501-18_0_2_line_12 | NAYY 4x150 SE | 11 | 13 | 0.033637 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1501-18_0_2_line_13 | NAYY 4x150 SE | 12 | 14 | 0.016197 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1501-18_0_2_line_14 | NAYY 4x150 SE | 13 | 15 | 0.023823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1501-18_0_2_line_15 | NAYY 4x150 SE | 13 | 16 | 0.017398 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1501-18_0_2_line_16 | NAYY 4x150 SE | 14 | 17 | 0.022229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1501-18_0_2_line_17 | NAYY 4x150 SE | 15 | 18 | 0.028413 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1501-18_0_2_line_18 | NAYY 4x150 SE | 16 | 19 | 0.046706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1501-18_0_2_line_19 | NAYY 4x150 SE | 17 | 20 | 1.2437e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1501-18_0_2_line_20 | NAYY 4x150 SE | 18 | 21 | 0.034143 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1501-18_0_2_line_21 | NAYY 4x150 SE | 19 | 22 | 0.014614 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1501-18_0_2_line_22 | NAYY 4x150 SE | 20 | 23 | 0.022476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1501-18_0_2_line_23 | NAYY 4x150 SE | 21 | 25 | 0.011928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1501-18_0_2_line_24 | NAYY 4x150 SE | 22 | 24 | 0.029382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1501-18_0_2_line_25 | NAYY 4x150 SE | 23 | 29 | 0.0095961 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1501-18_0_2_line_26 | NAYY 4x150 SE | 25 | 26 | 0.020361 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1501-18_0_2_line_27 | NAYY 4x150 SE | 26 | 27 | 0.022126 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1501-18_0_2_line_28 | NAYY 4x150 SE | 27 | 28 | 0.030211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1501-18_0_2_trafo_13 | 0.25 MVA 20/0.4 kV | 30 | 15 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2677842.9249 | 1202735.7564 | 2677868.4718 | 1202730.4507
1 | 2677842.9249 | 1202735.7564 | 2677842.5771 | 1202731.4937 | 2677841.74 | 1202729.1591
2 | 2677842.9249 | 1202735.7564 | 2677809.5677 | 1202742.4945
3 | 2677846.8732 | 1202670.4893 | 2677845.8582 | 1202677.1247 | 2677845.6712 | 1202719.4931 | 2677844.4758 | 1202724.2027 | 2677841.74 | 1202729.1591
4 | 2677841.74 | 1202729.1591 | 2677831.8255 | 1202727.2621 | 2677824.7052 | 1202726.4245
5 | 2677846.8732 | 1202670.4893 | 2677850.4921 | 1202654.4264 | 2677859.3608 | 1202627.4026
6 | 2677846.8732 | 1202670.4893 | 2677837.0079 | 1202672.1499
7 | 2677846.8732 | 1202670.4893 | 2677863.8263 | 1202664.8845 | 2677875.5901 | 1202662.2582
8 | 2677824.7052 | 1202726.4245 | 2677806.4228 | 1202724.2738 | 2677789.4622 | 1202723.512
9 | 2677815.7313 | 1202675.7314 | 2677837.0079 | 1202672.1499
10 | 2677765.9819 | 1202722.4573 | 2677789.4622 | 1202723.512
11 | 2677767.7909 | 1202631.5428 | 2677757.3877 | 1202630.978
12 | 2677801.3881 | 1202632.8956 | 2677794.5525 | 1202632.9956 | 2677767.7909 | 1202631.5428
13 | 2677741.214 | 1202630.0999 | 2677757.3877 | 1202630.978
14 | 2677801.3881 | 1202632.8956 | 2677792.9194 | 1202649.6959 | 2677791.2476 | 1202654.4172
15 | 2677801.3881 | 1202632.8956 | 2677806.2967 | 1202625.3104 | 2677808.2905 | 1202619.4882 | 2677808.4307 | 1202617.2834
16 | 2677741.214 | 1202630.0999 | 2677719.0181 | 1202628.895
17 | 2677791.2476 | 1202654.4172 | 2677783.7224 | 1202675.6701 | 2677781.7682 | 1202681.2021
18 | 2677808.4307 | 1202617.2834 | 2677808.7786 | 1202611.812 | 2677807.0001 | 1202599.9481 | 2677807.7693 | 1202590.5634 | 2677815.1541 | 1202572.1806
19 | 2677719.0181 | 1202628.895 | 2677719.0057 | 1202628.8943
20 | 2677781.7682 | 1202681.2021 | 2677781.4862 | 1202682.0005 | 2677776.5038 | 1202691.1636 | 2677770.9846 | 1202698.2962 | 2677767.1626 | 1202702.5047 | 2677766.24 | 1202705.5612 | 2677766.1641 | 1202710.5308
21 | 2677815.1541 | 1202572.1806 | 2677820.1657 | 1202559.7055 | 2677820.573 | 1202558.6086
22 | 2677696.5631 | 1202627.676 | 2677719.0057 | 1202628.8943
23 | 2677765.9819 | 1202722.4573 | 2677766.1641 | 1202710.5308
24 | 2677820.573 | 1202558.6086 | 2677824.5985 | 1202547.7669 | 2677827.4696 | 1202535.3521 | 2677828.3241 | 1202530.3503
25 | 2677696.5631 | 1202627.676 | 2677686.9811 | 1202627.1558
26 | 2677765.9819 | 1202722.4573 | 2677747.6839 | 1202722.0745 | 2677745.7261 | 1202721.4355
27 | 2677727.7425 | 1202709.0042 | 2677734.9887 | 1202715.7165 | 2677742.1139 | 1202720.2565 | 2677745.7261 | 1202721.4355
28 | 2677702.8389 | 1202692.1237 | 2677721.8292 | 1202703.5266 | 2677727.7425 | 1202709.0042

## bus_geodata
| x | y | coords
0 | 2677868.4718 | 1202730.4507
1 | 2677842.9249 | 1202735.7564
2 | 2677841.74 | 1202729.1591
3 | 2677809.5677 | 1202742.4945
4 | 2677846.8732 | 1202670.4893
5 | 2677824.7052 | 1202726.4245
6 | 2677859.3608 | 1202627.4026
7 | 2677837.0079 | 1202672.1499
8 | 2677875.5901 | 1202662.2582
9 | 2677789.4622 | 1202723.512
10 | 2677815.7313 | 1202675.7314
11 | 2677767.7909 | 1202631.5427
12 | 2677757.3877 | 1202630.978
13 | 2677801.3881 | 1202632.8956
14 | 2677741.214 | 1202630.0999
15 | 2677791.2476 | 1202654.4172
16 | 2677808.4307 | 1202617.2834
17 | 2677719.0181 | 1202628.895
18 | 2677781.7682 | 1202681.2021
19 | 2677815.1541 | 1202572.1806
20 | 2677719.0057 | 1202628.8943
21 | 2677766.1641 | 1202710.5308
22 | 2677820.573 | 1202558.6086
23 | 2677696.5631 | 1202627.676
24 | 2677828.3241 | 1202530.3503
25 | 2677765.9819 | 1202722.4573
26 | 2677745.7261 | 1202721.4355
27 | 2677727.7425 | 1202709.0042
28 | 2677702.8389 | 1202692.1237
29 | 2677686.9811 | 1202627.1558
30 | 2677801.3881 | 1202632.8956

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98354 | -0.11527 | 0.0090501 | 0.0022682
1 | 0.98388 | -0.11283 | 0 | 0
2 | 0.98399 | -0.11205 | 0 | 0
3 | 0.98377 | -0.1136 | 0.0022023 | 0.00055194
4 | 0.98077 | -0.13501 | 0 | 0
5 | 0.98521 | -0.10343 | 0.0078178 | 0.0019593
6 | 0.98032 | -0.13821 | 0.0068754 | 0.0017231
7 | 0.98038 | -0.13774 | 0.0083635 | 0.0020961
8 | 0.98059 | -0.13625 | 0.0040101 | 0.001005
9 | 0.9881 | -0.082991 | 0.0035925 | 0.00090037
10 | 0.97982 | -0.14177 | 0.017983 | 0.004507
11 | 0.99509 | -0.034315 | 0.0068975 | 0.0017287
12 | 0.99439 | -0.039232 | 0.0075893 | 0.0019021
13 | 0.99768 | -0.01616 | 0 | 0
14 | 0.99348 | -0.045646 | 0.0045804 | 0.001148
15 | 1 | 0 | -0.16574 | -0.041575
16 | 0.99733 | -0.018624 | 0.0051697 | 0.0012956
17 | 0.99237 | -0.053435 | 0.0067747 | 0.0016979
18 | 0.99608 | -0.027148 | 0.0051414 | 0.0012886
19 | 0.99674 | -0.02282 | 0.0045601 | 0.0011429
20 | 0.99237 | -0.053439 | 0.0078226 | 0.0019605
21 | 0.99162 | -0.058271 | 0.0048347 | 0.0012117
22 | 0.99664 | -0.023464 | 0.0021606 | 0.00054151
23 | 0.99173 | -0.058001 | 0.007525 | 0.0018859
24 | 0.99655 | -0.024119 | 0.0022199 | 0.00055635
25 | 0.99015 | -0.068623 | 0 | 0
26 | 0.9894 | -0.073903 | 0.0022754 | 0.00057027
27 | 0.98866 | -0.079135 | 0.012159 | 0.0030473
28 | 0.98818 | -0.082535 | 0.011013 | 0.0027602
29 | 0.99155 | -0.059218 | 0.01249 | 0.0031302
30 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0090501 | -0.0022682 | 0.0090531 | 0.002269 | 3.0523e-06 | 8.427e-07 | 0.013692 | 0.013692 | 0.013692 | 0.98354 | -0.11527 | 0.98388 | -0.11283 | 5.0711
1 | -0.011256 | -0.0028206 | 0.011257 | 0.002821 | 1.222e-06 | 3.8416e-07 | 0.017023 | 0.017023 | 0.017023 | 0.98388 | -0.11283 | 0.98399 | -0.11205 | 6.3047
2 | 0.0022025 | 0.0005516 | -0.0022023 | -0.00055194 | 2.3561e-07 | -3.4152e-07 | 0.0033309 | 0.003331 | 0.003331 | 0.98388 | -0.11283 | 0.98377 | -0.1136 | 1.2337
3 | 0.037375 | 0.009384 | -0.037256 | -0.009339 | 0.00011885 | 4.4955e-05 | 0.056525 | 0.056525 | 0.056525 | 0.98399 | -0.11205 | 0.98077 | -0.13501 | 20.9352
4 | -0.048631 | -0.012205 | 0.04869 | 0.012227 | 5.8271e-05 | 2.2192e-05 | 0.073547 | 0.073547 | 0.073547 | 0.98399 | -0.11205 | 0.98521 | -0.10343 | 27.2398
5 | 0.0068784 | 0.0017237 | -0.0068754 | -0.0017231 | 3.0519e-06 | 6.0735e-07 | 0.010436 | 0.010436 | 0.010436 | 0.98077 | -0.13501 | 0.98032 | -0.13821 | 3.8652
6 | 0.026367 | 0.0066104 | -0.026357 | -0.0066066 | 9.9901e-06 | 3.7161e-06 | 0.040004 | 0.040004 | 0.040004 | 0.98077 | -0.13501 | 0.98038 | -0.13774 | 14.8163
7 | 0.0040108 | 0.0010049 | -0.0040101 | -0.001005 | 6.9109e-07 | -1.1156e-07 | 0.0060851 | 0.0060853 | 0.0060853 | 0.98077 | -0.13501 | 0.98059 | -0.13625 | 2.2538
8 | -0.056507 | -0.014186 | 0.056668 | 0.014248 | 0.00016087 | 6.1421e-05 | 0.085355 | 0.085355 | 0.085355 | 0.98521 | -0.10343 | 0.9881 | -0.082991 | 31.613
9 | 0.017993 | 0.0045106 | -0.017983 | -0.004507 | 1.0042e-05 | 3.5902e-06 | 0.02731 | 0.02731 | 0.02731 | 0.98038 | -0.13774 | 0.97982 | -0.14177 | 10.1149
10 | -0.060261 | -0.015148 | 0.060382 | 0.015194 | 0.00012083 | 4.617e-05 | 0.090765 | 0.090765 | 0.090765 | 0.9881 | -0.082991 | 0.99015 | -0.068623 | 33.6167
11 | 0.046901 | 0.011769 | -0.046869 | -0.011757 | 3.1982e-05 | 1.2166e-05 | 0.070139 | 0.070139 | 0.070139 | 0.99509 | -0.034315 | 0.99439 | -0.039232 | 25.9774
12 | -0.053798 | -0.013498 | 0.053934 | 0.01355 | 0.00013586 | 5.1815e-05 | 0.080453 | 0.080453 | 0.080453 | 0.99509 | -0.034315 | 0.99768 | -0.01616 | 29.7974
13 | 0.03928 | 0.0098551 | -0.039245 | -0.0098419 | 3.4924e-05 | 1.3222e-05 | 0.058782 | 0.058782 | 0.058782 | 0.99439 | -0.039232 | 0.99348 | -0.045646 | 21.7712
14 | -0.068055 | -0.017089 | 0.068208 | 0.017148 | 0.00015319 | 5.8606e-05 | 0.10151 | 0.10151 | 0.10151 | 0.99768 | -0.01616 | 1 | 0 | 37.5977
15 | 0.014121 | 0.003539 | -0.014116 | -0.0035374 | 4.8156e-06 | 1.625e-06 | 0.021061 | 0.021061 | 0.021061 | 0.99768 | -0.01616 | 0.99733 | -0.018624 | 7.8004
16 | 0.034664 | 0.008694 | -0.034627 | -0.0086799 | 3.7394e-05 | 1.4095e-05 | 0.051922 | 0.051922 | 0.051922 | 0.99348 | -0.045646 | 0.99237 | -0.053435 | 19.2303
17 | 0.096734 | 0.024428 | -0.096366 | -0.024287 | 0.00036767 | 0.00014104 | 0.14401 | 0.14401 | 0.14401 | 1 | 0 | 0.99608 | -0.027148 | 53.3356
18 | 0.0089464 | 0.0022418 | -0.0089412 | -0.0022404 | 5.1926e-06 | 1.388e-06 | 0.013348 | 0.013348 | 0.013348 | 0.99733 | -0.018624 | 0.99674 | -0.02282 | 4.9437
19 | 0.027852 | 0.006982 | -0.027852 | -0.006982 | 1.3536e-08 | 5.0472e-09 | 0.041764 | 0.041764 | 0.041764 | 0.99237 | -0.053435 | 0.99237 | -0.053439 | 15.468
20 | 0.091225 | 0.022998 | -0.090829 | -0.022846 | 0.00039595 | 0.00015185 | 0.13633 | 0.13633 | 0.13633 | 0.99608 | -0.027148 | 0.99162 | -0.058271 | 50.491
21 | 0.0043811 | 0.0010975 | -0.0043807 | -0.0010976 | 3.9009e-07 | -4.0426e-08 | 0.0065403 | 0.0065404 | 0.0065404 | 0.99674 | -0.02282 | 0.99664 | -0.023464 | 2.4224
22 | 0.02003 | 0.0050214 | -0.020017 | -0.0050169 | 1.2651e-05 | 4.5755e-06 | 0.030034 | 0.030034 | 0.030034 | 0.99237 | -0.053439 | 0.99173 | -0.058001 | 11.1237
23 | 0.085994 | 0.021634 | -0.08587 | -0.021587 | 0.000124 | 4.7537e-05 | 0.12907 | 0.12907 | 0.12907 | 0.99162 | -0.058271 | 0.99015 | -0.068623 | 47.804
24 | 0.0022201 | 0.00055604 | -0.0022199 | -0.00055635 | 2.0142e-07 | -3.0538e-07 | 0.0033145 | 0.0033146 | 0.0033146 | 0.99664 | -0.023464 | 0.99655 | -0.024119 | 1.2276
25 | 0.012492 | 0.0031309 | -0.01249 | -0.0031302 | 2.1036e-06 | 6.8529e-07 | 0.018743 | 0.018743 | 0.018743 | 0.99173 | -0.058001 | 0.99155 | -0.059218 | 6.942
26 | 0.025488 | 0.0063925 | -0.02547 | -0.0063856 | 1.8644e-05 | 6.9089e-06 | 0.038306 | 0.038306 | 0.038306 | 0.99015 | -0.068623 | 0.9894 | -0.073903 | 14.1874
27 | 0.023194 | 0.0058153 | -0.023177 | -0.0058091 | 1.6801e-05 | 6.178e-06 | 0.034884 | 0.034884 | 0.034884 | 0.9894 | -0.073903 | 0.98866 | -0.079135 | 12.92
28 | 0.011019 | 0.0027618 | -0.011013 | -0.0027602 | 5.1849e-06 | 1.607e-06 | 0.016584 | 0.016584 | 0.016584 | 0.98866 | -0.079135 | 0.98818 | -0.082535 | 6.1423

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.17026 | 0.042707

## res_load
| p_mw | q_mvar
0 | 0.0090501 | 0.0022682
1 | 0.0022023 | 0.00055194
2 | 0.0078178 | 0.0019593
3 | 0.0068754 | 0.0017231
4 | 0.0083635 | 0.0020961
5 | 0.0040101 | 0.001005
6 | 0.0035925 | 0.00090037
7 | 0.017983 | 0.004507
8 | 0.0068975 | 0.0017287
9 | 0.0075893 | 0.0019021
10 | 0.0045804 | 0.001148
11 | 0.0045151 | 0.0011316
12 | 0.0051697 | 0.0012956
13 | 0.0067747 | 0.0016979
14 | 0.0051414 | 0.0012886
15 | 0.0045601 | 0.0011429
16 | 0.0078226 | 0.0019605
17 | 0.0048347 | 0.0012117
18 | 0.0021606 | 0.00054151
19 | 0.007525 | 0.0018859
20 | 0.0022199 | 0.00055635
21 | 0.0022754 | 0.00057027
22 | 0.012159 | 0.0030473
23 | 0.011013 | 0.0027602
24 | 0.01249 | 0.0031302

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1