## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1501-19_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1501-19_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1501-19_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1501-19_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1501-19_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1501-19_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1501-19_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1501-19_0_3_node_11 | 0.4 | n |  | TRUE
8 | bus_LV_1501-19_0_3_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_1501-19_0_3_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_1501-19_0_3_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1501-19_0_3_node_13 | 0.4 | n |  | TRUE
12 | bus_LV_1501-19_0_3_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_1501-19_0_3_node_21 | 0.4 | n |  | TRUE
14 | bus_LV_1501-19_0_3_node_34 | 0.4 | n |  | TRUE
15 | bus_LV_1501-19_0_3_node_22 | 0.4 | n |  | TRUE
16 | bus_LV_1501-19_0_3_node_33 | 0.4 | n |  | TRUE
17 | bus_LV_1501-19_0_3_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_1501-19_0_3_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_1501-19_0_3_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_1501-19_0_3_node_20 | 0.4 | n |  | TRUE
21 | bus_LV_1501-19_0_3_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_1501-19_0_3_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_1501-19_0_3_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_1501-19_0_3_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_1501-19_0_3_node_27 | 0.4 | n |  | TRUE
26 | bus_LV_1501-19_0_3_node_28 | 0.4 | n |  | TRUE
27 | bus_LV_1501-19_0_3_node_30 | 0.4 | n |  | TRUE
28 | bus_LV_1501-19_0_3_node_29 | 0.4 | n |  | TRUE
29 | bus_LV_1501-19_0_3_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_1501-19_0_3_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_1501-19_0_3_node_25 | 0.4 | n |  | TRUE
32 | bus_LV_1501-19_0_3_node_26 | 0.4 | n |  | TRUE
33 | bus_LV_1501-19_0_3_node_35 | 0.4 | n |  | TRUE
34 | bus_LV_1501-19_0_3_node_31 | 0.4 | n |  | TRUE
35 | bus_LV_1501-19_0_3_node_32 | 0.4 | n |  | TRUE
36 | bus_MV_142_0_node_38 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1501-19_0_3_load_0 | 0 | 0.0051998 | 0.0013032 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1501-19_0_3_load_1 | 1 | 0.0072391 | 0.0018143 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1501-19_0_3_load_5 | 5 | 0.004376 | 0.0010967 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1501-19_0_3_load_6 | 6 | 0.0032366 | 0.00081117 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1501-19_0_3_load_11 | 7 | 0.0062013 | 0.0015542 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1501-19_0_3_load_9 | 8 | 0.008199 | 0.0020549 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1501-19_0_3_load_7 | 9 | 0.0045438 | 0.0011388 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1501-19_0_3_load_8 | 10 | 0.0033734 | 0.00084544 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1501-19_0_3_load_13 | 11 | 0.0062119 | 0.0015568 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1501-19_0_3_load_21 | 13 | 0.0041607 | 0.0010428 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1501-19_0_3_load_34 | 14 | 0.0038433 | 0.00096323 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1501-19_0_3_load_22 | 15 | 0.0031455 | 0.00078834 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1501-19_0_3_load_33 | 16 | 0.0045042 | 0.0011289 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1501-19_0_3_load_12 | 17 | 0.0055015 | 0.0013788 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1501-19_0_3_load_14 | 18 | 0.0049587 | 0.0012428 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1501-19_0_3_load_16 | 19 | 0.016998 | 0.00426 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1501-19_0_3_load_20 | 20 | 0.0096816 | 0.0024264 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1501-19_0_3_load_15 | 21 | 0.0094839 | 0.0023769 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1501-19_0_3_load_17 | 22 | 0.0078062 | 0.0019564 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1501-19_0_3_load_18 | 23 | 0.0036038 | 0.00090319 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1501-19_0_3_load_27 | 25 | 0.0037079 | 0.00092928 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1501-19_0_3_load_28 | 26 | 0.0048685 | 0.0012202 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1501-19_0_3_load_30 | 27 | 0.012523 | 0.0031386 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1501-19_0_3_load_29 | 28 | 0.0039146 | 0.00098109 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1501-19_0_3_load_23 | 29 | 0.0056757 | 0.0014225 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1501-19_0_3_load_24 | 30 | 0.019257 | 0.0048264 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1501-19_0_3_load_25 | 31 | 0.0051557 | 0.0012921 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1501-19_0_3_load_26 | 32 | 0.00076475 | 0.00019166 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1501-19_0_3_load_35 | 33 | 0.0040084 | 0.0010046 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1501-19_0_3_load_31 | 34 | 0.0093531 | 0.0023441 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1501-19_0_3_load_32 | 35 | 0.003143 | 0.00078772 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 21 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1501-19_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.024646 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1501-19_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.054305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1501-19_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0064475 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1501-19_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.066359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
4 | LV_1501-19_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.029694 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1501-19_0_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.014762 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1501-19_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.047158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
7 | LV_1501-19_0_3_line_7 | NAYY 4x150 SE | 4 | 8 | 0.06501 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1501-19_0_3_line_8 | NAYY 4x150 SE | 5 | 9 | 0.0039088 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1501-19_0_3_line_9 | NAYY 4x150 SE | 6 | 10 | 0.010666 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1501-19_0_3_line_10 | NAYY 4x150 SE | 7 | 11 | 0.017599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
11 | LV_1501-19_0_3_line_11 | NAYY 4x150 SE | 8 | 12 | 0.010448 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1501-19_0_3_line_12 | NAYY 4x150 SE | 9 | 13 | 0.022172 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1501-19_0_3_line_13 | NAYY 4x150 SE | 10 | 14 | 0.0049699 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1501-19_0_3_line_14 | NAYY 4x150 SE | 11 | 19 | 0.0071299 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
15 | LV_1501-19_0_3_line_15 | NAYY 4x150 SE | 12 | 17 | 0.034304 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1501-19_0_3_line_16 | NAYY 4x150 SE | 13 | 15 | 0.00041979 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1501-19_0_3_line_17 | NAYY 4x150 SE | 14 | 16 | 0.011099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1501-19_0_3_line_18 | NAYY 4x150 SE | 15 | 29 | 0.0010691 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1501-19_0_3_line_19 | NAYY 4x150 SE | 16 | 35 | 0.0019868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1501-19_0_3_line_20 | NAYY 4x150 SE | 17 | 18 | 0.023004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1501-19_0_3_line_21 | NAYY 4x150 SE | 18 | 20 | 0.054978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1501-19_0_3_line_22 | NAYY 4x150 SE | 19 | 21 | 0.018005 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
23 | LV_1501-19_0_3_line_23 | NAYY 4x150 SE | 21 | 22 | 0.021204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1501-19_0_3_line_24 | NAYY 4x150 SE | 22 | 23 | 0.01128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1501-19_0_3_line_25 | NAYY 4x150 SE | 23 | 24 | 0.0034207 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1501-19_0_3_line_26 | NAYY 4x150 SE | 24 | 25 | 0.0089001 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1501-19_0_3_line_27 | NAYY 4x150 SE | 24 | 26 | 0.018248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1501-19_0_3_line_28 | NAYY 4x150 SE | 25 | 27 | 0.026208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1501-19_0_3_line_29 | NAYY 4x150 SE | 26 | 28 | 0.016859 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1501-19_0_3_line_30 | NAYY 4x150 SE | 27 | 33 | 0.00013079 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1501-19_0_3_line_31 | NAYY 4x150 SE | 29 | 30 | 0.015192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1501-19_0_3_line_32 | NAYY 4x150 SE | 30 | 31 | 0.0078889 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1501-19_0_3_line_33 | NAYY 4x150 SE | 31 | 32 | 0.013253 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1501-19_0_3_line_34 | NAYY 4x150 SE | 34 | 35 | 0.018535 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1501-19_0_3_trafo_15 | 0.25 MVA 20/0.4 kV | 36 | 21 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2677896.0951 | 1202724.7137 | 2677920.2259 | 1202719.7021
1 | 2677842.9249 | 1202735.7564 | 2677896.0951 | 1202724.7137
2 | 2677926.5387 | 1202718.391 | 2677920.2259 | 1202719.7021
3 | 2677842.9249 | 1202735.7564 | 2677842.5771 | 1202731.4937 | 2677841.74 | 1202729.1591 | 2677844.4758 | 1202724.2027 | 2677845.6712 | 1202719.4931 | 2677845.8582 | 1202677.1247 | 2677846.8732 | 1202670.4893
4 | 2677926.5387 | 1202718.391 | 2677955.6371 | 1202712.4712
5 | 2677926.5387 | 1202718.391 | 2677926.806 | 1202721.8188 | 2677926.5258 | 1202728.1302 | 2677924.064 | 1202732.4898
6 | 2677846.8732 | 1202670.4893 | 2677863.8263 | 1202664.8845 | 2677892.4245 | 1202658.4999
7 | 2677846.8732 | 1202670.4893 | 2677850.4921 | 1202654.4264 | 2677865.6291 | 1202608.3026
8 | 2677959.4674 | 1202711.6919 | 2677955.6371 | 1202712.4712
9 | 2677915.8753 | 1202739.324 | 2677919.339 | 1202736.4862 | 2677924.064 | 1202732.4898
10 | 2677909.6005 | 1202654.6654 | 2677892.4245 | 1202658.4999
11 | 2677868.887 | 1202598.3755 | 2677865.6291 | 1202608.3026
12 | 2677959.4674 | 1202711.6919 | 2677981.1947 | 1202707.2717
13 | 2677915.8753 | 1202739.324 | 2677912.031 | 1202742.4737
14 | 2677909.6005 | 1202654.6654 | 2677916.5591 | 1202653.1119
15 | 2677868.887 | 1202598.3755 | 2677902.289 | 1202590.5597
16 | 2677981.1947 | 1202707.2717 | 2677981.606 | 1202707.188
17 | 2677904.2561 | 1202750.3361 | 2677908.5463 | 1202745.3288 | 2677912.031 | 1202742.4737
18 | 2677982.6536 | 1202706.9749 | 2677981.606 | 1202707.188
19 | 2677902.9634 | 1202751.8449 | 2677904.2561 | 1202750.3361
20 | 2677902.289 | 1202590.5597 | 2677924.6878 | 1202585.3186
21 | 2677978.2201 | 1202572.7924 | 2677924.6878 | 1202585.3186
22 | 2677934.1311 | 1202649.1889 | 2677916.5591 | 1202653.1119
23 | 2677954.8258 | 1202644.5688 | 2677934.1311 | 1202649.1889
24 | 2677954.8258 | 1202644.5688 | 2677965.8349 | 1202642.111
25 | 2677969.1734 | 1202641.3657 | 2677965.8349 | 1202642.111
26 | 2677969.1734 | 1202641.3657 | 2677977.9787 | 1202640.0694
27 | 2677969.1734 | 1202641.3657 | 2677983.5378 | 1202630.1108
28 | 2677998.8732 | 1202642.3065 | 2677989.8913 | 1202644.1267 | 2677989.1514 | 1202638.4246 | 2677977.9787 | 1202640.0694
29 | 2677996.8085 | 1202619.7128 | 2677983.5378 | 1202630.1108
30 | 2677999.0014 | 1202642.2805 | 2677998.8732 | 1202642.3065
31 | 2677982.6536 | 1202706.9749 | 2677997.5404 | 1202703.9463
32 | 2677997.5404 | 1202703.9463 | 2678005.271 | 1202702.3736
33 | 2678018.2582 | 1202699.7315 | 2678005.271 | 1202702.3736
34 | 2677890.0688 | 1202765.1225 | 2677890.0688 | 1202765.1225 | 2677897.8352 | 1202757.8303 | 2677902.9634 | 1202751.8449

## bus_geodata
| x | y | coords
0 | 2677896.0951 | 1202724.7137
1 | 2677920.2259 | 1202719.7021
2 | 2677842.9249 | 1202735.7564
3 | 2677926.5387 | 1202718.391
4 | 2677846.8732 | 1202670.4893
5 | 2677955.6371 | 1202712.4712
6 | 2677924.064 | 1202732.4898
7 | 2677892.4245 | 1202658.4999
8 | 2677865.6291 | 1202608.3026
9 | 2677959.4674 | 1202711.6919
10 | 2677915.8753 | 1202739.3241
11 | 2677909.6005 | 1202654.6654
12 | 2677868.887 | 1202598.3755
13 | 2677981.1947 | 1202707.2717
14 | 2677912.031 | 1202742.4737
15 | 2677981.606 | 1202707.188
16 | 2677904.2561 | 1202750.3361
17 | 2677902.289 | 1202590.5597
18 | 2677924.6878 | 1202585.3186
19 | 2677916.5591 | 1202653.1119
20 | 2677978.2201 | 1202572.7924
21 | 2677934.1311 | 1202649.1889
22 | 2677954.8258 | 1202644.5688
23 | 2677965.8349 | 1202642.111
24 | 2677969.1734 | 1202641.3657
25 | 2677977.9787 | 1202640.0694
26 | 2677983.5378 | 1202630.1108
27 | 2677998.8732 | 1202642.3065
28 | 2677996.8085 | 1202619.7128
29 | 2677982.6536 | 1202706.9749
30 | 2677997.5404 | 1202703.9463
31 | 2678005.271 | 1202702.3736
32 | 2678018.2582 | 1202699.7315
33 | 2677999.0014 | 1202642.2805
34 | 2677890.0688 | 1202765.1225
35 | 2677902.9634 | 1202751.8449
36 | 2677969.1734 | 1202641.3657

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9808 | -0.13391 | 0.0051998 | 0.0013032
1 | 0.97786 | -0.15488 | 0.0072391 | 0.0018143
2 | 0.98771 | -0.085238 | 0 | 0
3 | 0.97715 | -0.1599 | 0 | 0
4 | 0.99193 | -0.055833 | 0 | 0
5 | 0.97511 | -0.17455 | 0.004376 | 0.0010967
6 | 0.97656 | -0.16414 | 0.0032366 | 0.00081117
7 | 0.99589 | -0.028349 | 0.0062013 | 0.0015542
8 | 0.98927 | -0.074581 | 0.008199 | 0.0020549
9 | 0.97486 | -0.1763 | 0.0045438 | 0.0011388
10 | 0.97618 | -0.16685 | 0.0033734 | 0.00084544
11 | 0.99745 | -0.017601 | 0.0062119 | 0.0015568
12 | 0.98896 | -0.076729 | 0 | 0
13 | 0.97362 | -0.1852 | 0.0041607 | 0.0010428
14 | 0.97603 | -0.16793 | 0.0038433 | 0.00096323
15 | 0.9736 | -0.18535 | 0.0031455 | 0.00078834
16 | 0.97576 | -0.16991 | 0.0045042 | 0.0011289
17 | 0.98797 | -0.08379 | 0.0055015 | 0.0013788
18 | 0.98748 | -0.087237 | 0.0049587 | 0.0012428
19 | 0.99811 | -0.013034 | 0.016998 | 0.00426
20 | 0.98671 | -0.092691 | 0.0096816 | 0.0024264
21 | 1 | 0 | -0.18861 | -0.047414
22 | 0.99878 | -0.0085689 | 0.0078062 | 0.0019564
23 | 0.99825 | -0.012254 | 0.0036038 | 0.00090319
24 | 0.99811 | -0.013248 | 0 | 0
25 | 0.99785 | -0.015054 | 0.0037079 | 0.00092928
26 | 0.99788 | -0.014855 | 0.0048685 | 0.0012202
27 | 0.99723 | -0.019399 | 0.012523 | 0.0031386
28 | 0.99778 | -0.015517 | 0.0039146 | 0.00098109
29 | 0.97355 | -0.1857 | 0.0056757 | 0.0014225
30 | 0.97299 | -0.18973 | 0.019257 | 0.0048264
31 | 0.97292 | -0.19022 | 0.0051557 | 0.0012921
32 | 0.97291 | -0.19033 | 0.00076475 | 0.00019166
33 | 0.99723 | -0.019405 | 0.0040084 | 0.0010046
34 | 0.97547 | -0.17199 | 0.0093531 | 0.0023441
35 | 0.97572 | -0.17017 | 0.003143 | 0.00078772
36 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.08227 | 0.020683 | -0.08203 | -0.020591 | 0.00023967 | 9.1872e-05 | 0.12484 | 0.12484 | 0.12484 | 0.9808 | -0.13391 | 0.97786 | -0.15488 | 46.2364
1 | -0.08747 | -0.021986 | 0.088067 | 0.022215 | 0.00059695 | 0.00022891 | 0.13273 | 0.13273 | 0.13273 | 0.9808 | -0.13391 | 0.98771 | -0.085238 | 49.1582
2 | 0.074791 | 0.018777 | -0.074739 | -0.018757 | 5.2124e-05 | 1.9967e-05 | 0.11382 | 0.11382 | 0.11382 | 0.97786 | -0.15488 | 0.97715 | -0.1599 | 42.1565
3 | -0.088067 | -0.022215 | 0.088431 | 0.022354 | 0.00036473 | 0.00013857 | 0.13273 | 0.13273 | 0.13273 | 0.98771 | -0.085238 | 0.99193 | -0.055833 | 24.5791
4 | 0.04725 | 0.011864 | -0.047154 | -0.011827 | 9.595e-05 | 3.6533e-05 | 0.07196 | 0.07196 | 0.07196 | 0.97715 | -0.1599 | 0.97511 | -0.17455 | 26.6519
5 | 0.027489 | 0.0068935 | -0.027473 | -0.0068875 | 1.6143e-05 | 6.0242e-06 | 0.041863 | 0.041863 | 0.041863 | 0.97715 | -0.1599 | 0.97656 | -0.16414 | 15.5047
6 | -0.11689 | -0.029498 | 0.11734 | 0.029671 | 0.00045274 | 0.00017291 | 0.17542 | 0.17542 | 0.17542 | 0.99193 | -0.055833 | 0.99589 | -0.028349 | 32.4845
7 | 0.028455 | 0.0071443 | -0.028381 | -0.0071167 | 7.3931e-05 | 2.7598e-05 | 0.04269 | 0.042691 | 0.042691 | 0.99193 | -0.055833 | 0.98927 | -0.074581 | 15.8113
8 | 0.042778 | 0.01073 | -0.042767 | -0.010726 | 1.0395e-05 | 3.9493e-06 | 0.065282 | 0.065282 | 0.065282 | 0.97511 | -0.17455 | 0.97486 | -0.1763 | 24.1787
9 | 0.024237 | 0.0060763 | -0.024228 | -0.006073 | 9.0777e-06 | 3.358e-06 | 0.036931 | 0.036931 | 0.036931 | 0.97656 | -0.16414 | 0.97618 | -0.16685 | 13.6781
10 | -0.12354 | -0.031225 | 0.12373 | 0.031297 | 0.00018728 | 7.1571e-05 | 0.18468 | 0.18468 | 0.18468 | 0.99589 | -0.028349 | 0.99745 | -0.017601 | 34.2003
11 | 0.020182 | 0.0050618 | -0.020176 | -0.0050597 | 6.0085e-06 | 2.1769e-06 | 0.030358 | 0.030358 | 0.030358 | 0.98927 | -0.074581 | 0.98896 | -0.076729 | 11.2437
12 | 0.038224 | 0.0095875 | -0.038176 | -0.0095697 | 4.7101e-05 | 1.784e-05 | 0.058347 | 0.058347 | 0.058347 | 0.97486 | -0.1763 | 0.97362 | -0.1852 | 21.61
13 | 0.020854 | 0.0052275 | -0.020851 | -0.0052264 | 3.1338e-06 | 1.1432e-06 | 0.031789 | 0.031789 | 0.031789 | 0.97618 | -0.16685 | 0.97603 | -0.16793 | 11.7737
14 | -0.12994 | -0.032854 | 0.13002 | 0.032886 | 8.3678e-05 | 3.1998e-05 | 0.19395 | 0.19395 | 0.19395 | 0.99745 | -0.017601 | 0.99811 | -0.013034 | 35.9164
15 | 0.020176 | 0.0050597 | -0.020156 | -0.0050525 | 1.9728e-05 | 7.148e-06 | 0.030358 | 0.030358 | 0.030358 | 0.98896 | -0.076729 | 0.98797 | -0.08379 | 11.2438
16 | 0.034016 | 0.0085269 | -0.034015 | -0.0085266 | 7.0797e-07 | 2.6708e-07 | 0.051988 | 0.051988 | 0.051988 | 0.97362 | -0.1852 | 0.9736 | -0.18535 | 19.2548
17 | 0.017008 | 0.0042631 | -0.017003 | -0.0042615 | 4.6564e-06 | 1.6523e-06 | 0.02593 | 0.02593 | 0.02593 | 0.97603 | -0.16793 | 0.97576 | -0.16991 | 9.6035
18 | 0.03087 | 0.0077383 | -0.030868 | -0.0077378 | 1.4849e-06 | 5.5784e-07 | 0.047181 | 0.047181 | 0.047181 | 0.9736 | -0.18535 | 0.97355 | -0.1857 | 17.4743
19 | 0.012499 | 0.0031326 | -0.012498 | -0.0031325 | 4.5042e-07 | 1.4842e-07 | 0.019061 | 0.019061 | 0.019061 | 0.97576 | -0.16991 | 0.97572 | -0.17017 | 7.0595
20 | 0.014655 | 0.0036737 | -0.014648 | -0.0036713 | 6.9933e-06 | 2.3953e-06 | 0.022072 | 0.022072 | 0.022072 | 0.98797 | -0.08379 | 0.98748 | -0.087237 | 8.1749
21 | 0.0096889 | 0.0024285 | -0.0096816 | -0.0024264 | 7.313e-06 | 2.1099e-06 | 0.0146 | 0.0146 | 0.0146 | 0.98748 | -0.087237 | 0.98671 | -0.092691 | 5.4075
22 | -0.14702 | -0.037146 | 0.14729 | 0.037249 | 0.00027013 | 0.00010342 | 0.21929 | 0.21929 | 0.21929 | 0.99811 | -0.013034 | 1 | 0 | 40.6091
23 | 0.040519 | 0.010165 | -0.04047 | -0.010147 | 4.8104e-05 | 1.8224e-05 | 0.060296 | 0.060296 | 0.060296 | 1 | 0 | 0.99878 | -0.0085689 | 22.3318
24 | 0.032664 | 0.0081904 | -0.032648 | -0.0081841 | 1.667e-05 | 6.2642e-06 | 0.048666 | 0.048666 | 0.048666 | 0.99878 | -0.0085689 | 0.99825 | -0.012254 | 18.0244
25 | 0.029044 | 0.0072809 | -0.02904 | -0.0072795 | 4.0009e-06 | 1.4941e-06 | 0.043294 | 0.043294 | 0.043294 | 0.99825 | -0.012254 | 0.99811 | -0.013248 | 16.0348
26 | 0.020254 | 0.0050778 | -0.020249 | -0.0050759 | 5.064e-06 | 1.8314e-06 | 0.030196 | 0.030197 | 0.030197 | 0.99811 | -0.013248 | 0.99785 | -0.015054 | 11.1839
27 | 0.0087854 | 0.0022017 | -0.0087835 | -0.0022012 | 1.9534e-06 | 5.1287e-07 | 0.013098 | 0.013098 | 0.013098 | 0.99811 | -0.013248 | 0.99788 | -0.014855 | 4.851
28 | 0.016541 | 0.0041467 | -0.016531 | -0.0041432 | 9.9508e-06 | 3.4851e-06 | 0.024667 | 0.024667 | 0.024667 | 0.99785 | -0.015054 | 0.99723 | -0.019399 | 9.1361
29 | 0.0039149 | 0.000981 | -0.0039146 | -0.00098109 | 3.5853e-07 | -8.2325e-08 | 0.0058378 | 0.0058379 | 0.0058379 | 0.99788 | -0.014855 | 0.99778 | -0.015517 | 2.1622
30 | 0.0040084 | 0.0010046 | -0.0040084 | -0.0010046 | 2.9198e-09 | -5.8358e-10 | 0.0059811 | 0.0059811 | 0.0059811 | 0.99723 | -0.019399 | 0.99723 | -0.019405 | 2.2152
31 | 0.025192 | 0.0063153 | -0.025178 | -0.0063101 | 1.4055e-05 | 5.217e-06 | 0.038505 | 0.038506 | 0.038506 | 0.97355 | -0.1857 | 0.97299 | -0.18973 | 14.2613
32 | 0.0059208 | 0.0014837 | -0.0059204 | -0.0014836 | 4.0361e-07 | 5.7259e-08 | 0.0090548 | 0.0090548 | 0.0090548 | 0.97299 | -0.18973 | 0.97292 | -0.19022 | 3.3536
33 | 0.00076476 | 0.0001915 | -0.00076475 | -0.00019166 | 1.1313e-08 | -1.6023e-07 | 0.0011696 | 0.0011697 | 0.0011697 | 0.97292 | -0.19022 | 0.97291 | -0.19033 | 0.4332
34 | -0.0093531 | -0.0023441 | 0.0093554 | 0.0023448 | 2.3544e-06 | 6.7409e-07 | 0.014268 | 0.014267 | 0.014268 | 0.97547 | -0.17199 | 0.97572 | -0.17017 | 5.2843

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.19809 | 0.049791

## res_load
| p_mw | q_mvar
0 | 0.0051998 | 0.0013032
1 | 0.0072391 | 0.0018143
2 | 0.004376 | 0.0010967
3 | 0.0032366 | 0.00081117
4 | 0.0062013 | 0.0015542
5 | 0.008199 | 0.0020549
6 | 0.0045438 | 0.0011388
7 | 0.0033734 | 0.00084544
8 | 0.0062119 | 0.0015568
9 | 0.0041607 | 0.0010428
10 | 0.0038433 | 0.00096323
11 | 0.0031455 | 0.00078834
12 | 0.0045042 | 0.0011289
13 | 0.0055015 | 0.0013788
14 | 0.0049587 | 0.0012428
15 | 0.016998 | 0.00426
16 | 0.0096816 | 0.0024264
17 | 0.0094839 | 0.0023769
18 | 0.0078062 | 0.0019564
19 | 0.0036038 | 0.00090319
20 | 0.0037079 | 0.00092928
21 | 0.0048685 | 0.0012202
22 | 0.012523 | 0.0031386
23 | 0.0039146 | 0.00098109
24 | 0.0056757 | 0.0014225
25 | 0.019257 | 0.0048264
26 | 0.0051557 | 0.0012921
27 | 0.00076475 | 0.00019166
28 | 0.0040084 | 0.0010046
29 | 0.0093531 | 0.0023441
30 | 0.003143 | 0.00078772

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1