## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1501-1_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1501-1_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1501-1_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1501-1_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1501-1_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1501-1_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1501-1_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1501-1_0_3_node_35 | 0.4 | n |  | TRUE
8 | bus_LV_1501-1_0_3_node_36 | 0.4 | n |  | TRUE
9 | bus_LV_1501-1_0_3_node_34 | 0.4 | n |  | TRUE
10 | bus_LV_1501-1_0_3_node_18 | 0.4 | n |  | TRUE
11 | bus_LV_1501-1_0_3_node_40 | 0.4 | n |  | TRUE
12 | bus_LV_1501-1_0_3_node_56 | 0.4 | n |  | TRUE
13 | bus_LV_1501-1_0_3_node_16 | 0.4 | n |  | TRUE
14 | bus_LV_1501-1_0_3_node_17 | 0.4 | n |  | TRUE
15 | bus_LV_1501-1_0_3_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_1501-1_0_3_node_39 | 0.4 | n |  | TRUE
17 | bus_LV_1501-1_0_3_node_7 | 0.4 | n |  | TRUE
18 | bus_LV_1501-1_0_3_node_8 | 0.4 | n |  | TRUE
19 | bus_LV_1501-1_0_3_node_9 | 0.4 | n |  | TRUE
20 | bus_LV_1501-1_0_3_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_1501-1_0_3_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_1501-1_0_3_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_1501-1_0_3_node_22 | 0.4 | n |  | TRUE
24 | bus_LV_1501-1_0_3_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_1501-1_0_3_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_1501-1_0_3_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_1501-1_0_3_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_1501-1_0_3_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_1501-1_0_3_node_31 | 0.4 | n |  | TRUE
30 | bus_LV_1501-1_0_3_node_27 | 0.4 | n |  | TRUE
31 | bus_LV_1501-1_0_3_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_1501-1_0_3_node_37 | 0.4 | n |  | TRUE
33 | bus_LV_1501-1_0_3_node_38 | 0.4 | n |  | TRUE
34 | bus_LV_1501-1_0_3_node_50 | 0.4 | n |  | TRUE
35 | bus_LV_1501-1_0_3_node_57 | 0.4 | n |  | TRUE
36 | bus_LV_1501-1_0_3_node_24 | 0.4 | n |  | TRUE
37 | bus_LV_1501-1_0_3_node_25 | 0.4 | n |  | TRUE
38 | bus_LV_1501-1_0_3_node_26 | 0.4 | n |  | TRUE
39 | bus_LV_1501-1_0_3_node_28 | 0.4 | n |  | TRUE
40 | bus_LV_1501-1_0_3_node_30 | 0.4 | n |  | TRUE
41 | bus_LV_1501-1_0_3_node_54 | 0.4 | n |  | TRUE
42 | bus_LV_1501-1_0_3_node_29 | 0.4 | n |  | TRUE
43 | bus_LV_1501-1_0_3_node_49 | 0.4 | n |  | TRUE
44 | bus_LV_1501-1_0_3_node_48 | 0.4 | n |  | TRUE
45 | bus_LV_1501-1_0_3_node_53 | 0.4 | n |  | TRUE
46 | bus_LV_1501-1_0_3_node_46 | 0.4 | n |  | TRUE
47 | bus_LV_1501-1_0_3_node_32 | 0.4 | n |  | TRUE
48 | bus_LV_1501-1_0_3_node_33 | 0.4 | n |  | TRUE
49 | bus_LV_1501-1_0_3_node_117 | 0.4 | n |  | TRUE
50 | bus_LV_1501-1_0_3_node_64 | 0.4 | n |  | TRUE
51 | bus_LV_1501-1_0_3_node_110 | 0.4 | n |  | TRUE
52 | bus_LV_1501-1_0_3_node_111 | 0.4 | n |  | TRUE
53 | bus_LV_1501-1_0_3_node_112 | 0.4 | n |  | TRUE
54 | bus_LV_1501-1_0_3_node_113 | 0.4 | n |  | TRUE
55 | bus_LV_1501-1_0_3_node_122 | 0.4 | n |  | TRUE
56 | bus_LV_1501-1_0_3_node_61 | 0.4 | n |  | TRUE
57 | bus_LV_1501-1_0_3_node_51 | 0.4 | n |  | TRUE
58 | bus_LV_1501-1_0_3_node_41 | 0.4 | n |  | TRUE
59 | bus_LV_1501-1_0_3_node_42 | 0.4 | n |  | TRUE
60 | bus_LV_1501-1_0_3_node_116 | 0.4 | n |  | TRUE
61 | bus_LV_1501-1_0_3_node_43 | 0.4 | n |  | TRUE
62 | bus_LV_1501-1_0_3_node_44 | 0.4 | n |  | TRUE
63 | bus_LV_1501-1_0_3_node_52 | 0.4 | n |  | TRUE
64 | bus_LV_1501-1_0_3_node_55 | 0.4 | n |  | TRUE
65 | bus_LV_1501-1_0_3_node_58 | 0.4 | n |  | TRUE
66 | bus_LV_1501-1_0_3_node_59 | 0.4 | n |  | TRUE
67 | bus_LV_1501-1_0_3_node_60 | 0.4 | n |  | TRUE
68 | bus_LV_1501-1_0_3_node_62 | 0.4 | n |  | TRUE
69 | bus_LV_1501-1_0_3_node_63 | 0.4 | n |  | TRUE
70 | bus_LV_1501-1_0_3_node_136 | 0.4 | n |  | TRUE
71 | bus_LV_1501-1_0_3_node_108 | 0.4 | n |  | TRUE
72 | bus_MV_142_0_node_39 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1501-1_0_3_load_0 | 0 | 0.0036786 | 0.00092195 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1501-1_0_3_load_3 | 3 | 0.00037621 | 9.4286e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1501-1_0_3_load_4 | 4 | 0.00035386 | 8.8686e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1501-1_0_3_load_5 | 5 | 0.002678 | 0.00067118 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1501-1_0_3_load_35 | 7 | 0.00032983 | 8.2663e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1501-1_0_3_load_36 | 8 | 0.00043667 | 0.00010944 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1501-1_0_3_load_34 | 9 | 0.002201 | 0.00055163 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1501-1_0_3_load_40 | 11 | 0.0027602 | 0.00069178 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1501-1_0_3_load_56 | 12 | 0.0015026 | 0.00037658 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1501-1_0_3_load_17 | 14 | 0.0019081 | 0.00047821 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1501-1_0_3_load_15 | 15 | 0.0044464 | 0.0011144 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1501-1_0_3_load_39 | 16 | 0.0039309 | 0.00098517 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1501-1_0_3_load_7 | 17 | 0.0032753 | 0.00082087 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1501-1_0_3_load_8 | 18 | 0.0039327 | 0.00098562 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1501-1_0_3_load_9 | 19 | 0.0033532 | 0.0008404 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1501-1_0_3_load_10 | 20 | 0.0028776 | 0.0007212 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1501-1_0_3_load_11 | 21 | 0.0049356 | 0.001237 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1501-1_0_3_load_12 | 22 | 0.0032193 | 0.00080683 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1501-1_0_3_load_22 | 23 | 0.0039187 | 0.00098213 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1501-1_0_3_load_13 | 24 | 0.0052031 | 0.001304 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1501-1_0_3_load_19 | 25 | 0.0041375 | 0.001037 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1501-1_0_3_load_14 | 27 | 0.0028758 | 0.00072075 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1501-1_0_3_load_20 | 28 | 0.012404 | 0.0031087 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1501-1_0_3_load_31 | 29 | 0.0025182 | 0.00063112 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1501-1_0_3_load_21 | 31 | 0.0068929 | 0.0017275 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1501-1_0_3_load_37 | 32 | 0.0030242 | 0.00075793 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1501-1_0_3_load_50 | 34 | 0.011178 | 0.0028015 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1501-1_0_3_load_57 | 35 | 0.0023868 | 0.00059818 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1501-1_0_3_load_24 | 36 | 0.0042358 | 0.0010616 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1501-1_0_3_load_28 | 39 | 0.0067337 | 0.0016876 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1501-1_0_3_load_30 | 40 | 0.0073783 | 0.0018492 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1501-1_0_3_load_54 | 41 | 0.0054401 | 0.0013634 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1501-1_0_3_load_48 | 44 | 0.006145 | 0.0015401 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1501-1_0_3_load_53 | 45 | 0.0066578 | 0.0016686 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1501-1_0_3_load_46 | 46 | 0.0071904 | 0.0018021 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1501-1_0_3_load_33 | 48 | 0.00043054 | 0.0001079 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1501-1_0_3_load_117 | 49 | 0.0012069 | 0.00030249 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1501-1_0_3_load_110 | 51 | 0.00035464 | 8.8881e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1501-1_0_3_load_111 | 52 | 0.00018309 | 4.5887e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1501-1_0_3_load_112 | 53 | 0.0010215 | 0.00025601 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1501-1_0_3_load_122 | 55 | 0.00034674 | 8.6902e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1501-1_0_3_load_51 | 57 | 0.004416 | 0.0011067 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1501-1_0_3_load_42 | 59 | 0.0046267 | 0.0011596 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1501-1_0_3_load_116 | 60 | 0.0035975 | 0.00090162 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1501-1_0_3_load_43 | 61 | 0.0067138 | 0.0016826 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1501-1_0_3_load_44 | 62 | 0.0062472 | 0.0015657 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1501-1_0_3_load_52 | 63 | 0.011425 | 0.0028633 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1501-1_0_3_load_55 | 64 | 0.0057965 | 0.0014527 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1501-1_0_3_load_58 | 65 | 0.00066544 | 0.00016677 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1501-1_0_3_load_59 | 66 | 0.00054948 | 0.00013771 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1501-1_0_3_load_63 | 69 | 0.00019206 | 4.8134e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1501-1_0_3_load_136 | 70 | 0.00047208 | 0.00011832 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1501-1_0_3_load_108 | 71 | 0.00044502 | 0.00011153 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 25 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1501-1_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.018571 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1501-1_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.027881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1501-1_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.032231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1501-1_0_3_line_3 | NAYY 4x150 SE | 1 | 4 | 0.0066874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1501-1_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.0084538 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1501-1_0_3_line_5 | NAYY 4x150 SE | 2 | 6 | 0.040149 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1501-1_0_3_line_6 | NAYY 4x150 SE | 3 | 7 | 0.014614 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1501-1_0_3_line_7 | NAYY 4x150 SE | 4 | 8 | 0.020353 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1501-1_0_3_line_8 | NAYY 4x150 SE | 5 | 9 | 0.016658 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1501-1_0_3_line_9 | NAYY 4x150 SE | 6 | 10 | 0.02352 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1501-1_0_3_line_10 | NAYY 4x150 SE | 6 | 11 | 0.026251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1501-1_0_3_line_11 | NAYY 4x150 SE | 10 | 12 | 0.0014474 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1501-1_0_3_line_12 | NAYY 4x150 SE | 10 | 13 | 0.017101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1501-1_0_3_line_13 | NAYY 4x150 SE | 11 | 16 | 0.028468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1501-1_0_3_line_14 | NAYY 4x150 SE | 12 | 30 | 0.033897 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1501-1_0_3_line_15 | NAYY 4x150 SE | 13 | 14 | 0.027659 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1501-1_0_3_line_16 | NAYY 4x150 SE | 13 | 15 | 0.044392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1501-1_0_3_line_17 | NAYY 4x150 SE | 14 | 29 | 0.022137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1501-1_0_3_line_18 | NAYY 4x150 SE | 15 | 27 | 0.0057844 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
19 | LV_1501-1_0_3_line_19 | NAYY 4x150 SE | 16 | 58 | 0.11883 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1501-1_0_3_line_20 | NAYY 4x150 SE | 17 | 18 | 0.010746 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1501-1_0_3_line_21 | NAYY 4x150 SE | 17 | 19 | 0.014679 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1501-1_0_3_line_22 | NAYY 4x150 SE | 18 | 20 | 0.015242 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1501-1_0_3_line_23 | NAYY 4x150 SE | 19 | 21 | 0.027054 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
24 | LV_1501-1_0_3_line_24 | NAYY 4x150 SE | 19 | 22 | 0.014835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
25 | LV_1501-1_0_3_line_25 | NAYY 4x150 SE | 20 | 23 | 0.0068664 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1501-1_0_3_line_26 | NAYY 4x150 SE | 21 | 24 | 0.010768 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
27 | LV_1501-1_0_3_line_27 | NAYY 4x150 SE | 22 | 25 | 0.021785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
28 | LV_1501-1_0_3_line_28 | NAYY 4x150 SE | 23 | 26 | 0.037233 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1501-1_0_3_line_29 | NAYY 4x150 SE | 24 | 27 | 0.014439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
30 | LV_1501-1_0_3_line_30 | NAYY 4x150 SE | 25 | 28 | 0.047442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1501-1_0_3_line_31 | NAYY 4x150 SE | 26 | 32 | 0.028283 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1501-1_0_3_line_32 | NAYY 4x150 SE | 26 | 33 | 0.061692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1501-1_0_3_line_33 | NAYY 4x150 SE | 28 | 31 | 0.016863 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1501-1_0_3_line_34 | NAYY 4x150 SE | 30 | 41 | 0.010065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1501-1_0_3_line_35 | NAYY 4x150 SE | 30 | 37 | 0.009649 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1501-1_0_3_line_36 | NAYY 4x150 SE | 32 | 34 | 0.00065654 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1501-1_0_3_line_37 | NAYY 4x150 SE | 33 | 35 | 0.08621 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1501-1_0_3_line_38 | NAYY 4x150 SE | 34 | 57 | 0.024045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1501-1_0_3_line_39 | NAYY 4x150 SE | 36 | 37 | 0.057705 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1501-1_0_3_line_40 | NAYY 4x150 SE | 36 | 38 | 0.024934 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1501-1_0_3_line_41 | NAYY 4x150 SE | 37 | 39 | 0.026895 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1501-1_0_3_line_42 | NAYY 4x150 SE | 38 | 40 | 0.014735 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1501-1_0_3_line_43 | NAYY 4x150 SE | 40 | 43 | 0.03143 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1501-1_0_3_line_44 | NAYY 4x150 SE | 41 | 45 | 0.019047 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1501-1_0_3_line_45 | NAYY 4x150 SE | 42 | 43 | 0.011652 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1501-1_0_3_line_46 | NAYY 4x150 SE | 42 | 44 | 0.019654 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1501-1_0_3_line_47 | NAYY 4x150 SE | 43 | 46 | 0.012528 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1501-1_0_3_line_48 | NAYY 4x150 SE | 45 | 64 | 0.024153 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1501-1_0_3_line_49 | NAYY 4x150 SE | 46 | 62 | 0.01182 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1501-1_0_3_line_50 | NAYY 4x150 SE | 47 | 48 | 0.16314 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1501-1_0_3_line_51 | NAYY 4x150 SE | 47 | 49 | 0.10022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1501-1_0_3_line_52 | NAYY 4x150 SE | 48 | 50 | 0.29646 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1501-1_0_3_line_53 | NAYY 4x150 SE | 49 | 54 | 0.091549 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1501-1_0_3_line_54 | NAYY 4x150 SE | 50 | 56 | 0.11849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1501-1_0_3_line_55 | NAYY 4x150 SE | 51 | 52 | 0.010921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1501-1_0_3_line_56 | NAYY 4x150 SE | 51 | 53 | 0.026862 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1501-1_0_3_line_57 | NAYY 4x150 SE | 52 | 54 | 0.10542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1501-1_0_3_line_58 | NAYY 4x150 SE | 53 | 55 | 0.28753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1501-1_0_3_line_59 | NAYY 4x150 SE | 54 | 60 | 0.1468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1501-1_0_3_line_60 | NAYY 4x150 SE | 56 | 69 | 0.1084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1501-1_0_3_line_61 | NAYY 4x150 SE | 56 | 66 | 0.0014436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1501-1_0_3_line_62 | NAYY 4x150 SE | 57 | 63 | 7.3095e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1501-1_0_3_line_63 | NAYY 4x150 SE | 58 | 59 | 0.036323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1501-1_0_3_line_64 | NAYY 4x150 SE | 59 | 60 | 0.027672 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1501-1_0_3_line_65 | NAYY 4x150 SE | 61 | 62 | 0.022592 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1501-1_0_3_line_66 | NAYY 4x150 SE | 65 | 66 | 0.14275 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1501-1_0_3_line_67 | NAYY 4x150 SE | 65 | 67 | 0.073787 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1501-1_0_3_line_68 | NAYY 4x150 SE | 67 | 68 | 0.13163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1501-1_0_3_line_69 | NAYY 4x150 SE | 68 | 70 | 0.13202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1501-1_0_3_line_70 | NAYY 4x150 SE | 69 | 71 | 0.020562 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1501-1_0_3_trafo_19 | 0.25 MVA 20/0.4 kV | 72 | 25 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2677387.8791 | 1202555.8667 | 2677401.747 | 1202550.4763 | 2677405.1839 | 1202549.1271
1 | 2677431.1367 | 1202538.9387 | 2677405.1839 | 1202549.1271
2 | 2677387.8791 | 1202555.8667 | 2677378.7476 | 1202540.5055 | 2677366.3991 | 1202533.1744
3 | 2677387.8791 | 1202555.8667 | 2677381.2629 | 1202556.8401
4 | 2677431.1367 | 1202538.9387 | 2677431.4063 | 1202530.4892
5 | 2677431.1367 | 1202538.9387 | 2677447.3892 | 1202540.4058 | 2677452.9246 | 1202541.3893 | 2677456.8619 | 1202542.3632 | 2677459.0012 | 1202542.8912 | 2677463.0003 | 1202544.3773 | 2677469.9834 | 1202547.581
6 | 2677352.3646 | 1202529.1013 | 2677366.3991 | 1202533.1744
7 | 2677361.1265 | 1202559.8025 | 2677381.2629 | 1202556.8401
8 | 2677425.7389 | 1202516.188 | 2677431.6622 | 1202522.4686 | 2677431.4063 | 1202530.4892
9 | 2677469.9834 | 1202547.581 | 2677472.3299 | 1202548.5676 | 2677481.3574 | 1202549.6409 | 2677483.1918 | 1202549.6202 | 2677485.198 | 1202549.2682 | 2677489.7862 | 1202547.5822 | 2677491.2191 | 1202550.3581
10 | 2677469.9834 | 1202547.581 | 2677473.8605 | 1202529.7312 | 2677474.771 | 1202521.7979
11 | 2677491.2191 | 1202550.3581 | 2677492.0943 | 1202551.5109
12 | 2677488.98 | 1202534.0522 | 2677488.1987 | 1202536.199 | 2677487.8468 | 1202538.6848 | 2677487.8842 | 1202540.4976 | 2677488.0815 | 1202542.3012 | 2677488.7719 | 1202544.8118 | 2677489.7862 | 1202547.5822 | 2677491.2191 | 1202550.3581
13 | 2677478.017 | 1202493.516 | 2677474.771 | 1202521.7979
14 | 2677519.1074 | 1202571.8221 | 2677504.9791 | 1202561.499 | 2677499.5394 | 1202557.8373 | 2677494.9161 | 1202554.5976 | 2677493.2394 | 1202553.0193 | 2677492.0943 | 1202551.5109
15 | 2677488.98 | 1202534.0522 | 2677486.9142 | 1202530.2008 | 2677486.2264 | 1202527.4902 | 2677486.0884 | 1202525.8096 | 2677486.0513 | 1202523.3853 | 2677488.0474 | 1202507.1259
16 | 2677488.98 | 1202534.0522 | 2677490.3469 | 1202531.3571 | 2677492.6408 | 1202528.1849 | 2677495.2344 | 1202525.9616 | 2677501.1867 | 1202521.2136 | 2677522.8074 | 1202506.0201
17 | 2677490.7449 | 1202485.1536 | 2677488.0474 | 1202507.1259
18 | 2677527.54 | 1202502.6943 | 2677522.8074 | 1202506.0201
19 | 2677482.8372 | 1202375.1735 | 2677485.0765 | 1202394.3923 | 2677484.4382 | 1202435.9655 | 2677480.9996 | 1202467.5294 | 2677478.017 | 1202493.516
20 | 2677582.5908 | 1202464.6242 | 2677591.59 | 1202458.751
21 | 2677570.2983 | 1202472.6468 | 2677582.5908 | 1202464.6242
22 | 2677604.9585 | 1202451.4351 | 2677592.2128 | 1202458.3446 | 2677591.59 | 1202458.751
23 | 2677570.2983 | 1202472.6468 | 2677548.1636 | 1202488.2015
24 | 2677570.2983 | 1202472.6468 | 2677578.911 | 1202484.7255
25 | 2677610.995 | 1202448.1628 | 2677604.9585 | 1202451.4351
26 | 2677548.1636 | 1202488.2015 | 2677539.3536 | 1202494.3925
27 | 2677578.911 | 1202484.7255 | 2677590.2628 | 1202500.6456 | 2677591.3928 | 1202502.5703
28 | 2677643.7277 | 1202430.4185 | 2677610.995 | 1202448.1628
29 | 2677527.54 | 1202502.6943 | 2677539.3536 | 1202494.3925
30 | 2677616.9998 | 1202541.2867 | 2677613.5654 | 1202530.0222 | 2677600.2552 | 1202517.6638 | 2677591.3928 | 1202502.5703
31 | 2677643.7277 | 1202430.4185 | 2677646.0479 | 1202435.185 | 2677641.0571 | 1202457.6185
32 | 2677643.7277 | 1202430.4185 | 2677648.8023 | 1202427.6272 | 2677668.3956 | 1202416.8529 | 2677682.4425 | 1202409.4531 | 2677698.4093 | 1202401.9004
33 | 2677603.7511 | 1202547.7584 | 2677611.7977 | 1202546.5762 | 2677617.5947 | 1202543.2383 | 2677616.9998 | 1202541.2867
34 | 2677519.1074 | 1202571.8221 | 2677527.6919 | 1202566.5674
35 | 2677527.2671 | 1202577.009 | 2677519.1074 | 1202571.8221
36 | 2677640.9146 | 1202458.2594 | 2677641.0571 | 1202457.6185
37 | 2677698.4093 | 1202401.9004 | 2677688.4812 | 1202487.5367
38 | 2677640.9146 | 1202458.2594 | 2677635.6931 | 1202481.7302
39 | 2677527.2671 | 1202577.009 | 2677573.4066 | 1202610.6732 | 2677573.8947 | 1202611.0046
40 | 2677594.5222 | 1202625.0119 | 2677573.8947 | 1202611.0046
41 | 2677527.2671 | 1202577.009 | 2677503.5326 | 1202589.6592
42 | 2677594.5222 | 1202625.0119 | 2677599.9792 | 1202617.9673 | 2677601.1094 | 1202617.0814 | 2677602.6806 | 1202616.8238 | 2677604.2514 | 1202617.1778 | 2677605.2709 | 1202617.784
43 | 2677631.9739 | 1202634.3597 | 2677606.0865 | 1202618.269 | 2677605.2709 | 1202617.784
44 | 2677546.323 | 1202564.2062 | 2677534.3344 | 1202564.3372 | 2677531.1676 | 1202564.9854 | 2677528.2672 | 1202566.2152 | 2677527.6919 | 1202566.5674
45 | 2677625.0632 | 1202643.7536 | 2677631.9739 | 1202634.3597
46 | 2677625.0632 | 1202643.7536 | 2677641.697 | 1202654.223
47 | 2677631.9739 | 1202634.3597 | 2677635.0183 | 1202630.8304 | 2677639.1818 | 1202627.8605 | 2677641.75 | 1202626.87
48 | 2677546.323 | 1202564.2062 | 2677570.4749 | 1202563.9422
49 | 2677641.75 | 1202626.87 | 2677643.6717 | 1202626.1288 | 2677647.9673 | 1202625.2952 | 2677652.587 | 1202625.2886 | 2677653.3506 | 1202625.33
50 | 2677458.2247 | 1202248.9312 | 2677430.4117 | 1202176.9148 | 2677411.1995 | 1202130.0812 | 2677398.4842 | 1202099.3084 | 2677398.122 | 1202097.3219
51 | 2677458.2247 | 1202248.9312 | 2677358.2003 | 1202255.252
52 | 2677422.3482 | 1201838.9888 | 2677414.5202 | 1201843.3568 | 2677400.1066 | 1201853.1428 | 2677374.3733 | 1201869.4975 | 2677363.7491 | 1201885.2476 | 2677356.5503 | 1201905.1001 | 2677359.9572 | 1201925.9016 | 2677369.4878 | 1201946.3821 | 2677390.4721 | 1201996.9187 | 2677394.5691 | 1202027.3017 | 2677394.6557 | 1202052.3296 | 2677393.8794 | 1202074.0553 | 2677398.122 | 1202097.3219
53 | 2677324.9817 | 1202336.8826 | 2677333.6458 | 1202327.2554 | 2677348.1091 | 1202308.8422 | 2677352.8736 | 1202300.6099 | 2677357.9622 | 1202256.7818 | 2677358.2003 | 1202255.252
54 | 2677422.3482 | 1201838.9888 | 2677432.0892 | 1201847.9317 | 2677442.2195 | 1201855.6122 | 2677449.3148 | 1201863.7203 | 2677454.0361 | 1201874.1213 | 2677452.3508 | 1201899.6042 | 2677454.7307 | 1201919.1583 | 2677463.9258 | 1201942.5921
55 | 2677287.0778 | 1202257.3142 | 2677297.7066 | 1202259.8222
56 | 2677260.9341 | 1202251.1452 | 2677287.0778 | 1202257.3142
57 | 2677324.9817 | 1202336.8826 | 2677326.9379 | 1202324.5225 | 2677337.1951 | 1202311.1802 | 2677339.1207 | 1202294.7282 | 2677332.5199 | 1202274.319 | 2677320.1776 | 1202266.4655 | 2677298.3724 | 1202259.9793 | 2677297.7066 | 1202259.8222
58 | 2677260.9341 | 1202251.1452 | 2676975.822 | 1202213.9339
59 | 2677469.7706 | 1202312.6922 | 2677324.9817 | 1202336.8826
60 | 2677463.9258 | 1201942.5921 | 2677476.2877 | 1201935.4812 | 2677489.9344 | 1201922.0276 | 2677500.7566 | 1201906.2914 | 2677509.882 | 1201879.949 | 2677517.4107 | 1201865.8045 | 2677526.8439 | 1201858.4205
61 | 2677463.9258 | 1201942.5921 | 2677464.8182 | 1201943.7268
62 | 2677635.6772 | 1202481.8015 | 2677635.6931 | 1202481.7302
63 | 2677482.8372 | 1202375.1735 | 2677479.8235 | 1202349.9298 | 2677477.0633 | 1202339.3846
64 | 2677469.7706 | 1202312.6922 | 2677473.7468 | 1202326.7143 | 2677477.0633 | 1202339.3846
65 | 2677675.9096 | 1202626.5547 | 2677653.3506 | 1202625.33
66 | 2677582.1391 | 1202018.3586 | 2677577.3965 | 1202012.3297 | 2677565.775 | 1201999.3596 | 2677535.8066 | 1201982.5603 | 2677524.1111 | 1201977.6277 | 2677509.3934 | 1201973.9011 | 2677492.6698 | 1201968.7366 | 2677475.869 | 1201957.7786 | 2677464.8182 | 1201943.7268
67 | 2677639.0007 | 1202064.5734 | 2677606.5861 | 1202042.7721 | 2677590.9866 | 1202029.6058 | 2677582.1391 | 1202018.3586
68 | 2677639.0007 | 1202064.5734 | 2677661.3193 | 1202077.8495 | 2677694.1616 | 1201998.2934 | 2677700.7647 | 1201979.8456
69 | 2677700.7647 | 1201979.8456 | 2677691.2481 | 1201965.4017 | 2677676.9825 | 1201947.9943 | 2677666.3001 | 1201927.1981 | 2677653.791 | 1201898.7845 | 2677647.2855 | 1201876.3638 | 2677646.2294 | 1201861.9598
70 | 2677537.1186 | 1201841.634 | 2677535.5874 | 1201849.3522 | 2677531.229 | 1201854.9881 | 2677526.8439 | 1201858.4205

## bus_geodata
| x | y | coords
0 | 2677405.1839 | 1202549.1271
1 | 2677387.8791 | 1202555.8667
2 | 2677431.1367 | 1202538.9387
3 | 2677366.3991 | 1202533.1744
4 | 2677381.2629 | 1202556.8401
5 | 2677431.4063 | 1202530.4892
6 | 2677469.9834 | 1202547.581
7 | 2677352.3646 | 1202529.1013
8 | 2677361.1265 | 1202559.8025
9 | 2677425.7389 | 1202516.188
10 | 2677491.2191 | 1202550.3581
11 | 2677474.771 | 1202521.7979
12 | 2677492.0943 | 1202551.5109
13 | 2677488.98 | 1202534.0522
14 | 2677488.0474 | 1202507.1259
15 | 2677522.8074 | 1202506.0201
16 | 2677478.017 | 1202493.516
17 | 2677582.5908 | 1202464.6242
18 | 2677591.59 | 1202458.751
19 | 2677570.2983 | 1202472.6468
20 | 2677604.9585 | 1202451.4351
21 | 2677548.1636 | 1202488.2015
22 | 2677578.911 | 1202484.7255
23 | 2677610.995 | 1202448.1628
24 | 2677539.3536 | 1202494.3925
25 | 2677591.3928 | 1202502.5703
26 | 2677643.7277 | 1202430.4185
27 | 2677527.54 | 1202502.6943
28 | 2677616.9998 | 1202541.2867
29 | 2677490.7449 | 1202485.1536
30 | 2677519.1074 | 1202571.8221
31 | 2677603.7511 | 1202547.7584
32 | 2677641.0571 | 1202457.6185
33 | 2677698.4093 | 1202401.9004
34 | 2677640.9146 | 1202458.2594
35 | 2677688.4812 | 1202487.5367
36 | 2677573.8947 | 1202611.0046
37 | 2677527.2671 | 1202577.009
38 | 2677594.5222 | 1202625.0119
39 | 2677503.5326 | 1202589.6592
40 | 2677605.2709 | 1202617.784
41 | 2677527.6919 | 1202566.5674
42 | 2677625.0632 | 1202643.7536
43 | 2677631.9739 | 1202634.3597
44 | 2677641.697 | 1202654.223
45 | 2677546.323 | 1202564.2062
46 | 2677641.75 | 1202626.87
47 | 2677458.2247 | 1202248.9312
48 | 2677398.122 | 1202097.3219
49 | 2677358.2003 | 1202255.252
50 | 2677422.3482 | 1201838.9888
51 | 2677287.0778 | 1202257.3142
52 | 2677297.7066 | 1202259.8222
53 | 2677260.9341 | 1202251.1452
54 | 2677324.9817 | 1202336.8826
55 | 2676975.822 | 1202213.9339
56 | 2677463.9258 | 1201942.5921
57 | 2677635.6931 | 1202481.7302
58 | 2677482.8372 | 1202375.1735
59 | 2677477.0633 | 1202339.3847
60 | 2677469.7706 | 1202312.6922
61 | 2677675.9096 | 1202626.5547
62 | 2677653.3506 | 1202625.3301
63 | 2677635.6772 | 1202481.8015
64 | 2677570.4749 | 1202563.9422
65 | 2677582.1391 | 1202018.3586
66 | 2677464.8182 | 1201943.7268
67 | 2677639.0007 | 1202064.5734
68 | 2677700.7647 | 1201979.8456
69 | 2677526.8439 | 1201858.4205
70 | 2677646.2294 | 1201861.9598
71 | 2677537.1186 | 1201841.634
72 | 2677570.2983 | 1202472.6468

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98012 | -0.13925 | 0.0036786 | 0.00092195
1 | 0.98008 | -0.13954 | 0 | 0
2 | 0.98033 | -0.13775 | 0 | 0
3 | 0.98005 | -0.13978 | 0.00037621 | 9.4286e-05
4 | 0.98007 | -0.1396 | 0.00035386 | 8.8686e-05
5 | 0.98027 | -0.13818 | 0.002678 | 0.00067118
6 | 0.98092 | -0.13356 | 0 | 0
7 | 0.98004 | -0.13983 | 0.00032983 | 8.2663e-05
8 | 0.98006 | -0.13969 | 0.00043667 | 0.00010944
9 | 0.98022 | -0.13856 | 0.002201 | 0.00055163
10 | 0.98197 | -0.12599 | 0 | 0
11 | 0.98012 | -0.13928 | 0.0027602 | 0.00069178
12 | 0.98184 | -0.12695 | 0.0015026 | 0.00037658
13 | 0.98434 | -0.10919 | 0 | 0
14 | 0.98417 | -0.11045 | 0.0019081 | 0.00047821
15 | 0.99078 | -0.063959 | 0.0044464 | 0.0011144
16 | 0.97937 | -0.14467 | 0.0039309 | 0.00098517
17 | 0.99454 | -0.037855 | 0.0032753 | 0.00082087
18 | 0.99388 | -0.04254 | 0.0039327 | 0.00098562
19 | 0.99552 | -0.03098 | 0.0033532 | 0.0008404
20 | 0.99301 | -0.04859 | 0.0028776 | 0.0007212
21 | 0.99322 | -0.04696 | 0.0049356 | 0.001237
22 | 0.99732 | -0.018539 | 0.0032193 | 0.00080683
23 | 0.99265 | -0.051119 | 0.0039187 | 0.00098213
24 | 0.99234 | -0.053071 | 0.0052031 | 0.001304
25 | 1 | 0 | -0.19285 | -0.048491
26 | 0.99092 | -0.063378 | 0 | 0
27 | 0.99122 | -0.060902 | 0.0028758 | 0.00072075
28 | 0.99869 | -0.0091507 | 0.012404 | 0.0031087
29 | 0.98409 | -0.11103 | 0.0025182 | 0.00063112
30 | 0.97874 | -0.14897 | 0 | 0
31 | 0.99853 | -0.010314 | 0.0068929 | 0.0017275
32 | 0.98969 | -0.072026 | 0.0030242 | 0.00075793
33 | 0.9907 | -0.064882 | 0 | 0
34 | 0.98967 | -0.072207 | 0.011178 | 0.0028015
35 | 0.99041 | -0.066979 | 0.0023868 | 0.00059818
36 | 0.9749 | -0.17637 | 0.0042358 | 0.0010616
37 | 0.97811 | -0.15347 | 0 | 0
38 | 0.97367 | -0.18521 | 0 | 0
39 | 0.97784 | -0.15536 | 0.0067337 | 0.0016876
40 | 0.97294 | -0.19044 | 0.0073783 | 0.0018492
41 | 0.97847 | -0.15085 | 0.0054401 | 0.0013634
42 | 0.97162 | -0.19992 | 0 | 0
43 | 0.97172 | -0.19916 | 0 | 0
44 | 0.97144 | -0.2012 | 0.006145 | 0.0015401
45 | 0.97813 | -0.15333 | 0.0066578 | 0.0016686
46 | 0.97135 | -0.20183 | 0.0071904 | 0.0018021
47 | 0.9736 | -0.18687 | 0 | 0
48 | 0.97294 | -0.19178 | 0.00043054 | 0.0001079
49 | 0.974 | -0.18384 | 0.0012069 | 0.00030249
50 | 0.97193 | -0.1993 | 0 | 0
51 | 0.97421 | -0.18226 | 0.00035464 | 8.8881e-05
52 | 0.97424 | -0.18206 | 0.00018309 | 4.5887e-05
53 | 0.97416 | -0.18266 | 0.0010215 | 0.00025601
54 | 0.97453 | -0.17991 | 0 | 0
55 | 0.97401 | -0.18375 | 0.00034674 | 8.6902e-05
56 | 0.97153 | -0.20229 | 0 | 0
57 | 0.98912 | -0.076091 | 0.004416 | 0.0011067
58 | 0.97692 | -0.16238 | 0 | 0
59 | 0.97618 | -0.1678 | 0.0046267 | 0.0011596
60 | 0.97579 | -0.1706 | 0.0035975 | 0.00090162
61 | 0.97091 | -0.20506 | 0.0067138 | 0.0016826
62 | 0.97113 | -0.20345 | 0.0062472 | 0.0015657
63 | 0.98912 | -0.076099 | 0.011425 | 0.0028633
64 | 0.97792 | -0.15479 | 0.0057965 | 0.0014527
65 | 0.97128 | -0.20409 | 0.00066544 | 0.00016677
66 | 0.97152 | -0.20232 | 0.00054948 | 0.00013771
67 | 0.97123 | -0.20448 | 0 | 0
68 | 0.97114 | -0.20517 | 0 | 0
69 | 0.97142 | -0.20303 | 0.00019206 | 4.8134e-05
70 | 0.97105 | -0.20583 | 0.00047208 | 0.00011832
71 | 0.97141 | -0.20313 | 0.00044502 | 0.00011153
72 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0014967 | 0.00037395 | -0.0014966 | -0.00037416 | 5.9811e-08 | -2.1103e-07 | 0.0022718 | 0.0022719 | 0.0022719 | 0.98012 | -0.13925 | 0.98008 | -0.13954 | 0.84144
1 | -0.0051753 | -0.0012959 | 0.0051764 | 0.001296 | 1.0739e-06 | 6.1589e-08 | 0.0078567 | 0.0078566 | 0.0078567 | 0.98012 | -0.13925 | 0.98033 | -0.13775 | 2.9099
2 | 0.00070606 | 0.00017637 | -0.00070604 | -0.00017677 | 2.3106e-08 | -3.9727e-07 | 0.0010718 | 0.0010719 | 0.0010719 | 0.98008 | -0.13954 | 0.98005 | -0.13978 | 0.39701
3 | 0.00079054 | 0.00019779 | -0.00079053 | -0.00019787 | 6.0105e-09 | -8.1961e-08 | 0.0012001 | 0.0012002 | 0.0012002 | 0.98008 | -0.13954 | 0.98007 | -0.1396 | 0.4445
4 | 0.0048795 | 0.0012226 | -0.0048792 | -0.0012226 | 2.8936e-07 | 4.7129e-09 | 0.0074063 | 0.0074064 | 0.0074064 | 0.98033 | -0.13775 | 0.98027 | -0.13818 | 2.7431
5 | -0.010056 | -0.0025186 | 0.010062 | 0.0025203 | 5.8363e-06 | 1.7382e-06 | 0.015263 | 0.015263 | 0.015263 | 0.98033 | -0.13775 | 0.98092 | -0.13356 | 5.6529
6 | 0.00032983 | 8.248e-05 | -0.00032983 | -8.2663e-05 | 2.2866e-09 | -1.8326e-07 | 0.00050072 | 0.00050079 | 0.00050079 | 0.98005 | -0.13978 | 0.98004 | -0.13983 | 0.18548
7 | 0.00043667 | 0.00010918 | -0.00043667 | -0.00010944 | 5.5817e-09 | -2.5433e-07 | 0.00066289 | 0.00066299 | 0.00066299 | 0.98007 | -0.1396 | 0.98006 | -0.13969 | 0.24555
8 | 0.0022012 | 0.00055147 | -0.002201 | -0.00055163 | 1.1604e-07 | -1.6536e-07 | 0.0033412 | 0.0033413 | 0.0033413 | 0.98027 | -0.13818 | 0.98022 | -0.13856 | 1.2375
9 | -0.03094 | -0.0077383 | 0.030972 | 0.0077504 | 3.2322e-05 | 1.2134e-05 | 0.046929 | 0.046929 | 0.046929 | 0.98092 | -0.13356 | 0.98197 | -0.12599 | 17.381
10 | 0.020878 | 0.0052179 | -0.020861 | -0.005212 | 1.6426e-05 | 5.9864e-06 | 0.031666 | 0.031666 | 0.031666 | 0.98092 | -0.13356 | 0.98012 | -0.13928 | 11.7281
11 | 0.064515 | 0.016228 | -0.064507 | -0.016225 | 8.6357e-06 | 3.3031e-06 | 0.097783 | 0.097783 | 0.097783 | 0.98197 | -0.12599 | 0.98184 | -0.12695 | 36.2161
12 | -0.095487 | -0.023979 | 0.095711 | 0.024065 | 0.00022346 | 8.573e-05 | 0.14471 | 0.14471 | 0.14471 | 0.98197 | -0.12599 | 0.98434 | -0.10919 | 53.597
13 | 0.018101 | 0.0045202 | -0.018088 | -0.0045154 | 1.341e-05 | 4.7991e-06 | 0.027475 | 0.027476 | 0.027476 | 0.98012 | -0.13928 | 0.97937 | -0.14467 | 10.1761
14 | 0.063004 | 0.015849 | -0.062811 | -0.015775 | 0.00019293 | 7.3778e-05 | 0.095506 | 0.095506 | 0.095506 | 0.98184 | -0.12695 | 0.97874 | -0.14897 | 35.3727
15 | 0.0044273 | 0.0011091 | -0.0044265 | -0.0011091 | 7.7304e-07 | -5.4209e-08 | 0.0066924 | 0.0066926 | 0.0066926 | 0.98434 | -0.10919 | 0.98417 | -0.11045 | 2.4787
16 | -0.10014 | -0.025174 | 0.10077 | 0.025417 | 0.00063499 | 0.00024366 | 0.1514 | 0.1514 | 0.1514 | 0.98434 | -0.10919 | 0.99078 | -0.063959 | 56.0756
17 | 0.0025184 | 0.00063092 | -0.0025182 | -0.00063112 | 2.0028e-07 | -2.0425e-07 | 0.0038076 | 0.0038077 | 0.0038077 | 0.98417 | -0.11045 | 0.98409 | -0.11103 | 1.4103
18 | -0.10522 | -0.026532 | 0.10526 | 0.026549 | 4.51e-05 | 1.7197e-05 | 0.15808 | 0.15808 | 0.15808 | 0.99078 | -0.063959 | 0.99122 | -0.060902 | 29.2744
19 | 0.014157 | 0.0035302 | -0.014123 | -0.0035185 | 3.4288e-05 | 1.1696e-05 | 0.021503 | 0.021504 | 0.021504 | 0.97937 | -0.14467 | 0.97692 | -0.16238 | 7.9643
20 | 0.043335 | 0.010881 | -0.043306 | -0.01087 | 2.8195e-05 | 1.0705e-05 | 0.064844 | 0.064844 | 0.064844 | 0.99454 | -0.037855 | 0.99388 | -0.04254 | 24.0161
21 | -0.04661 | -0.011702 | 0.046654 | 0.011719 | 4.4554e-05 | 1.6946e-05 | 0.069744 | 0.069744 | 0.069744 | 0.99454 | -0.037855 | 0.99552 | -0.03098 | 25.8311
22 | 0.039374 | 0.0098844 | -0.039341 | -0.0098719 | 3.3058e-05 | 1.2517e-05 | 0.058956 | 0.058956 | 0.058956 | 0.99388 | -0.04254 | 0.99301 | -0.04859 | 21.8354
23 | 0.11876 | 0.029995 | -0.11849 | -0.029893 | 0.00026622 | 0.00010169 | 0.17759 | 0.1776 | 0.1776 | 0.99552 | -0.03098 | 0.99322 | -0.04696 | 32.888
24 | -0.16877 | -0.042554 | 0.16906 | 0.042667 | 0.00029475 | 0.00011298 | 0.25235 | 0.25235 | 0.25235 | 0.99552 | -0.03098 | 0.99732 | -0.018539 | 46.7316
25 | 0.036463 | 0.0091507 | -0.03645 | -0.0091459 | 1.2794e-05 | 4.8318e-06 | 0.054644 | 0.054644 | 0.054644 | 0.99301 | -0.04859 | 0.99265 | -0.051119 | 20.2384
26 | 0.11356 | 0.028656 | -0.11346 | -0.028619 | 9.732e-05 | 3.7152e-05 | 0.1702 | 0.1702 | 0.1702 | 0.99322 | -0.04696 | 0.99234 | -0.053071 | 31.5187
27 | -0.17228 | -0.043474 | 0.17273 | 0.043646 | 0.00044946 | 0.0001723 | 0.25715 | 0.25715 | 0.25715 | 0.99732 | -0.018539 | 1 | 0 | 47.6211
28 | 0.032532 | 0.0081637 | -0.032476 | -0.008143 | 5.526e-05 | 2.0773e-05 | 0.048769 | 0.04877 | 0.04877 | 0.99265 | -0.051119 | 0.99092 | -0.063378 | 18.0628
29 | 0.10826 | 0.027315 | -0.10814 | -0.02727 | 0.00011881 | 4.5323e-05 | 0.1624 | 0.1624 | 0.1624 | 0.99234 | -0.053071 | 0.99122 | -0.060902 | 30.0739
30 | 0.019323 | 0.0048453 | -0.019298 | -0.0048365 | 2.4475e-05 | 8.7919e-06 | 0.028753 | 0.028753 | 0.028753 | 1 | 0 | 0.99869 | -0.0091507 | 10.6494
31 | 0.030088 | 0.0075462 | -0.030052 | -0.0075327 | 3.6032e-05 | 1.3495e-05 | 0.045184 | 0.045184 | 0.045184 | 0.99092 | -0.063378 | 0.98969 | -0.072026 | 16.735
32 | 0.002388 | 0.00059673 | -0.0023875 | -0.00059734 | 4.9487e-07 | -6.0421e-07 | 0.0035853 | 0.0035856 | 0.0035856 | 0.99092 | -0.063378 | 0.9907 | -0.064882 | 1.328
33 | 0.006894 | 0.0017277 | -0.0068929 | -0.0017275 | 1.1102e-06 | 2.064e-07 | 0.010272 | 0.010272 | 0.010272 | 0.99869 | -0.0091507 | 0.99853 | -0.010314 | 3.8044
34 | 0.017904 | 0.0044879 | -0.0179 | -0.0044863 | 4.6539e-06 | 1.6635e-06 | 0.027221 | 0.027221 | 0.027221 | 0.97874 | -0.14897 | 0.97847 | -0.15085 | 10.0819
35 | 0.044907 | 0.011287 | -0.044879 | -0.011276 | 2.8075e-05 | 1.0677e-05 | 0.068285 | 0.068285 | 0.068285 | 0.97874 | -0.14897 | 0.97811 | -0.15347 | 25.2908
36 | 0.027028 | 0.0067748 | -0.027027 | -0.0067745 | 6.7655e-07 | 2.5177e-07 | 0.040637 | 0.040638 | 0.040638 | 0.98969 | -0.072026 | 0.98967 | -0.072207 | 15.0509
37 | 0.0023875 | 0.00059734 | -0.0023868 | -0.00059818 | 6.9168e-07 | -8.4372e-07 | 0.0035856 | 0.003586 | 0.003586 | 0.9907 | -0.064882 | 0.99041 | -0.066979 | 1.3281
38 | 0.015849 | 0.003973 | -0.015841 | -0.0039701 | 8.5206e-06 | 2.9684e-06 | 0.023831 | 0.023831 | 0.023831 | 0.98967 | -0.072207 | 0.98912 | -0.076091 | 8.8262
39 | -0.038022 | -0.0095422 | 0.038143 | 0.0095882 | 0.00012129 | 4.5929e-05 | 0.058039 | 0.058038 | 0.058039 | 0.9749 | -0.17637 | 0.97811 | -0.15347 | 21.4958
40 | 0.033786 | 0.0084806 | -0.033745 | -0.008465 | 4.1384e-05 | 1.5606e-05 | 0.051573 | 0.051574 | 0.051574 | 0.9749 | -0.17637 | 0.97367 | -0.18521 | 19.1013
41 | 0.0067355 | 0.001688 | -0.0067337 | -0.0016876 | 1.7622e-06 | 3.4028e-07 | 0.010247 | 0.010247 | 0.010247 | 0.97811 | -0.15347 | 0.97784 | -0.15536 | 3.7952
42 | 0.033745 | 0.008465 | -0.03372 | -0.0084558 | 2.4457e-05 | 9.2234e-06 | 0.051574 | 0.051574 | 0.051574 | 0.97367 | -0.18521 | 0.97294 | -0.19044 | 19.1013
43 | 0.026342 | 0.0066066 | -0.02631 | -0.0065948 | 3.1835e-05 | 1.1854e-05 | 0.040289 | 0.040289 | 0.040289 | 0.97294 | -0.19044 | 0.97172 | -0.19916 | 14.922
44 | 0.01246 | 0.0031229 | -0.012455 | -0.0031215 | 4.2672e-06 | 1.4021e-06 | 0.018948 | 0.018948 | 0.018948 | 0.97847 | -0.15085 | 0.97813 | -0.15333 | 7.0179
45 | -0.0061461 | -0.0015403 | 0.0061468 | 0.0015404 | 6.4418e-07 | 1.0343e-07 | 0.0094126 | 0.0094126 | 0.0094126 | 0.97162 | -0.19992 | 0.97172 | -0.19916 | 3.4862
46 | 0.0061461 | 0.0015403 | -0.006145 | -0.0015401 | 1.0866e-06 | 1.7454e-07 | 0.0094126 | 0.0094127 | 0.0094127 | 0.97162 | -0.19992 | 0.97144 | -0.2012 | 3.4862
47 | 0.020163 | 0.0050544 | -0.020156 | -0.0050517 | 7.4528e-06 | 2.7113e-06 | 0.030877 | 0.030877 | 0.030877 | 0.97172 | -0.19916 | 0.97135 | -0.20183 | 11.4358
48 | 0.0057976 | 0.0014529 | -0.0057965 | -0.0014527 | 1.1724e-06 | 1.4783e-07 | 0.0088198 | 0.0088199 | 0.0088199 | 0.97813 | -0.15333 | 0.97792 | -0.15479 | 3.2666
49 | 0.012965 | 0.0032496 | -0.012962 | -0.0032486 | 2.9096e-06 | 9.728e-07 | 0.019862 | 0.019862 | 0.019862 | 0.97135 | -0.20183 | 0.97113 | -0.20345 | 7.3562
50 | 0.0027602 | 0.00067777 | -0.0027584 | -0.00067911 | 1.8076e-06 | -1.3321e-06 | 0.0042136 | 0.0042143 | 0.0042143 | 0.9736 | -0.18687 | 0.97294 | -0.19178 | 1.5608
51 | -0.0027602 | -0.00067777 | 0.0027613 | 0.00067695 | 1.1102e-06 | -8.1986e-07 | 0.0042136 | 0.0042131 | 0.0042136 | 0.9736 | -0.18687 | 0.974 | -0.18384 | 1.5606
52 | 0.0023278 | 0.0005712 | -0.0023255 | -0.00057398 | 2.3398e-06 | -2.7779e-06 | 0.0035558 | 0.0035571 | 0.0035571 | 0.97294 | -0.19178 | 0.97193 | -0.1993 | 1.3174
53 | -0.0039682 | -0.00097944 | 0.0039703 | 0.00097911 | 2.0957e-06 | -3.3401e-07 | 0.006057 | 0.0060566 | 0.006057 | 0.974 | -0.18384 | 0.97453 | -0.17991 | 2.2433
54 | 0.0023255 | 0.00057398 | -0.0023245 | -0.00057509 | 9.3564e-07 | -1.1079e-06 | 0.0035571 | 0.0035576 | 0.0035576 | 0.97193 | -0.1993 | 0.97153 | -0.20229 | 1.3176
55 | -0.001723 | -0.00042793 | 0.001723 | 0.00042781 | 4.7146e-08 | -1.1785e-07 | 0.0026303 | 0.0026303 | 0.0026303 | 0.97421 | -0.18226 | 0.97424 | -0.18206 | 0.9742
56 | 0.0013684 | 0.00033905 | -0.0013683 | -0.00033935 | 7.3126e-08 | -3.0632e-07 | 0.0020886 | 0.0020888 | 0.0020888 | 0.97421 | -0.18226 | 0.97416 | -0.18266 | 0.77362
57 | -0.0019061 | -0.0004737 | 0.0019067 | 0.0004726 | 5.5693e-07 | -1.0989e-06 | 0.0029099 | 0.0029095 | 0.0029099 | 0.97424 | -0.18206 | 0.97453 | -0.17991 | 1.0778
58 | 0.00034679 | 8.3342e-05 | -0.00034674 | -8.6902e-05 | 5.0225e-08 | -3.5599e-06 | 0.00052846 | 0.00052972 | 0.00052972 | 0.97416 | -0.18266 | 0.97401 | -0.18375 | 0.19619
59 | -0.005877 | -0.0014517 | 0.0058844 | 0.0014527 | 7.3632e-06 | 1.0006e-06 | 0.008966 | 0.0089654 | 0.008966 | 0.97453 | -0.17991 | 0.97579 | -0.1706 | 3.3208
60 | 0.00063715 | 0.0001581 | -0.00063709 | -0.00015942 | 6.4376e-08 | -1.3174e-06 | 0.00097531 | 0.00097579 | 0.00097579 | 0.97153 | -0.20229 | 0.97142 | -0.20303 | 0.3614
61 | 0.0016874 | 0.00041699 | -0.0016874 | -0.00041701 | 6.0068e-09 | -1.5565e-08 | 0.0025823 | 0.0025823 | 0.0025823 | 0.97153 | -0.20229 | 0.97152 | -0.20232 | 0.95642
62 | 0.011425 | 0.0028633 | -0.011425 | -0.0028633 | 1.3474e-08 | 4.2439e-09 | 0.017187 | 0.017187 | 0.017187 | 0.98912 | -0.076091 | 0.98912 | -0.076099 | 6.3657
63 | 0.014123 | 0.0035185 | -0.014112 | -0.0035149 | 1.0481e-05 | 3.5767e-06 | 0.021504 | 0.021504 | 0.021504 | 0.97692 | -0.16238 | 0.97618 | -0.1678 | 7.9644
64 | 0.0094855 | 0.0023554 | -0.0094819 | -0.0023543 | 3.6061e-06 | 1.0411e-06 | 0.014451 | 0.014451 | 0.014451 | 0.97618 | -0.1678 | 0.97579 | -0.1706 | 5.3523
65 | -0.0067138 | -0.0016826 | 0.0067153 | 0.0016829 | 1.4926e-06 | 2.946e-07 | 0.01029 | 0.010289 | 0.01029 | 0.97091 | -0.20506 | 0.97113 | -0.20345 | 3.811
66 | -0.0011376 | -0.00028096 | 0.0011379 | 0.00027929 | 2.7002e-07 | -1.6634e-06 | 0.0017414 | 0.0017407 | 0.0017414 | 0.97128 | -0.20409 | 0.97152 | -0.20232 | 0.64495
67 | 0.00047219 | 0.00011418 | -0.00047217 | -0.00011509 | 2.4007e-08 | -9.0396e-07 | 0.00072193 | 0.00072225 | 0.00072225 | 0.97128 | -0.20409 | 0.97123 | -0.20448 | 0.2675
68 | 0.00047217 | 0.00011509 | -0.00047213 | -0.0001167 | 4.288e-08 | -1.6123e-06 | 0.00072225 | 0.00072282 | 0.00072282 | 0.97123 | -0.20448 | 0.97114 | -0.20517 | 0.26771
69 | 0.00047213 | 0.0001167 | -0.00047208 | -0.00011832 | 4.3075e-08 | -1.6167e-06 | 0.00072282 | 0.00072341 | 0.00072341 | 0.97114 | -0.20517 | 0.97105 | -0.20583 | 0.26793
70 | 0.00044503 | 0.00011128 | -0.00044502 | -0.00011153 | 5.9617e-09 | -2.5226e-07 | 0.0006816 | 0.00068169 | 0.00068169 | 0.97142 | -0.20303 | 0.97141 | -0.20313 | 0.25248

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.19699 | 0.049528

## res_load
| p_mw | q_mvar
0 | 0.0036786 | 0.00092195
1 | 0.00037621 | 9.4286e-05
2 | 0.00035386 | 8.8686e-05
3 | 0.002678 | 0.00067118
4 | 0.00032983 | 8.2663e-05
5 | 0.00043667 | 0.00010944
6 | 0.002201 | 0.00055163
7 | 0.0027602 | 0.00069178
8 | 0.0015026 | 0.00037658
9 | 0.0019081 | 0.00047821
10 | 0.0044464 | 0.0011144
11 | 0.0039309 | 0.00098517
12 | 0.0032753 | 0.00082087
13 | 0.0039327 | 0.00098562
14 | 0.0033532 | 0.0008404
15 | 0.0028776 | 0.0007212
16 | 0.0049356 | 0.001237
17 | 0.0032193 | 0.00080683
18 | 0.0039187 | 0.00098213
19 | 0.0052031 | 0.001304
20 | 0.0041375 | 0.001037
21 | 0.0028758 | 0.00072075
22 | 0.012404 | 0.0031087
23 | 0.0025182 | 0.00063112
24 | 0.0068929 | 0.0017275
25 | 0.0030242 | 0.00075793
26 | 0.011178 | 0.0028015
27 | 0.0023868 | 0.00059818
28 | 0.0042358 | 0.0010616
29 | 0.0067337 | 0.0016876
30 | 0.0073783 | 0.0018492
31 | 0.0054401 | 0.0013634
32 | 0.006145 | 0.0015401
33 | 0.0066578 | 0.0016686
34 | 0.0071904 | 0.0018021
35 | 0.00043054 | 0.0001079
36 | 0.0012069 | 0.00030249
37 | 0.00035464 | 8.8881e-05
38 | 0.00018309 | 4.5887e-05
39 | 0.0010215 | 0.00025601
40 | 0.00034674 | 8.6902e-05
41 | 0.004416 | 0.0011067
42 | 0.0046267 | 0.0011596
43 | 0.0035975 | 0.00090162
44 | 0.0067138 | 0.0016826
45 | 0.0062472 | 0.0015657
46 | 0.011425 | 0.0028633
47 | 0.0057965 | 0.0014527
48 | 0.00066544 | 0.00016677
49 | 0.00054948 | 0.00013771
50 | 0.00019206 | 4.8134e-05
51 | 0.00047208 | 0.00011832
52 | 0.00044502 | 0.00011153

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1