## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1502-14_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1502-14_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1502-14_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1502-14_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1502-14_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1502-14_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1502-14_0_3_node_22 | 0.4 | n |  | TRUE
7 | bus_LV_1502-14_0_3_node_19 | 0.4 | n |  | TRUE
8 | bus_LV_1502-14_0_3_node_12 | 0.4 | n |  | TRUE
9 | bus_LV_1502-14_0_3_node_23 | 0.4 | n |  | TRUE
10 | bus_LV_1502-14_0_3_node_20 | 0.4 | n |  | TRUE
11 | bus_LV_1502-14_0_3_node_13 | 0.4 | n |  | TRUE
12 | bus_LV_1502-14_0_3_node_16 | 0.4 | n |  | TRUE
13 | bus_LV_1502-14_0_3_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_1502-14_0_3_node_27 | 0.4 | n |  | TRUE
15 | bus_LV_1502-14_0_3_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_1502-14_0_3_node_28 | 0.4 | n |  | TRUE
17 | bus_LV_1502-14_0_3_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_1502-14_0_3_node_6 | 0.4 | n |  | TRUE
19 | bus_LV_1502-14_0_3_node_7 | 0.4 | n |  | TRUE
20 | bus_LV_1502-14_0_3_node_9 | 0.4 | n |  | TRUE
21 | bus_LV_1502-14_0_3_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_1502-14_0_3_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_1502-14_0_3_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_1502-14_0_3_node_29 | 0.4 | n |  | TRUE
25 | bus_LV_1502-14_0_3_node_26 | 0.4 | n |  | TRUE
26 | bus_LV_1502-14_0_3_node_25 | 0.4 | n |  | TRUE
27 | bus_LV_1502-14_0_3_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_1502-14_0_3_node_24 | 0.4 | n |  | TRUE
29 | bus_MV_142_1_node_76 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1502-14_0_3_load_0 | 0 | 0.030099 | 0.0075434 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1502-14_0_3_load_1 | 1 | 0.0093067 | 0.0023325 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1502-14_0_3_load_2 | 2 | 0.020438 | 0.0051221 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1502-14_0_3_load_3 | 3 | 0.017536 | 0.0043949 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1502-14_0_3_load_19 | 7 | 0.0011664 | 0.00029233 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1502-14_0_3_load_12 | 8 | 0.0058523 | 0.0014667 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1502-14_0_3_load_23 | 9 | 0.004693 | 0.0011762 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1502-14_0_3_load_20 | 10 | 0.0038056 | 0.00095378 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1502-14_0_3_load_16 | 12 | 0.0058498 | 0.0014661 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1502-14_0_3_load_27 | 14 | 0.019917 | 0.0049917 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1502-14_0_3_load_28 | 16 | 0.020804 | 0.0052141 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1502-14_0_3_load_6 | 18 | 0.0065994 | 0.001654 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1502-14_0_3_load_10 | 21 | 0.0065423 | 0.0016397 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1502-14_0_3_load_18 | 22 | 0.0065429 | 0.0016398 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1502-14_0_3_load_17 | 23 | 0.0058523 | 0.0014667 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1502-14_0_3_load_29 | 24 | 0.018337 | 0.0045956 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1502-14_0_3_load_26 | 25 | 0.0038548 | 0.00096612 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1502-14_0_3_load_24 | 28 | 0.052714 | 0.013211 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 8 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1502-14_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.01031 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
1 | LV_1502-14_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.011674 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1502-14_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0067625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
3 | LV_1502-14_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.020548 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1502-14_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.0097665 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
5 | LV_1502-14_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.10863 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1502-14_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.035227 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1502-14_0_3_line_7 | NAYY 4x150 SE | 5 | 8 | 0.013777 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_1502-14_0_3_line_8 | NAYY 4x150 SE | 6 | 9 | 0.064333 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1502-14_0_3_line_9 | NAYY 4x150 SE | 7 | 10 | 0.00095866 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1502-14_0_3_line_10 | NAYY 4x150 SE | 8 | 11 | 0.013681 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1502-14_0_3_line_11 | NAYY 4x150 SE | 9 | 28 | 0.0062943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1502-14_0_3_line_12 | NAYY 4x150 SE | 10 | 27 | 0.041556 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1502-14_0_3_line_13 | NAYY 4x150 SE | 11 | 12 | 0.011342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1502-14_0_3_line_14 | NAYY 4x150 SE | 11 | 13 | 0.048311 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1502-14_0_3_line_15 | NAYY 4x150 SE | 12 | 23 | 0.0073191 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1502-14_0_3_line_16 | NAYY 4x150 SE | 13 | 14 | 0.009568 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1502-14_0_3_line_17 | NAYY 4x150 SE | 13 | 15 | 0.033334 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1502-14_0_3_line_18 | NAYY 4x150 SE | 15 | 16 | 0.011039 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1502-14_0_3_line_19 | NAYY 4x150 SE | 15 | 17 | 0.013409 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1502-14_0_3_line_20 | NAYY 4x150 SE | 17 | 24 | 0.012311 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1502-14_0_3_line_21 | NAYY 4x150 SE | 18 | 19 | 0.022221 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1502-14_0_3_line_22 | NAYY 4x150 SE | 19 | 20 | 0.003651 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1502-14_0_3_line_23 | NAYY 4x150 SE | 19 | 21 | 0.005687 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1502-14_0_3_line_24 | NAYY 4x150 SE | 20 | 22 | 0.005868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1502-14_0_3_line_25 | NAYY 4x150 SE | 20 | 23 | 0.01594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1502-14_0_3_line_26 | NAYY 4x150 SE | 25 | 26 | 0.041688 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1502-14_0_3_line_27 | NAYY 4x150 SE | 26 | 27 | 0.028749 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1502-14_0_3_trafo_12 | 0.25 MVA 20/0.4 kV | 29 | 8 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2674527.6098 | 1203297.5855 | 2674537.3675 | 1203300.9162
1 | 2674516.5621 | 1203293.8146 | 2674527.6098 | 1203297.5855
2 | 2674537.3675 | 1203300.9162 | 2674543.7675 | 1203303.1007
3 | 2674499.4859 | 1203283.5851 | 2674505.2052 | 1203289.9381 | 2674516.5621 | 1203293.8146
4 | 2674553.0103 | 1203306.2556 | 2674543.7675 | 1203303.1007
5 | 2674499.4859 | 1203283.5851 | 2674513.8266 | 1203274.1025 | 2674551.9346 | 1203247.3613 | 2674587.7412 | 1203220.2914
6 | 2674499.4859 | 1203283.5851 | 2674470.9366 | 1203304.2215
7 | 2674553.0103 | 1203306.2556 | 2674564.8536 | 1203310.9063 | 2674565.0201 | 1203311.9463
8 | 2674587.7412 | 1203220.2914 | 2674616.8186 | 1203251.8963 | 2674603.3082 | 1203267.9931 | 2674602.9416 | 1203268.0523
9 | 2674470.1596 | 1203304.7831 | 2674470.9366 | 1203304.2215
10 | 2674567.1831 | 1203325.4555 | 2674565.0201 | 1203311.9463
11 | 2674596.7278 | 1203269.056 | 2674602.9416 | 1203268.0523
12 | 2674437.3277 | 1203330.2281 | 2674443.9277 | 1203324.529 | 2674451.1967 | 1203318.8828 | 2674462.8043 | 1203310.0997 | 2674470.1596 | 1203304.7831
13 | 2674567.1831 | 1203325.4555 | 2674578.3897 | 1203327.2052
14 | 2674548.1456 | 1203358.2382 | 2674553.9618 | 1203358.6443 | 2674556.3091 | 1203327.2764 | 2674567.1831 | 1203325.4555
15 | 2674578.3897 | 1203327.2052 | 2674585.6212 | 1203328.3343
16 | 2674544.9414 | 1203351.583 | 2674544.9152 | 1203353.6839 | 2674548.1977 | 1203354.0696 | 2674548.1456 | 1203358.2382
17 | 2674548.1456 | 1203358.2382 | 2674553.9618 | 1203358.6443 | 2674581.4011 | 1203360.5213
18 | 2674579.0315 | 1203352.231 | 2674578.7201 | 1203354.0171 | 2674582.0068 | 1203354.6697 | 2674581.4011 | 1203360.5213
19 | 2674581.4011 | 1203360.5213 | 2674585.788 | 1203360.8207 | 2674594.6938 | 1203362.4329
20 | 2674600.0653 | 1203354.584 | 2674600.0414 | 1203356.496 | 2674596.0427 | 1203356.1792 | 2674594.6938 | 1203362.4329
21 | 2674605.0653 | 1203330.7872 | 2674624.0397 | 1203332.9144 | 2674627.1483 | 1203333.2571
22 | 2674601.4253 | 1203330.386 | 2674605.0653 | 1203330.7872
23 | 2674605.8889 | 1203325.1607 | 2674605.0653 | 1203330.7872
24 | 2674602.4335 | 1203324.6061 | 2674601.4253 | 1203330.386
25 | 2674601.4253 | 1203330.386 | 2674591.8735 | 1203329.3105 | 2674585.6212 | 1203328.3343
26 | 2674418.8293 | 1203352.1779 | 2674428.1196 | 1203356.5185 | 2674459.5528 | 1203356.7504
27 | 2674437.3277 | 1203330.2281 | 2674429.9603 | 1203337.6631 | 2674424.4386 | 1203344.1539 | 2674418.8293 | 1203352.1779

## bus_geodata
| x | y | coords
0 | 2674527.6098 | 1203297.5855
1 | 2674537.3675 | 1203300.9162
2 | 2674516.5621 | 1203293.8146
3 | 2674543.7675 | 1203303.1007
4 | 2674499.4859 | 1203283.5851
5 | 2674553.0103 | 1203306.2556
6 | 2674587.7412 | 1203220.2914
7 | 2674470.9366 | 1203304.2215
8 | 2674565.0201 | 1203311.9463
9 | 2674602.9416 | 1203268.0523
10 | 2674470.1596 | 1203304.7831
11 | 2674567.1831 | 1203325.4555
12 | 2674578.3897 | 1203327.2052
13 | 2674548.1456 | 1203358.2382
14 | 2674544.9414 | 1203351.583
15 | 2674581.4011 | 1203360.5213
16 | 2674579.0315 | 1203352.231
17 | 2674594.6938 | 1203362.4329
18 | 2674627.1483 | 1203333.2571
19 | 2674605.0653 | 1203330.7872
20 | 2674601.4253 | 1203330.386
21 | 2674605.8889 | 1203325.1607
22 | 2674602.4335 | 1203324.6061
23 | 2674585.6212 | 1203328.3343
24 | 2674600.0653 | 1203354.584
25 | 2674459.5528 | 1203356.7504
26 | 2674418.8293 | 1203352.1779
27 | 2674437.3277 | 1203330.2281
28 | 2674596.7278 | 1203269.056
29 | 2674567.1831 | 1203325.4555

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99608 | -0.02725 | 0.030099 | 0.0075434
1 | 0.99695 | -0.021198 | 0.0093067 | 0.0023325
2 | 0.99461 | -0.037446 | 0.020438 | 0.0051221
3 | 0.99756 | -0.016918 | 0.017536 | 0.0043949
4 | 0.99263 | -0.051211 | 0 | 0
5 | 0.99857 | -0.0098902 | 0 | 0
6 | 0.98354 | -0.11498 | 0 | 0
7 | 0.99218 | -0.054367 | 0.0011664 | 0.00029233
8 | 1 | 0 | -0.23701 | -0.05948
9 | 0.97815 | -0.15329 | 0.004693 | 0.0011762
10 | 0.99217 | -0.054441 | 0.0038056 | 0.00095378
11 | 0.99823 | -0.012374 | 0 | 0
12 | 0.99772 | -0.015942 | 0.0058498 | 0.0014661
13 | 0.99413 | -0.041074 | 0 | 0
14 | 0.99385 | -0.042999 | 0.019917 | 0.0049917
15 | 0.99225 | -0.054276 | 0 | 0
16 | 0.99192 | -0.056605 | 0.020804 | 0.0052141
17 | 0.9919 | -0.05677 | 0 | 0
18 | 0.99672 | -0.022922 | 0.0065994 | 0.001654
19 | 0.99693 | -0.021449 | 0 | 0
20 | 0.997 | -0.020967 | 0 | 0
21 | 0.99688 | -0.021823 | 0.0065423 | 0.0016397
22 | 0.99695 | -0.021353 | 0.0065429 | 0.0016398
23 | 0.99745 | -0.017817 | 0.0058523 | 0.0014667
24 | 0.99157 | -0.059061 | 0.018337 | 0.0045956
25 | 0.99155 | -0.058827 | 0.0038548 | 0.00096612
26 | 0.99178 | -0.057195 | 0 | 0
27 | 0.99194 | -0.056069 | 0 | 0
28 | 0.97767 | -0.15676 | 0.052714 | 0.013211
29 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.11788 | -0.029688 | 0.11798 | 0.029726 | 9.9817e-05 | 3.8122e-05 | 0.17615 | 0.17615 | 0.17615 | 0.99608 | -0.02725 | 0.99695 | -0.021198 | 32.6205
1 | 0.087783 | 0.022145 | -0.087657 | -0.022097 | 0.00012536 | 4.8065e-05 | 0.13119 | 0.13119 | 0.13119 | 0.99608 | -0.02725 | 0.99461 | -0.037446 | 48.5879
2 | -0.12729 | -0.032059 | 0.12736 | 0.032088 | 7.6201e-05 | 2.9132e-05 | 0.19004 | 0.19004 | 0.19004 | 0.99695 | -0.021198 | 0.99756 | -0.016918 | 35.1929
3 | 0.06722 | 0.016974 | -0.06709 | -0.016925 | 0.00012979 | 4.9655e-05 | 0.10061 | 0.10061 | 0.10061 | 0.99461 | -0.037446 | 0.99263 | -0.051211 | 37.2635
4 | -0.1449 | -0.036483 | 0.14504 | 0.036537 | 0.00014243 | 5.4525e-05 | 0.2162 | 0.2162 | 0.2162 | 0.99756 | -0.016918 | 0.99857 | -0.0098902 | 40.0369
5 | 0.058257 | 0.014712 | -0.057739 | -0.014514 | 0.00051746 | 0.00019763 | 0.08737 | 0.087371 | 0.087371 | 0.99263 | -0.051211 | 0.98354 | -0.11498 | 32.3595
6 | 0.0088332 | 0.0022127 | -0.0088293 | -0.0022117 | 3.854e-06 | 1.0272e-06 | 0.013241 | 0.013241 | 0.013241 | 0.99263 | -0.051211 | 0.99218 | -0.054367 | 4.9042
7 | -0.14504 | -0.036537 | 0.14524 | 0.036614 | 0.00020092 | 7.6915e-05 | 0.2162 | 0.2162 | 0.2162 | 0.99857 | -0.0098902 | 1 | 0 | 40.0369
8 | 0.057739 | 0.014514 | -0.057433 | -0.014397 | 0.00030644 | 0.00011705 | 0.087371 | 0.087371 | 0.087371 | 0.98354 | -0.11498 | 0.97815 | -0.15329 | 32.3596
9 | 0.0076629 | 0.0019194 | -0.0076628 | -0.0019194 | 7.9002e-08 | 1.8004e-08 | 0.011492 | 0.011492 | 0.011492 | 0.99218 | -0.054367 | 0.99217 | -0.054441 | 4.2563
10 | 0.090967 | 0.022866 | -0.090811 | -0.022806 | 0.00015648 | 6.0004e-05 | 0.13538 | 0.13538 | 0.13538 | 1 | 0 | 0.99823 | -0.012374 | 50.1424
11 | 0.05274 | 0.013221 | -0.052714 | -0.013211 | 2.5283e-05 | 9.6452e-06 | 0.080232 | 0.080232 | 0.080232 | 0.97815 | -0.15329 | 0.97767 | -0.15676 | 29.7155
12 | 0.0038572 | 0.00096557 | -0.0038563 | -0.00096577 | 8.6767e-07 | -2.0284e-07 | 0.0057844 | 0.0057846 | 0.0057846 | 0.99217 | -0.054441 | 0.99194 | -0.056069 | 2.1425
13 | 0.03142 | 0.0078783 | -0.031405 | -0.0078724 | 1.5527e-05 | 5.8238e-06 | 0.046838 | 0.046838 | 0.046838 | 0.99823 | -0.012374 | 0.99772 | -0.015942 | 17.3476
14 | 0.059391 | 0.014928 | -0.059154 | -0.014837 | 0.00023636 | 9.0279e-05 | 0.088546 | 0.088546 | 0.088546 | 0.99823 | -0.012374 | 0.99413 | -0.041074 | 32.795
15 | 0.025555 | 0.0064063 | -0.025548 | -0.0064039 | 6.6346e-06 | 2.4562e-06 | 0.038114 | 0.038114 | 0.038114 | 0.99772 | -0.015942 | 0.99745 | -0.017817 | 14.1163
16 | 0.019923 | 0.0049936 | -0.019917 | -0.0049917 | 5.3092e-06 | 1.918e-06 | 0.02982 | 0.02982 | 0.02982 | 0.99413 | -0.041074 | 0.99385 | -0.042999 | 11.0446
17 | 0.039232 | 0.0098436 | -0.03916 | -0.0098164 | 7.1735e-05 | 2.7159e-05 | 0.058726 | 0.058726 | 0.058726 | 0.99413 | -0.041074 | 0.99225 | -0.054276 | 21.7505
18 | 0.020811 | 0.0052165 | -0.020804 | -0.0052141 | 6.7094e-06 | 2.438e-06 | 0.031209 | 0.031209 | 0.031209 | 0.99225 | -0.054276 | 0.99192 | -0.056605 | 11.559
19 | 0.018349 | 0.0045999 | -0.018342 | -0.0045977 | 6.3355e-06 | 2.2636e-06 | 0.027517 | 0.027517 | 0.027517 | 0.99225 | -0.054276 | 0.9919 | -0.05677 | 10.1915
20 | 0.018342 | 0.0045977 | -0.018337 | -0.0045956 | 5.8168e-06 | 2.0784e-06 | 0.027517 | 0.027517 | 0.027517 | 0.9919 | -0.05677 | 0.99157 | -0.059061 | 10.1915
21 | -0.0065994 | -0.001654 | 0.0066007 | 0.0016542 | 1.3459e-06 | 2.2798e-07 | 0.0098523 | 0.0098522 | 0.0098523 | 0.99672 | -0.022922 | 0.99693 | -0.021449 | 3.649
22 | -0.013143 | -0.0032939 | 0.013144 | 0.0032942 | 8.7678e-07 | 2.8962e-07 | 0.019618 | 0.019618 | 0.019618 | 0.99693 | -0.021449 | 0.997 | -0.020967 | 7.2658
23 | 0.0065426 | 0.0016397 | -0.0065423 | -0.0016397 | 3.3842e-07 | 5.6014e-08 | 0.0097655 | 0.0097655 | 0.0097655 | 0.99693 | -0.021449 | 0.99688 | -0.021823 | 3.6169
24 | 0.0065433 | 0.0016399 | -0.0065429 | -0.0016398 | 3.4921e-07 | 5.7794e-08 | 0.0097658 | 0.0097658 | 0.0097658 | 0.997 | -0.020967 | 0.99695 | -0.021353 | 3.617
25 | -0.019688 | -0.0049341 | 0.019696 | 0.0049372 | 8.5878e-06 | 3.095e-06 | 0.029383 | 0.029383 | 0.029383 | 0.997 | -0.020967 | 0.99745 | -0.017817 | 10.8828
26 | -0.0038548 | -0.00096612 | 0.0038557 | 0.00096591 | 8.7053e-07 | -2.0302e-07 | 0.005785 | 0.0057848 | 0.005785 | 0.99155 | -0.058827 | 0.99178 | -0.057195 | 2.1426
27 | -0.0038557 | -0.00096591 | 0.0038563 | 0.00096577 | 6.003e-07 | -1.4017e-07 | 0.0057848 | 0.0057846 | 0.0057848 | 0.99178 | -0.057195 | 0.99194 | -0.056069 | 2.1425

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.24286 | 0.060947

## res_load
| p_mw | q_mvar
0 | 0.030099 | 0.0075434
1 | 0.0093067 | 0.0023325
2 | 0.020438 | 0.0051221
3 | 0.017536 | 0.0043949
4 | 0.0011664 | 0.00029233
5 | 0.0058523 | 0.0014667
6 | 0.004693 | 0.0011762
7 | 0.0038056 | 0.00095378
8 | 0.0058498 | 0.0014661
9 | 0.019917 | 0.0049917
10 | 0.020804 | 0.0052141
11 | 0.0065994 | 0.001654
12 | 0.0065423 | 0.0016397
13 | 0.0065429 | 0.0016398
14 | 0.0058523 | 0.0014667
15 | 0.018337 | 0.0045956
16 | 0.0038548 | 0.00096612
17 | 0.052714 | 0.013211

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1