## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1502-20_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1502-20_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1502-20_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1502-20_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1502-20_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1502-20_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1502-20_0_3_node_37 | 0.4 | n |  | TRUE
7 | bus_LV_1502-20_0_3_node_36 | 0.4 | n |  | TRUE
8 | bus_LV_1502-20_0_3_node_13 | 0.4 | n |  | TRUE
9 | bus_LV_1502-20_0_3_node_38 | 0.4 | n |  | TRUE
10 | bus_LV_1502-20_0_3_node_35 | 0.4 | n |  | TRUE
11 | bus_LV_1502-20_0_3_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_1502-20_0_3_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_1502-20_0_3_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_1502-20_0_3_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_1502-20_0_3_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_1502-20_0_3_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_1502-20_0_3_node_28 | 0.4 | n |  | TRUE
18 | bus_LV_1502-20_0_3_node_29 | 0.4 | n |  | TRUE
19 | bus_LV_1502-20_0_3_node_18 | 0.4 | n |  | TRUE
20 | bus_LV_1502-20_0_3_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_1502-20_0_3_node_24 | 0.4 | n |  | TRUE
22 | bus_LV_1502-20_0_3_node_30 | 0.4 | n |  | TRUE
23 | bus_LV_1502-20_0_3_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_1502-20_0_3_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_1502-20_0_3_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_1502-20_0_3_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_1502-20_0_3_node_46 | 0.4 | n |  | TRUE
28 | bus_LV_1502-20_0_3_node_40 | 0.4 | n |  | TRUE
29 | bus_LV_1502-20_0_3_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_1502-20_0_3_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_1502-20_0_3_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_1502-20_0_3_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_1502-20_0_3_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_1502-20_0_3_node_27 | 0.4 | n |  | TRUE
35 | bus_LV_1502-20_0_3_node_25 | 0.4 | n |  | TRUE
36 | bus_LV_1502-20_0_3_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_1502-20_0_3_node_47 | 0.4 | n |  | TRUE
38 | bus_LV_1502-20_0_3_node_48 | 0.4 | n |  | TRUE
39 | bus_LV_1502-20_0_3_node_45 | 0.4 | n |  | TRUE
40 | bus_LV_1502-20_0_3_node_44 | 0.4 | n |  | TRUE
41 | bus_LV_1502-20_0_3_node_43 | 0.4 | n |  | TRUE
42 | bus_LV_1502-20_0_3_node_42 | 0.4 | n |  | TRUE
43 | bus_LV_1502-20_0_3_node_31 | 0.4 | n |  | TRUE
44 | bus_LV_1502-20_0_3_node_32 | 0.4 | n |  | TRUE
45 | bus_LV_1502-20_0_3_node_33 | 0.4 | n |  | TRUE
46 | bus_LV_1502-20_0_3_node_34 | 0.4 | n |  | TRUE
47 | bus_LV_1502-20_0_3_node_39 | 0.4 | n |  | TRUE
48 | bus_LV_1502-20_0_3_node_41 | 0.4 | n |  | TRUE
49 | bus_MV_142_1_node_292 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1502-20_0_3_load_0 | 0 | 0.0047657 | 0.0011944 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1502-20_0_3_load_1 | 1 | 0.0051423 | 0.0012888 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1502-20_0_3_load_3 | 3 | 0.0052116 | 0.0013061 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1502-20_0_3_load_5 | 5 | 0.0052799 | 0.0013233 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1502-20_0_3_load_37 | 6 | 0.0060353 | 0.0015126 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1502-20_0_3_load_36 | 7 | 0.0053997 | 0.0013533 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1502-20_0_3_load_13 | 8 | 0.0052352 | 0.0013121 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1502-20_0_3_load_35 | 10 | 0.0059137 | 0.0014821 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1502-20_0_3_load_11 | 11 | 0.012702 | 0.0031833 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1502-20_0_3_load_6 | 12 | 0.0015323 | 0.00038403 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1502-20_0_3_load_7 | 13 | 0.00088229 | 0.00022112 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1502-20_0_3_load_8 | 14 | 0.0012144 | 0.00030436 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1502-20_0_3_load_9 | 15 | 0.0014744 | 0.00036952 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1502-20_0_3_load_10 | 16 | 0.0055698 | 0.0013959 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1502-20_0_3_load_28 | 17 | 0.0014585 | 0.00036553 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1502-20_0_3_load_29 | 18 | 0.0035906 | 0.00089988 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1502-20_0_3_load_18 | 19 | 0.0014712 | 0.00036871 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1502-20_0_3_load_17 | 20 | 0.00072688 | 0.00018217 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1502-20_0_3_load_24 | 21 | 0.00055744 | 0.00013971 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1502-20_0_3_load_12 | 23 | 0.0044889 | 0.001125 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1502-20_0_3_load_14 | 24 | 0.0038397 | 0.00096233 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1502-20_0_3_load_15 | 25 | 0.0073603 | 0.0018447 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1502-20_0_3_load_16 | 26 | 0.0080887 | 0.0020272 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1502-20_0_3_load_46 | 27 | 0.0052687 | 0.0013205 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1502-20_0_3_load_40 | 28 | 0.022345 | 0.0056001 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1502-20_0_3_load_19 | 29 | 0.0017412 | 0.00043639 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1502-20_0_3_load_22 | 32 | 0.00028213 | 7.0709e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1502-20_0_3_load_23 | 33 | 0.00083178 | 0.00020846 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1502-20_0_3_load_25 | 35 | 0.00023475 | 5.8833e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1502-20_0_3_load_26 | 36 | 0.0033516 | 0.00083999 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1502-20_0_3_load_47 | 37 | 0.0043425 | 0.0010883 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1502-20_0_3_load_48 | 38 | 0.0025909 | 0.00064935 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1502-20_0_3_load_45 | 39 | 0.0049227 | 0.0012337 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1502-20_0_3_load_44 | 40 | 0.012671 | 0.0031757 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1502-20_0_3_load_43 | 41 | 0.0032482 | 0.00081408 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1502-20_0_3_load_42 | 42 | 0.0022073 | 0.00055321 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1502-20_0_3_load_31 | 43 | 0.0061617 | 0.0015443 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1502-20_0_3_load_32 | 44 | 0.028944 | 0.0072542 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1502-20_0_3_load_33 | 45 | 0.0067999 | 0.0017042 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1502-20_0_3_load_34 | 46 | 0.0036277 | 0.00090918 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1502-20_0_3_load_39 | 47 | 0.0056795 | 0.0014234 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1502-20_0_3_load_41 | 48 | 0.001666 | 0.00041754 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 4 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1502-20_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.029412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1502-20_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.027567 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1502-20_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.00011694 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1502-20_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.045147 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1502-20_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.02966 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1502-20_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.010062 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1502-20_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.022984 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1502-20_0_3_line_7 | NAYY 4x150 SE | 5 | 8 | 0.0029278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1502-20_0_3_line_8 | NAYY 4x150 SE | 6 | 9 | 0.0033034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1502-20_0_3_line_9 | NAYY 4x150 SE | 7 | 10 | 0.0031114 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1502-20_0_3_line_10 | NAYY 4x150 SE | 8 | 11 | 0.024978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1502-20_0_3_line_11 | NAYY 4x150 SE | 9 | 47 | 0.015741 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1502-20_0_3_line_12 | NAYY 4x150 SE | 9 | 28 | 0.017207 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1502-20_0_3_line_13 | NAYY 4x150 SE | 10 | 46 | 0.017598 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1502-20_0_3_line_14 | NAYY 4x150 SE | 11 | 23 | 0.0079385 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1502-20_0_3_line_15 | NAYY 4x150 SE | 12 | 13 | 0.020466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1502-20_0_3_line_16 | NAYY 4x150 SE | 12 | 14 | 0.049493 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1502-20_0_3_line_17 | NAYY 4x150 SE | 13 | 15 | 0.017814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1502-20_0_3_line_18 | NAYY 4x150 SE | 14 | 16 | 0.014121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1502-20_0_3_line_19 | NAYY 4x150 SE | 15 | 17 | 0.028881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1502-20_0_3_line_20 | NAYY 4x150 SE | 16 | 18 | 0.014621 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1502-20_0_3_line_21 | NAYY 4x150 SE | 16 | 19 | 0.10489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1502-20_0_3_line_22 | NAYY 4x150 SE | 17 | 21 | 0.18808 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1502-20_0_3_line_23 | NAYY 4x150 SE | 18 | 22 | 0.018564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1502-20_0_3_line_24 | NAYY 4x150 SE | 19 | 20 | 0.0078303 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1502-20_0_3_line_25 | NAYY 4x150 SE | 21 | 32 | 0.0043785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1502-20_0_3_line_26 | NAYY 4x150 SE | 22 | 43 | 0.016432 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1502-20_0_3_line_27 | NAYY 4x150 SE | 22 | 44 | 0.030832 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1502-20_0_3_line_28 | NAYY 4x150 SE | 24 | 25 | 0.026407 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1502-20_0_3_line_29 | NAYY 4x150 SE | 25 | 26 | 0.0047812 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1502-20_0_3_line_30 | NAYY 4x150 SE | 26 | 27 | 0.024164 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1502-20_0_3_line_31 | NAYY 4x150 SE | 27 | 28 | 0.037072 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1502-20_0_3_line_32 | NAYY 4x150 SE | 29 | 30 | 0.054038 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1502-20_0_3_line_33 | NAYY 4x150 SE | 29 | 31 | 0.0071656 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1502-20_0_3_line_34 | NAYY 4x150 SE | 30 | 32 | 0.060534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1502-20_0_3_line_35 | NAYY 4x150 SE | 31 | 33 | 0.027789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1502-20_0_3_line_36 | NAYY 4x150 SE | 33 | 34 | 0.24287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1502-20_0_3_line_37 | NAYY 4x150 SE | 34 | 36 | 0.027205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1502-20_0_3_line_38 | NAYY 4x150 SE | 35 | 36 | 0.043676 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1502-20_0_3_line_39 | NAYY 4x150 SE | 37 | 38 | 0.0088998 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1502-20_0_3_line_40 | NAYY 4x150 SE | 37 | 39 | 0.019633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1502-20_0_3_line_41 | NAYY 4x150 SE | 39 | 40 | 0.010515 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1502-20_0_3_line_42 | NAYY 4x150 SE | 40 | 41 | 0.030285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1502-20_0_3_line_43 | NAYY 4x150 SE | 41 | 42 | 0.0070849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1502-20_0_3_line_44 | NAYY 4x150 SE | 42 | 48 | 0.0089936 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1502-20_0_3_line_45 | NAYY 4x150 SE | 43 | 45 | 0.035467 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1502-20_0_3_line_46 | NAYY 4x150 SE | 45 | 46 | 0.0048579 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1502-20_0_3_line_47 | NAYY 4x150 SE | 47 | 48 | 0.011048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1502-20_0_3_trafo_4 | 0.25 MVA 20/0.4 kV | 49 | 4 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2674319.5908 | 1202730.8711 | 2674345.905 | 1202744.0109
1 | 2674301.6246 | 1202711.49 | 2674309.8835 | 1202726.0239 | 2674319.5908 | 1202730.8711
2 | 2674345.905 | 1202744.0109 | 2674346.0096 | 1202744.0631
3 | 2674336.9126 | 1202683.4449 | 2674310.14 | 1202706.6373 | 2674301.6246 | 1202711.49
4 | 2674372.545 | 1202757.3133 | 2674346.0096 | 1202744.0631
5 | 2674336.9126 | 1202683.4449 | 2674345.9289 | 1202678.9788
6 | 2674336.9126 | 1202683.4449 | 2674314.1433 | 1202680.3074
7 | 2674372.545 | 1202757.3133 | 2674375.1644 | 1202758.6213
8 | 2674348.8891 | 1202677.5125 | 2674345.9289 | 1202678.9788
9 | 2674314.1433 | 1202680.3074 | 2674311.061 | 1202679.8826
10 | 2674396.9789 | 1202770.7492 | 2674384.9867 | 1202763.526 | 2674375.1644 | 1202758.6213
11 | 2674348.8891 | 1202677.5125 | 2674359.3325 | 1202665.7352
12 | 2674348.8891 | 1202677.5125 | 2674355.3783 | 1202684.4308 | 2674361.8118 | 1202688.7011
13 | 2674293.6277 | 1202677.4803 | 2674311.061 | 1202679.8826
14 | 2674396.9789 | 1202770.7492 | 2674403.7791 | 1202774.8451
15 | 2674126.8086 | 1202637.0147 | 2674144.9427 | 1202646.5023
16 | 2674190.4226 | 1202664.184 | 2674175.3323 | 1202662.4018 | 2674144.9427 | 1202646.5023
17 | 2674111.0244 | 1202628.7565 | 2674126.8086 | 1202637.0147
18 | 2674190.4226 | 1202664.184 | 2674204.446 | 1202665.8403
19 | 2674085.7642 | 1202614.8977 | 2674087.3944 | 1202616.3936 | 2674111.0244 | 1202628.7565
20 | 2674204.446 | 1202665.8403 | 2674218.9664 | 1202667.5552
21 | 2674204.446 | 1202665.8403 | 2674187.0563 | 1202769.274
22 | 2674085.7642 | 1202614.8977 | 2674136.6053 | 1202433.8186
23 | 2674237.4027 | 1202669.7327 | 2674218.9664 | 1202667.5552
24 | 2674187.0563 | 1202769.274 | 2674181.4047 | 1202774.6936
25 | 2674136.6053 | 1202433.8186 | 2674134.8545 | 1202429.8054
26 | 2674237.4027 | 1202669.7327 | 2674253.6805 | 1202671.9757
27 | 2674240.098 | 1202639.025 | 2674237.4027 | 1202669.7327
28 | 2674420.8605 | 1202718.1465 | 2674444.5891 | 1202729.7334
29 | 2674416.5642 | 1202716.0485 | 2674420.8605 | 1202718.1465
30 | 2674394.8506 | 1202705.4456 | 2674416.5642 | 1202716.0485
31 | 2674361.8118 | 1202688.7011 | 2674365.2963 | 1202691.0139 | 2674394.8506 | 1202705.4456
32 | 2674110.4279 | 1202374.4189 | 2674110.9473 | 1202367.5211 | 2674113.2812 | 1202359.1448 | 2674117.8155 | 1202353.7644 | 2674124.5748 | 1202348.167 | 2674132.5286 | 1202346.2868 | 2674140.2143 | 1202346.3822 | 2674146.9458 | 1202346.926
33 | 2674153.9127 | 1202348.2978 | 2674151.1096 | 1202347.2624 | 2674146.9458 | 1202346.926
34 | 2674110.4279 | 1202374.4189 | 2674126.5232 | 1202410.7075 | 2674134.8545 | 1202429.8054
35 | 2674153.9127 | 1202348.2978 | 2674168.6629 | 1202340.287 | 2674173.9218 | 1202338.4623 | 2674179.3435 | 1202338.0475
36 | 2674179.3435 | 1202338.0475 | 2674406.5986 | 1202252.3573
37 | 2674406.5986 | 1202252.3573 | 2674415.7831 | 1202255.5625 | 2674419.2153 | 1202257.4175 | 2674422.9779 | 1202260.8554 | 2674427.8817 | 1202264.9412 | 2674429.6618 | 1202266.0479
38 | 2674471.7377 | 1202276.1305 | 2674471.2709 | 1202275.9664 | 2674464.9939 | 1202274.5873 | 2674455.5028 | 1202273.3905 | 2674448.0029 | 1202272.4298 | 2674442.6324 | 1202271.5957 | 2674438.0967 | 1202270.3384 | 2674432.7907 | 1202267.9931 | 2674429.6618 | 1202266.0479
39 | 2674445.4546 | 1202663.8467 | 2674454.3385 | 1202664.3778
40 | 2674445.4546 | 1202663.8467 | 2674435.6726 | 1202663.2619 | 2674425.8553 | 1202662.697
41 | 2674415.358 | 1202662.093 | 2674425.8553 | 1202662.697
42 | 2674385.1231 | 1202660.3534 | 2674415.358 | 1202662.093
43 | 2674385.1231 | 1202660.3534 | 2674378.0499 | 1202659.9464
44 | 2674369.396 | 1202661.1761 | 2674372.7798 | 1202659.6432 | 2674378.0499 | 1202659.9464
45 | 2674253.6805 | 1202671.9757 | 2674288.8152 | 1202676.8172
46 | 2674293.6277 | 1202677.4803 | 2674288.8152 | 1202676.8172
47 | 2674359.3325 | 1202665.7352 | 2674369.396 | 1202661.1761

## bus_geodata
| x | y | coords
0 | 2674319.5908 | 1202730.8711
1 | 2674345.905 | 1202744.0109
2 | 2674301.6246 | 1202711.49
3 | 2674346.0096 | 1202744.0631
4 | 2674336.9126 | 1202683.4449
5 | 2674372.545 | 1202757.3133
6 | 2674345.9289 | 1202678.9788
7 | 2674314.1433 | 1202680.3074
8 | 2674375.1644 | 1202758.6213
9 | 2674348.8891 | 1202677.5125
10 | 2674311.061 | 1202679.8826
11 | 2674396.9789 | 1202770.7492
12 | 2674144.9427 | 1202646.5023
13 | 2674126.8086 | 1202637.0147
14 | 2674190.4226 | 1202664.184
15 | 2674111.0244 | 1202628.7565
16 | 2674204.446 | 1202665.8403
17 | 2674085.7642 | 1202614.8977
18 | 2674218.9664 | 1202667.5552
19 | 2674187.0563 | 1202769.274
20 | 2674181.4047 | 1202774.6936
21 | 2674136.6053 | 1202433.8186
22 | 2674237.4027 | 1202669.7327
23 | 2674403.7791 | 1202774.8451
24 | 2674444.5891 | 1202729.7334
25 | 2674420.8605 | 1202718.1465
26 | 2674416.5642 | 1202716.0485
27 | 2674394.8506 | 1202705.4456
28 | 2674361.8118 | 1202688.7011
29 | 2674146.9458 | 1202346.926
30 | 2674110.4279 | 1202374.4189
31 | 2674153.9127 | 1202348.2978
32 | 2674134.8545 | 1202429.8054
33 | 2674179.3435 | 1202338.0475
34 | 2674406.5986 | 1202252.3573
35 | 2674471.7377 | 1202276.1305
36 | 2674429.6618 | 1202266.0479
37 | 2674445.4546 | 1202663.8467
38 | 2674454.3385 | 1202664.3778
39 | 2674425.8553 | 1202662.697
40 | 2674415.358 | 1202662.093
41 | 2674385.1231 | 1202660.3534
42 | 2674378.0499 | 1202659.9464
43 | 2674253.6805 | 1202671.9757
44 | 2674240.098 | 1202639.025
45 | 2674288.8152 | 1202676.8172
46 | 2674293.6277 | 1202677.4803
47 | 2674359.3325 | 1202665.7352
48 | 2674369.396 | 1202661.1761
49 | 2674348.8891 | 1202677.5125

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99553 | -0.031227 | 0.0047657 | 0.0011944
1 | 0.99392 | -0.042521 | 0.0051423 | 0.0012888
2 | 0.99722 | -0.019356 | 0 | 0
3 | 0.99392 | -0.042559 | 0.0052116 | 0.0013061
4 | 1 | 0 | -0.21704 | -0.054362
5 | 0.99274 | -0.050873 | 0.0052799 | 0.0013233
6 | 0.9987 | -0.0090785 | 0.0060353 | 0.0015126
7 | 0.9973 | -0.01883 | 0.0053997 | 0.0013533
8 | 0.99264 | -0.051538 | 0.0052352 | 0.0013121
9 | 0.9983 | -0.011865 | 0 | 0
10 | 0.99695 | -0.021219 | 0.0059137 | 0.0014821
11 | 0.99203 | -0.05589 | 0.012702 | 0.0031833
12 | 0.98808 | -0.083731 | 0.0015323 | 0.00038403
13 | 0.98775 | -0.086008 | 0.00088229 | 0.00022112
14 | 0.98896 | -0.077454 | 0.0012144 | 0.00030436
15 | 0.9875 | -0.08783 | 0.0014744 | 0.00036952
16 | 0.98924 | -0.075489 | 0.0055698 | 0.0013959
17 | 0.98715 | -0.09035 | 0.0014585 | 0.00036553
18 | 0.98969 | -0.072298 | 0.0035906 | 0.00089988
19 | 0.9889 | -0.077848 | 0.0014712 | 0.00036871
20 | 0.9889 | -0.077906 | 0.00072688 | 0.00018217
21 | 0.98524 | -0.10396 | 0.00055744 | 0.00013971
22 | 0.99035 | -0.06757 | 0 | 0
23 | 0.99197 | -0.056252 | 0.0044889 | 0.001125
24 | 0.99495 | -0.035367 | 0.0038397 | 0.00096233
25 | 0.9951 | -0.034345 | 0.0073603 | 0.0018447
26 | 0.99518 | -0.033805 | 0.0080887 | 0.0020272
27 | 0.99584 | -0.02911 | 0.0052687 | 0.0013205
28 | 0.99715 | -0.019958 | 0.022345 | 0.0056001
29 | 0.98417 | -0.11156 | 0.0017412 | 0.00043639
30 | 0.98466 | -0.10811 | 0 | 0
31 | 0.98413 | -0.11189 | 0 | 0
32 | 0.9852 | -0.10425 | 0.00028213 | 7.0709e-05
33 | 0.98395 | -0.11316 | 0.00083178 | 0.00020846
34 | 0.98269 | -0.1222 | 0 | 0
35 | 0.98253 | -0.12332 | 0.00023475 | 5.8833e-05
36 | 0.98255 | -0.12321 | 0.0033516 | 0.00083999
37 | 0.99485 | -0.036061 | 0.0043425 | 0.0010883
38 | 0.99482 | -0.036294 | 0.0025909 | 0.00064935
39 | 0.99505 | -0.034688 | 0.0049227 | 0.0012337
40 | 0.99523 | -0.033432 | 0.012671 | 0.0031757
41 | 0.99629 | -0.025953 | 0.0032482 | 0.00081408
42 | 0.99657 | -0.023975 | 0.0022073 | 0.00055321
43 | 0.99163 | -0.05856 | 0.0061617 | 0.0015443
44 | 0.98907 | -0.076664 | 0.028944 | 0.0072542
45 | 0.9947 | -0.036986 | 0.0067999 | 0.0017042
46 | 0.99517 | -0.033708 | 0.0036277 | 0.00090918
47 | 0.99746 | -0.017755 | 0.0056795 | 0.0014234
48 | 0.99696 | -0.021265 | 0.001666 | 0.00041754
49 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.038164 | 0.0095776 | -0.038104 | -0.009555 | 5.9731e-05 | 2.2592e-05 | 0.057048 | 0.057048 | 0.057048 | 0.99553 | -0.031227 | 0.99392 | -0.042521 | 21.129
1 | -0.04293 | -0.010772 | 0.043001 | 0.010799 | 7.0836e-05 | 2.6885e-05 | 0.064171 | 0.064171 | 0.064171 | 0.99553 | -0.031227 | 0.99722 | -0.019356 | 23.7672
2 | 0.032962 | 0.0082662 | -0.032962 | -0.0082661 | 1.7771e-07 | 6.6833e-08 | 0.04935 | 0.04935 | 0.04935 | 0.99392 | -0.042521 | 0.99392 | -0.042559 | 18.2776
3 | -0.043001 | -0.010799 | 0.043117 | 0.010843 | 0.00011601 | 4.4028e-05 | 0.064171 | 0.064171 | 0.064171 | 0.99722 | -0.019356 | 1 | 0 | 23.7671
4 | 0.02775 | 0.00696 | -0.027718 | -0.0069481 | 3.1947e-05 | 1.1904e-05 | 0.041547 | 0.041547 | 0.041547 | 0.99392 | -0.042559 | 0.99274 | -0.050873 | 15.3879
5 | 0.090604 | 0.02275 | -0.09049 | -0.022706 | 0.00011415 | 4.3771e-05 | 0.13483 | 0.13483 | 0.13483 | 1 | 0 | 0.9987 | -0.0090785 | 49.9389
6 | 0.082522 | 0.02077 | -0.082306 | -0.020687 | 0.00021637 | 8.2918e-05 | 0.12282 | 0.12283 | 0.12283 | 1 | 0 | 0.9973 | -0.01883 | 45.4907
7 | 0.022438 | 0.0056248 | -0.022436 | -0.0056241 | 2.0666e-06 | 7.5701e-07 | 0.033633 | 0.033633 | 0.033633 | 0.99274 | -0.050873 | 0.99264 | -0.051538 | 12.4568
8 | 0.084454 | 0.021193 | -0.084422 | -0.021181 | 3.2644e-05 | 1.2512e-05 | 0.12584 | 0.12584 | 0.12584 | 0.9987 | -0.0090785 | 0.9983 | -0.011865 | 46.6084
9 | 0.076906 | 0.019333 | -0.07688 | -0.019324 | 2.5573e-05 | 9.7953e-06 | 0.11477 | 0.11477 | 0.11477 | 0.9973 | -0.01883 | 0.99695 | -0.021219 | 42.5068
10 | 0.017201 | 0.004312 | -0.017191 | -0.0043083 | 1.0363e-05 | 3.6632e-06 | 0.025785 | 0.025786 | 0.025786 | 0.99264 | -0.051538 | 0.99203 | -0.05589 | 9.5502
11 | 0.037422 | 0.00939 | -0.037391 | -0.0093784 | 3.0565e-05 | 1.155e-05 | 0.055783 | 0.055783 | 0.055783 | 0.9983 | -0.011865 | 0.99746 | -0.017755 | 20.6605
12 | 0.047 | 0.011791 | -0.046947 | -0.011771 | 5.2702e-05 | 2.0045e-05 | 0.070059 | 0.07006 | 0.07006 | 0.9983 | -0.011865 | 0.99715 | -0.019958 | 25.948
13 | 0.070967 | 0.017842 | -0.070843 | -0.017794 | 0.00012325 | 4.7175e-05 | 0.10594 | 0.10594 | 0.10594 | 0.99695 | -0.021219 | 0.99517 | -0.033708 | 39.2377
14 | 0.0044892 | 0.001125 | -0.0044889 | -0.001125 | 2.2461e-07 | -1.6101e-08 | 0.0067336 | 0.0067336 | 0.0067336 | 0.99203 | -0.05589 | 0.99197 | -0.056252 | 2.4939
15 | 0.010849 | 0.0027143 | -0.010845 | -0.0027133 | 3.4081e-06 | 1.0488e-06 | 0.016336 | 0.016336 | 0.016336 | 0.98808 | -0.083731 | 0.98775 | -0.086008 | 6.0504
16 | -0.012381 | -0.0030983 | 0.012392 | 0.0031018 | 1.0734e-05 | 3.4941e-06 | 0.018644 | 0.018643 | 0.018644 | 0.98808 | -0.083731 | 0.98896 | -0.077454 | 6.905
17 | 0.0099628 | 0.0024921 | -0.0099603 | -0.0024914 | 2.5034e-06 | 7.3489e-07 | 0.015007 | 0.015007 | 0.015007 | 0.98775 | -0.086008 | 0.9875 | -0.08783 | 5.5581
18 | -0.013606 | -0.0034062 | 0.01361 | 0.0034074 | 3.6924e-06 | 1.2389e-06 | 0.020471 | 0.02047 | 0.020471 | 0.98896 | -0.077454 | 0.98924 | -0.075489 | 7.5817
19 | 0.0084859 | 0.0021219 | -0.008483 | -0.0021211 | 2.9459e-06 | 7.637e-07 | 0.012785 | 0.012785 | 0.012785 | 0.9875 | -0.08783 | 0.98715 | -0.09035 | 4.7353
20 | -0.021378 | -0.0053531 | 0.021388 | 0.0053565 | 9.4338e-06 | 3.4406e-06 | 0.032156 | 0.032156 | 0.032156 | 0.98924 | -0.075489 | 0.98969 | -0.072298 | 11.9095
21 | 0.0021988 | 0.00054971 | -0.002198 | -0.00055078 | 7.1582e-07 | -1.0708e-06 | 0.0033069 | 0.0033074 | 0.0033074 | 0.98924 | -0.075489 | 0.9889 | -0.077848 | 1.225
22 | 0.0070245 | 0.0017556 | -0.0070113 | -0.0017529 | 1.3155e-05 | 2.6599e-06 | 0.010587 | 0.010588 | 0.010588 | 0.98715 | -0.09035 | 0.98524 | -0.10396 | 3.9214
23 | -0.024978 | -0.0062564 | 0.024995 | 0.0062624 | 1.6337e-05 | 6.0448e-06 | 0.037554 | 0.037554 | 0.037554 | 0.98969 | -0.072298 | 0.99035 | -0.06757 | 13.9089
24 | 0.00072689 | 0.00018208 | -0.00072688 | -0.00018217 | 5.8451e-09 | -9.8212e-08 | 0.0010937 | 0.0010938 | 0.0010938 | 0.9889 | -0.077848 | 0.9889 | -0.077906 | 0.4051
25 | 0.0064539 | 0.0016132 | -0.0064536 | -0.0016132 | 2.5951e-07 | 4.4053e-08 | 0.0097458 | 0.0097459 | 0.0097459 | 0.98524 | -0.10396 | 0.9852 | -0.10425 | 3.6096
26 | -0.053975 | -0.01353 | 0.054043 | 0.013556 | 6.7437e-05 | 2.5726e-05 | 0.0811 | 0.0811 | 0.0811 | 0.99035 | -0.06757 | 0.99163 | -0.05856 | 30.0369
27 | 0.028981 | 0.0072678 | -0.028944 | -0.0072542 | 3.6482e-05 | 1.3635e-05 | 0.043546 | 0.043546 | 0.043546 | 0.99035 | -0.06757 | 0.98907 | -0.076664 | 16.1281
28 | -0.0038397 | -0.00096233 | 0.0038403 | 0.00096219 | 5.4337e-07 | -1.3401e-07 | 0.0057426 | 0.0057424 | 0.0057426 | 0.99495 | -0.035367 | 0.9951 | -0.034345 | 2.1269
29 | -0.011201 | -0.0028069 | 0.011201 | 0.0028071 | 8.3691e-07 | 2.5977e-07 | 0.016749 | 0.016749 | 0.016749 | 0.9951 | -0.034345 | 0.99518 | -0.033805 | 6.2032
30 | -0.01929 | -0.0048343 | 0.019303 | 0.0048389 | 1.2544e-05 | 4.5104e-06 | 0.028843 | 0.028843 | 0.028843 | 0.99518 | -0.033805 | 0.99584 | -0.02911 | 10.6826
31 | -0.024571 | -0.0061593 | 0.024603 | 0.0061708 | 3.1184e-05 | 1.1511e-05 | 0.036716 | 0.036715 | 0.036716 | 0.99584 | -0.02911 | 0.99715 | -0.019958 | 13.5984
32 | -0.0061653 | -0.0015415 | 0.0061682 | 0.001542 | 2.929e-06 | 4.3954e-07 | 0.0093203 | 0.00932 | 0.0093203 | 0.98417 | -0.11156 | 0.98466 | -0.10811 | 3.4519
33 | 0.0044241 | 0.0011051 | -0.0044239 | -0.0011052 | 1.9998e-07 | -1.4136e-08 | 0.0066876 | 0.0066877 | 0.0066877 | 0.98417 | -0.11156 | 0.98413 | -0.11189 | 2.4769
34 | -0.0061682 | -0.001542 | 0.0061715 | 0.0015425 | 3.281e-06 | 4.9151e-07 | 0.00932 | 0.0093197 | 0.00932 | 0.98466 | -0.10811 | 0.9852 | -0.10425 | 3.4519
35 | 0.0044239 | 0.0011052 | -0.0044231 | -0.0011052 | 7.7557e-07 | -5.4735e-08 | 0.0066877 | 0.0066878 | 0.0066878 | 0.98413 | -0.11189 | 0.98395 | -0.11316 | 2.477
36 | 0.0035913 | 0.00089676 | -0.0035868 | -0.00089812 | 4.4693e-06 | -1.362e-06 | 0.0054299 | 0.005431 | 0.005431 | 0.98395 | -0.11316 | 0.98269 | -0.1222 | 2.0115
37 | 0.0035868 | 0.00089812 | -0.0035863 | -0.00089827 | 5.0073e-07 | -1.5202e-07 | 0.005431 | 0.0054311 | 0.0054311 | 0.98269 | -0.1222 | 0.98255 | -0.12321 | 2.0115
38 | -0.00023475 | -5.8833e-05 | 0.00023475 | 5.8281e-05 | 3.4428e-09 | -5.5184e-07 | 0.00035552 | 0.00035532 | 0.00035552 | 0.98253 | -0.12332 | 0.98255 | -0.12321 | 0.13167
39 | 0.002591 | 0.00064926 | -0.0025909 | -0.00064935 | 8.3406e-08 | -8.3478e-08 | 0.0038754 | 0.0038754 | 0.0038754 | 0.99485 | -0.036061 | 0.99482 | -0.036294 | 1.4353
40 | -0.0069335 | -0.0017376 | 0.0069348 | 0.0017378 | 1.3175e-06 | 2.5177e-07 | 0.01037 | 0.01037 | 0.01037 | 0.99485 | -0.036061 | 0.99505 | -0.034688 | 3.8409
41 | -0.011857 | -0.0029716 | 0.01186 | 0.0029722 | 2.0629e-06 | 6.5683e-07 | 0.017732 | 0.017732 | 0.017732 | 0.99505 | -0.034688 | 0.99523 | -0.033432 | 6.5673
42 | -0.024531 | -0.0061479 | 0.024556 | 0.0061573 | 2.5421e-05 | 9.3835e-06 | 0.036677 | 0.036677 | 0.036677 | 0.99523 | -0.033432 | 0.99629 | -0.025953 | 13.5841
43 | -0.027804 | -0.0069714 | 0.027812 | 0.0069742 | 7.6244e-06 | 2.8402e-06 | 0.041528 | 0.041528 | 0.041528 | 0.99629 | -0.025953 | 0.99657 | -0.023975 | 15.3809
44 | -0.030019 | -0.0075275 | 0.030031 | 0.0075317 | 1.1276e-05 | 4.2196e-06 | 0.044824 | 0.044824 | 0.044824 | 0.99657 | -0.023975 | 0.99696 | -0.021265 | 16.6015
45 | -0.060205 | -0.0151 | 0.060385 | 0.015169 | 0.00018064 | 6.9019e-05 | 0.090346 | 0.090345 | 0.090346 | 0.99163 | -0.05856 | 0.9947 | -0.036986 | 33.4613
46 | -0.067185 | -0.016873 | 0.067216 | 0.016885 | 3.0628e-05 | 1.1717e-05 | 0.10052 | 0.10052 | 0.10052 | 0.9947 | -0.036986 | 0.99517 | -0.033708 | 37.2287
47 | 0.031712 | 0.007955 | -0.031697 | -0.0079492 | 1.5431e-05 | 5.7908e-06 | 0.047311 | 0.047311 | 0.047311 | 0.99746 | -0.017755 | 0.99696 | -0.021265 | 17.5225

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.21704 | 0.054362

## res_load
| p_mw | q_mvar
0 | 0.0047657 | 0.0011944
1 | 0.0051423 | 0.0012888
2 | 0.0052116 | 0.0013061
3 | 0.0052799 | 0.0013233
4 | 0.0060353 | 0.0015126
5 | 0.0053997 | 0.0013533
6 | 0.0052352 | 0.0013121
7 | 0.0059137 | 0.0014821
8 | 0.012702 | 0.0031833
9 | 0.0015323 | 0.00038403
10 | 0.00088229 | 0.00022112
11 | 0.0012144 | 0.00030436
12 | 0.0014744 | 0.00036952
13 | 0.0055698 | 0.0013959
14 | 0.0014585 | 0.00036553
15 | 0.0035906 | 0.00089988
16 | 0.0014712 | 0.00036871
17 | 0.00072688 | 0.00018217
18 | 0.00055744 | 0.00013971
19 | 0.0044889 | 0.001125
20 | 0.0038397 | 0.00096233
21 | 0.0073603 | 0.0018447
22 | 0.0080887 | 0.0020272
23 | 0.0052687 | 0.0013205
24 | 0.022345 | 0.0056001
25 | 0.0017412 | 0.00043639
26 | 0.00028213 | 7.0709e-05
27 | 0.00083178 | 0.00020846
28 | 0.00023475 | 5.8833e-05
29 | 0.0033516 | 0.00083999
30 | 0.0043425 | 0.0010883
31 | 0.0025909 | 0.00064935
32 | 0.0049227 | 0.0012337
33 | 0.012671 | 0.0031757
34 | 0.0032482 | 0.00081408
35 | 0.0022073 | 0.00055321
36 | 0.0061617 | 0.0015443
37 | 0.028944 | 0.0072542
38 | 0.0067999 | 0.0017042
39 | 0.0036277 | 0.00090918
40 | 0.0056795 | 0.0014234
41 | 0.001666 | 0.00041754

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1