## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1502-22_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1502-22_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1502-22_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1502-22_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1502-22_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1502-22_0_2_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1502-22_0_2_node_16 | 0.4 | n |  | TRUE
7 | bus_LV_1502-22_0_2_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_1502-22_0_2_node_15 | 0.4 | n |  | TRUE
9 | bus_LV_1502-22_0_2_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_1502-22_0_2_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1502-22_0_2_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_1502-22_0_2_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_1502-22_0_2_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_1502-22_0_2_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_1502-22_0_2_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_1502-22_0_2_node_24 | 0.4 | n |  | TRUE
17 | bus_LV_1502-22_0_2_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_1502-22_0_2_node_22 | 0.4 | n |  | TRUE
19 | bus_LV_1502-22_0_2_node_25 | 0.4 | n |  | TRUE
20 | bus_LV_1502-22_0_2_node_21 | 0.4 | n |  | TRUE
21 | bus_LV_1502-22_0_2_node_23 | 0.4 | n |  | TRUE
22 | bus_LV_1502-22_0_2_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_1502-22_0_2_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_1502-22_0_2_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_1502-22_0_2_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_1502-22_0_2_node_26 | 0.4 | n |  | TRUE
27 | bus_LV_1502-22_0_2_node_27 | 0.4 | n |  | TRUE
28 | bus_LV_1502-22_0_2_node_28 | 0.4 | n |  | TRUE
29 | bus_MV_142_1_node_101 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1502-22_0_2_load_0 | 0 | 0.0098407 | 0.0024663 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1502-22_0_2_load_1 | 1 | 0.018556 | 0.0046505 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1502-22_0_2_load_3 | 3 | 0.027025 | 0.0067731 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1502-22_0_2_load_16 | 6 | 0.0075989 | 0.0019045 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1502-22_0_2_load_6 | 7 | 0.0094932 | 0.0023792 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1502-22_0_2_load_15 | 8 | 0.0060599 | 0.0015188 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1502-22_0_2_load_7 | 9 | 0.0083156 | 0.0020841 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1502-22_0_2_load_8 | 10 | 0.012691 | 0.0031806 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1502-22_0_2_load_10 | 12 | 0.004844 | 0.001214 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1502-22_0_2_load_11 | 13 | 0.0068615 | 0.0017197 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1502-22_0_2_load_12 | 14 | 0.0052676 | 0.0013202 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1502-22_0_2_load_13 | 15 | 0.013458 | 0.0033729 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1502-22_0_2_load_24 | 16 | 0.0082094 | 0.0020575 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1502-22_0_2_load_14 | 17 | 0.0032299 | 0.0008095 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1502-22_0_2_load_22 | 18 | 0.0032546 | 0.00081567 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1502-22_0_2_load_25 | 19 | 0.0039145 | 0.00098105 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1502-22_0_2_load_23 | 21 | 0.0014925 | 0.00037405 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1502-22_0_2_load_17 | 22 | 0.0071714 | 0.0017973 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1502-22_0_2_load_19 | 24 | 0.013415 | 0.003362 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1502-22_0_2_load_20 | 25 | 0.0021158 | 0.00053028 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1502-22_0_2_load_28 | 28 | 0.0095503 | 0.0023935 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1502-22_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.036262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1502-22_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.021644 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1502-22_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.040836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1502-22_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.08944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1502-22_0_2_line_4 | NAYY 4x150 SE | 2 | 5 | 0.053387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1502-22_0_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.018538 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1502-22_0_2_line_6 | NAYY 4x150 SE | 5 | 7 | 0.051225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1502-22_0_2_line_7 | NAYY 4x150 SE | 6 | 8 | 0.016158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1502-22_0_2_line_8 | NAYY 4x150 SE | 8 | 17 | 0.0040977 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1502-22_0_2_line_9 | NAYY 4x150 SE | 9 | 10 | 0.027318 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
10 | LV_1502-22_0_2_line_10 | NAYY 4x150 SE | 9 | 11 | 0.0091491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
11 | LV_1502-22_0_2_line_11 | NAYY 4x150 SE | 10 | 12 | 0.010236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
12 | LV_1502-22_0_2_line_12 | NAYY 4x150 SE | 10 | 13 | 0.019536 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1502-22_0_2_line_13 | NAYY 4x150 SE | 11 | 14 | 0.0080873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1502-22_0_2_line_14 | NAYY 4x150 SE | 11 | 15 | 0.030357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1502-22_0_2_line_15 | NAYY 4x150 SE | 13 | 16 | 0.014675 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1502-22_0_2_line_16 | NAYY 4x150 SE | 14 | 17 | 0.019738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1502-22_0_2_line_17 | NAYY 4x150 SE | 15 | 18 | 0.0081838 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1502-22_0_2_line_18 | NAYY 4x150 SE | 16 | 19 | 0.012828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1502-22_0_2_line_19 | NAYY 4x150 SE | 18 | 20 | 0.0088693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1502-22_0_2_line_20 | NAYY 4x150 SE | 19 | 26 | 0.021361 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1502-22_0_2_line_21 | NAYY 4x150 SE | 20 | 21 | 0.010614 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1502-22_0_2_line_22 | NAYY 4x150 SE | 21 | 25 | 0.0015863 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1502-22_0_2_line_23 | NAYY 4x150 SE | 22 | 23 | 0.023127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1502-22_0_2_line_24 | NAYY 4x150 SE | 22 | 24 | 0.014997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1502-22_0_2_line_25 | NAYY 4x150 SE | 23 | 25 | 0.020397 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1502-22_0_2_line_26 | NAYY 4x150 SE | 26 | 27 | 0.006505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1502-22_0_2_line_27 | NAYY 4x150 SE | 27 | 28 | 0.039662 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1502-22_0_2_trafo_10 | 0.25 MVA 20/0.4 kV | 29 | 12 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2675087.7902 | 1202981.5034 | 2675120.8398 | 1202992.6847 | 2675122.1877 | 1202992.9438
1 | 2675067.2878 | 1202974.5671 | 2675087.7902 | 1202981.5034
2 | 2675122.1877 | 1202992.9438 | 2675145.7783 | 1202997.479 | 2675162.2157 | 1203001.0148
3 | 2675067.2878 | 1202974.5671 | 2675048.2755 | 1202997.1756 | 2675052.9242 | 1203016.6238 | 2675048.5865 | 1203032.368 | 2675051.0382 | 1203050.4322 | 2675051.3133 | 1203055.7945
4 | 2675067.2878 | 1202974.5671 | 2675077.9822 | 1202960.4594 | 2675075.468 | 1202938.2918 | 2675088.7172 | 1202936.4683
5 | 2675069.5386 | 1203059.4591 | 2675051.3133 | 1203055.7945
6 | 2675088.7172 | 1202936.4683 | 2675117.9073 | 1202943.295 | 2675138.4274 | 1202948.8053
7 | 2675069.5386 | 1203059.4591 | 2675085.5063 | 1203061.9315
8 | 2675085.5063 | 1203061.9315 | 2675089.5558 | 1203062.5586
9 | 2675153.3723 | 1203070.0973 | 2675126.1655 | 1203067.6395
10 | 2675117.0535 | 1203066.8163 | 2675126.1655 | 1203067.6395
11 | 2675153.3723 | 1203070.0973 | 2675153.5837 | 1203059.8631
12 | 2675153.3723 | 1203070.0973 | 2675172.9065 | 1203070.3718
13 | 2675117.0535 | 1203066.8163 | 2675109.0615 | 1203065.5788
14 | 2675117.0535 | 1203066.8163 | 2675112.5612 | 1203096.8393
15 | 2675172.9065 | 1203070.3718 | 2675187.5796 | 1203070.5781
16 | 2675109.0615 | 1203065.5788 | 2675089.5558 | 1203062.5586
17 | 2675111.9886 | 1203105.0007 | 2675112.459 | 1203097.522 | 2675112.5612 | 1203096.8393
18 | 2675200.4068 | 1203070.7583 | 2675187.5796 | 1203070.5781
19 | 2675111.4317 | 1203113.8526 | 2675111.9886 | 1203105.0007
20 | 2675221.7655 | 1203071.0585 | 2675200.4068 | 1203070.7583
21 | 2675111.4317 | 1203113.8526 | 2675120.3026 | 1203119.6806
22 | 2675120.3026 | 1203119.6806 | 2675121.6283 | 1203120.5516
23 | 2675135.1029 | 1203135.8638 | 2675141.4379 | 1203131.3407 | 2675153.6943 | 1203130.372 | 2675156.7124 | 1203129.9403
24 | 2675169.7309 | 1203125.3151 | 2675166.1057 | 1203125.5474 | 2675164.1233 | 1203128.8801 | 2675156.7124 | 1203129.9403
25 | 2675135.1029 | 1203135.8638 | 2675121.6283 | 1203120.5516
26 | 2675221.7655 | 1203071.0585 | 2675222.8871 | 1203077.4655
27 | 2675222.8871 | 1203077.4655 | 2675219.3868 | 1203084.0922 | 2675220.0414 | 1203092.539 | 2675223.1965 | 1203103.0408 | 2675224.4908 | 1203110.2393 | 2675224.3009 | 1203115.6514

## bus_geodata
| x | y | coords
0 | 2675087.7902 | 1202981.5034
1 | 2675122.1877 | 1202992.9438
2 | 2675067.2878 | 1202974.5671
3 | 2675162.2157 | 1203001.0148
4 | 2675051.3133 | 1203055.7945
5 | 2675088.7172 | 1202936.4683
6 | 2675069.5386 | 1203059.4591
7 | 2675138.4274 | 1202948.8053
8 | 2675085.5063 | 1203061.9315
9 | 2675126.1655 | 1203067.6395
10 | 2675153.3723 | 1203070.0973
11 | 2675117.0535 | 1203066.8163
12 | 2675153.5837 | 1203059.8631
13 | 2675172.9065 | 1203070.3718
14 | 2675109.0615 | 1203065.5788
15 | 2675112.5612 | 1203096.8393
16 | 2675187.5796 | 1203070.5781
17 | 2675089.5558 | 1203062.5586
18 | 2675111.9886 | 1203105.0007
19 | 2675200.4068 | 1203070.7583
20 | 2675111.4317 | 1203113.8526
21 | 2675120.3026 | 1203119.6806
22 | 2675156.7124 | 1203129.9403
23 | 2675135.1029 | 1203135.8638
24 | 2675169.7309 | 1203125.3151
25 | 2675121.6283 | 1203120.5516
26 | 2675221.7655 | 1203071.0585
27 | 2675222.8871 | 1203077.4655
28 | 2675224.3009 | 1203115.6514
29 | 2675153.3723 | 1203070.0973

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97759 | -0.15703 | 0.0098407 | 0.0024663
1 | 0.97517 | -0.17434 | 0.018556 | 0.0046505
2 | 0.97934 | -0.14453 | 0 | 0
3 | 0.97355 | -0.18594 | 0.027025 | 0.0067731
4 | 0.98783 | -0.08461 | 0 | 0
5 | 0.9786 | -0.14981 | 0 | 0
6 | 0.98959 | -0.072319 | 0.0075989 | 0.0019045
7 | 0.97789 | -0.15488 | 0.0094932 | 0.0023792
8 | 0.9913 | -0.060393 | 0.0060599 | 0.0015188
9 | 0.99599 | -0.027769 | 0.0083156 | 0.0020841
10 | 0.99869 | -0.0090831 | 0.012691 | 0.0031806
11 | 0.99514 | -0.033666 | 0 | 0
12 | 1 | 0 | -0.18055 | -0.04534
13 | 0.99789 | -0.014668 | 0.0068615 | 0.0017197
14 | 0.99412 | -0.040772 | 0.0052676 | 0.0013202
15 | 0.99336 | -0.046206 | 0.013458 | 0.0033729
16 | 0.99744 | -0.017858 | 0.0082094 | 0.0020575
17 | 0.99176 | -0.057123 | 0.0032299 | 0.0008095
18 | 0.99304 | -0.04848 | 0.0032546 | 0.00081567
19 | 0.99719 | -0.019593 | 0.0039145 | 0.00098105
20 | 0.99273 | -0.050653 | 0 | 0
21 | 0.99236 | -0.053255 | 0.0014925 | 0.00037405
22 | 0.99102 | -0.062715 | 0.0071714 | 0.0017973
23 | 0.9917 | -0.05788 | 0 | 0
24 | 0.99073 | -0.06476 | 0.013415 | 0.003362
25 | 0.99231 | -0.05362 | 0.0021158 | 0.00053028
26 | 0.9969 | -0.021642 | 0 | 0
27 | 0.99681 | -0.022266 | 0 | 0
28 | 0.99627 | -0.026074 | 0.0095503 | 0.0023935
29 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.045734 | 0.011482 | -0.045624 | -0.01144 | 0.00010968 | 4.1729e-05 | 0.06962 | 0.06962 | 0.06962 | 0.97759 | -0.15703 | 0.97517 | -0.17434 | 25.7852
1 | -0.055575 | -0.013948 | 0.055671 | 0.013985 | 9.666e-05 | 3.6905e-05 | 0.084599 | 0.084599 | 0.084599 | 0.97759 | -0.15703 | 0.97934 | -0.14453 | 31.3329
2 | 0.027068 | 0.0067893 | -0.027025 | -0.0067731 | 4.3476e-05 | 1.6213e-05 | 0.041306 | 0.041306 | 0.041306 | 0.97517 | -0.17434 | 0.97355 | -0.18594 | 15.2986
3 | -0.065178 | -0.016368 | 0.065725 | 0.016577 | 0.00054748 | 0.00020943 | 0.099044 | 0.099043 | 0.099044 | 0.97934 | -0.14453 | 0.98783 | -0.08461 | 36.6828
4 | 0.0095068 | 0.0023831 | -0.0094998 | -0.0023811 | 6.9511e-06 | 2.0022e-06 | 0.014445 | 0.014445 | 0.014445 | 0.97934 | -0.14453 | 0.9786 | -0.14981 | 5.35
5 | -0.065725 | -0.016577 | 0.065839 | 0.016621 | 0.00011347 | 4.3406e-05 | 0.099043 | 0.099043 | 0.099043 | 0.98783 | -0.08461 | 0.98959 | -0.072319 | 36.6827
6 | 0.0094998 | 0.0023811 | -0.0094932 | -0.0023792 | 6.6698e-06 | 1.9222e-06 | 0.014445 | 0.014445 | 0.014445 | 0.9786 | -0.14981 | 0.97789 | -0.15488 | 5.3501
7 | -0.073438 | -0.018525 | 0.073561 | 0.018572 | 0.00012304 | 4.7116e-05 | 0.11047 | 0.11047 | 0.11047 | 0.98959 | -0.072319 | 0.9913 | -0.060393 | 40.9146
8 | -0.079621 | -0.020091 | 0.079657 | 0.020105 | 3.6554e-05 | 1.4007e-05 | 0.11957 | 0.11957 | 0.11957 | 0.9913 | -0.060393 | 0.99176 | -0.057123 | 44.2836
9 | -0.13789 | -0.034766 | 0.13825 | 0.034905 | 0.00036197 | 0.00013851 | 0.20608 | 0.20608 | 0.20608 | 0.99599 | -0.027769 | 0.99869 | -0.0090831 | 38.1633
10 | 0.12957 | 0.032682 | -0.12947 | -0.032641 | 0.00010705 | 4.0937e-05 | 0.19366 | 0.19366 | 0.19366 | 0.99599 | -0.027769 | 0.99514 | -0.033666 | 35.8627
11 | -0.17952 | -0.045252 | 0.17975 | 0.04534 | 0.00022866 | 8.7678e-05 | 0.26757 | 0.26757 | 0.26757 | 0.99869 | -0.0090831 | 1 | 0 | 49.5508
12 | 0.028579 | 0.0071669 | -0.028557 | -0.0071587 | 2.2106e-05 | 8.2469e-06 | 0.042584 | 0.042584 | 0.042584 | 0.99869 | -0.0090831 | 0.99789 | -0.014668 | 15.7717
13 | 0.088434 | 0.022342 | -0.088346 | -0.022308 | 8.8325e-05 | 3.3866e-05 | 0.1323 | 0.1323 | 0.1323 | 0.99514 | -0.033666 | 0.99412 | -0.040772 | 48.9987
14 | 0.041034 | 0.0103 | -0.040962 | -0.010272 | 7.1327e-05 | 2.704e-05 | 0.061362 | 0.061363 | 0.061363 | 0.99514 | -0.033666 | 0.99336 | -0.046206 | 22.7269
15 | 0.021696 | 0.005439 | -0.021686 | -0.0054355 | 9.5842e-06 | 3.4946e-06 | 0.032352 | 0.032352 | 0.032352 | 0.99789 | -0.014668 | 0.99744 | -0.017858 | 11.9823
16 | 0.083078 | 0.020988 | -0.082887 | -0.020915 | 0.00019064 | 7.3068e-05 | 0.12441 | 0.12441 | 0.12441 | 0.99412 | -0.040772 | 0.99176 | -0.057123 | 46.0785
17 | 0.027505 | 0.0068996 | -0.027496 | -0.0068964 | 8.6696e-06 | 3.2285e-06 | 0.041203 | 0.041203 | 0.041203 | 0.99336 | -0.046206 | 0.99304 | -0.04848 | 15.2604
18 | 0.013477 | 0.0033781 | -0.013473 | -0.003377 | 3.2357e-06 | 1.0771e-06 | 0.020105 | 0.020105 | 0.020105 | 0.99744 | -0.017858 | 0.99719 | -0.019593 | 7.4463
19 | 0.024241 | 0.0060807 | -0.024234 | -0.006078 | 7.3033e-06 | 2.6943e-06 | 0.036326 | 0.036326 | 0.036326 | 0.99304 | -0.04848 | 0.99273 | -0.050653 | 13.4542
20 | 0.0095589 | 0.0023959 | -0.0095562 | -0.0023952 | 2.712e-06 | 7.6448e-07 | 0.014264 | 0.014264 | 0.014264 | 0.99719 | -0.019593 | 0.9969 | -0.021642 | 5.283
21 | 0.024234 | 0.006078 | -0.024225 | -0.0060748 | 8.74e-06 | 3.2243e-06 | 0.036326 | 0.036326 | 0.036326 | 0.99273 | -0.050653 | 0.99236 | -0.053255 | 13.4542
22 | 0.022733 | 0.0057007 | -0.022732 | -0.0057003 | 1.1502e-06 | 4.2191e-07 | 0.034089 | 0.034089 | 0.034089 | 0.99236 | -0.053255 | 0.99231 | -0.05362 | 12.6254
23 | -0.02059 | -0.0051606 | 0.020604 | 0.0051656 | 1.3794e-05 | 5.007e-06 | 0.030916 | 0.030916 | 0.030916 | 0.99102 | -0.062715 | 0.9917 | -0.05788 | 11.4503
24 | 0.013418 | 0.0033633 | -0.013415 | -0.003362 | 3.7988e-06 | 1.2679e-06 | 0.020148 | 0.020148 | 0.020148 | 0.99102 | -0.062715 | 0.99073 | -0.06476 | 7.4623
25 | -0.020604 | -0.0051656 | 0.020616 | 0.0051701 | 1.2165e-05 | 4.4155e-06 | 0.030916 | 0.030916 | 0.030916 | 0.9917 | -0.05788 | 0.99231 | -0.05362 | 11.4503
26 | 0.0095562 | 0.0023952 | -0.0095553 | -0.0023949 | 8.2588e-07 | 2.3284e-07 | 0.014264 | 0.014264 | 0.014264 | 0.9969 | -0.021642 | 0.99681 | -0.022266 | 5.283
27 | 0.0095553 | 0.0023949 | -0.0095503 | -0.0023935 | 5.0356e-06 | 1.42e-06 | 0.014264 | 0.014264 | 0.014264 | 0.99681 | -0.022266 | 0.99627 | -0.026074 | 5.2831

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.18539 | 0.046554

## res_load
| p_mw | q_mvar
0 | 0.0098407 | 0.0024663
1 | 0.018556 | 0.0046505
2 | 0.027025 | 0.0067731
3 | 0.0075989 | 0.0019045
4 | 0.0094932 | 0.0023792
5 | 0.0060599 | 0.0015188
6 | 0.0083156 | 0.0020841
7 | 0.012691 | 0.0031806
8 | 0.004844 | 0.001214
9 | 0.0068615 | 0.0017197
10 | 0.0052676 | 0.0013202
11 | 0.013458 | 0.0033729
12 | 0.0082094 | 0.0020575
13 | 0.0032299 | 0.0008095
14 | 0.0032546 | 0.00081567
15 | 0.0039145 | 0.00098105
16 | 0.0014925 | 0.00037405
17 | 0.0071714 | 0.0017973
18 | 0.013415 | 0.003362
19 | 0.0021158 | 0.00053028
20 | 0.0095503 | 0.0023935

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1