## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1502-27_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1502-27_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1502-27_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1502-27_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1502-27_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1502-27_0_2_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1502-27_0_2_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1502-27_0_2_node_29 | 0.4 | n |  | TRUE
8 | bus_LV_1502-27_0_2_node_15 | 0.4 | n |  | TRUE
9 | bus_LV_1502-27_0_2_node_26 | 0.4 | n |  | TRUE
10 | bus_LV_1502-27_0_2_node_16 | 0.4 | n |  | TRUE
11 | bus_LV_1502-27_0_2_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1502-27_0_2_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_1502-27_0_2_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_1502-27_0_2_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_1502-27_0_2_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_1502-27_0_2_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_1502-27_0_2_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_1502-27_0_2_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_1502-27_0_2_node_33 | 0.4 | n |  | TRUE
20 | bus_LV_1502-27_0_2_node_31 | 0.4 | n |  | TRUE
21 | bus_LV_1502-27_0_2_node_37 | 0.4 | n |  | TRUE
22 | bus_LV_1502-27_0_2_node_32 | 0.4 | n |  | TRUE
23 | bus_LV_1502-27_0_2_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_1502-27_0_2_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_1502-27_0_2_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_1502-27_0_2_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_1502-27_0_2_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_1502-27_0_2_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_1502-27_0_2_node_30 | 0.4 | n |  | TRUE
30 | bus_LV_1502-27_0_2_node_23 | 0.4 | n |  | TRUE
31 | bus_LV_1502-27_0_2_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_1502-27_0_2_node_25 | 0.4 | n |  | TRUE
33 | bus_LV_1502-27_0_2_node_27 | 0.4 | n |  | TRUE
34 | bus_LV_1502-27_0_2_node_28 | 0.4 | n |  | TRUE
35 | bus_LV_1502-27_0_2_node_36 | 0.4 | n |  | TRUE
36 | bus_LV_1502-27_0_2_node_35 | 0.4 | n |  | TRUE
37 | bus_LV_1502-27_0_2_node_34 | 0.4 | n |  | TRUE
38 | bus_MV_142_1_node_113 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1502-27_0_2_load_0 | 0 | 0.012257 | 0.0030719 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1502-27_0_2_load_1 | 1 | 0.0026737 | 0.00067009 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1502-27_0_2_load_2 | 2 | 0.0032851 | 0.00082334 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1502-27_0_2_load_3 | 3 | 0.003933 | 0.0009857 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1502-27_0_2_load_5 | 5 | 0.0055512 | 0.0013913 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1502-27_0_2_load_29 | 7 | 0.012091 | 0.0030304 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1502-27_0_2_load_15 | 8 | 0.0041276 | 0.0010345 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1502-27_0_2_load_26 | 9 | 0.006268 | 0.0015709 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1502-27_0_2_load_7 | 11 | 0.0074003 | 0.0018547 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1502-27_0_2_load_9 | 12 | 0.0050922 | 0.0012762 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1502-27_0_2_load_8 | 13 | 0.0047913 | 0.0012008 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1502-27_0_2_load_12 | 16 | 0.0063082 | 0.001581 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1502-27_0_2_load_13 | 17 | 0.0052716 | 0.0013212 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1502-27_0_2_load_14 | 18 | 0.0072108 | 0.0018072 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1502-27_0_2_load_31 | 20 | 0.0085103 | 0.0021329 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1502-27_0_2_load_37 | 21 | 0.0056575 | 0.0014179 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1502-27_0_2_load_17 | 23 | 0.010426 | 0.0026129 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1502-27_0_2_load_18 | 24 | 0.0049877 | 0.00125 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1502-27_0_2_load_19 | 25 | 0.0048795 | 0.0012229 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1502-27_0_2_load_20 | 26 | 0.014688 | 0.0036813 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1502-27_0_2_load_21 | 27 | 0.0065504 | 0.0016417 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1502-27_0_2_load_30 | 29 | 0.015885 | 0.0039812 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1502-27_0_2_load_23 | 30 | 0.0168 | 0.0042105 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1502-27_0_2_load_25 | 32 | 0.003718 | 0.00093182 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1502-27_0_2_load_27 | 33 | 0.0069182 | 0.0017339 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1502-27_0_2_load_28 | 34 | 0.011406 | 0.0028585 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1502-27_0_2_load_36 | 35 | 0.0074672 | 0.0018715 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1502-27_0_2_load_35 | 36 | 0.0082714 | 0.002073 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1502-27_0_2_load_34 | 37 | 0.0051801 | 0.0012983 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 29 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1502-27_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.009839 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1502-27_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.012401 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1502-27_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0070405 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1502-27_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.026182 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1502-27_0_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.012142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1502-27_0_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.005747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1502-27_0_2_line_6 | NAYY 4x150 SE | 5 | 7 | 0.0070067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1502-27_0_2_line_7 | NAYY 4x150 SE | 6 | 8 | 0.010546 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1502-27_0_2_line_8 | NAYY 4x150 SE | 7 | 9 | 0.0070532 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1502-27_0_2_line_9 | NAYY 4x150 SE | 8 | 10 | 0.01409 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1502-27_0_2_line_10 | NAYY 4x150 SE | 9 | 31 | 0.01205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1502-27_0_2_line_11 | NAYY 4x150 SE | 10 | 23 | 0.028185 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1502-27_0_2_line_12 | NAYY 4x150 SE | 10 | 24 | 0.029237 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1502-27_0_2_line_13 | NAYY 4x150 SE | 11 | 12 | 0.015402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1502-27_0_2_line_14 | NAYY 4x150 SE | 12 | 15 | 0.01434 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1502-27_0_2_line_15 | NAYY 4x150 SE | 13 | 14 | 0.013096 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1502-27_0_2_line_16 | NAYY 4x150 SE | 14 | 16 | 0.008888 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1502-27_0_2_line_17 | NAYY 4x150 SE | 14 | 17 | 0.012913 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1502-27_0_2_line_18 | NAYY 4x150 SE | 15 | 18 | 0.014177 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1502-27_0_2_line_19 | NAYY 4x150 SE | 17 | 19 | 0.015121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1502-27_0_2_line_20 | NAYY 4x150 SE | 18 | 20 | 0.016818 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1502-27_0_2_line_21 | NAYY 4x150 SE | 19 | 21 | 0.0015591 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
22 | LV_1502-27_0_2_line_22 | NAYY 4x150 SE | 19 | 22 | 0.01505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
23 | LV_1502-27_0_2_line_23 | NAYY 4x150 SE | 20 | 22 | 0.009165 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1502-27_0_2_line_24 | NAYY 4x150 SE | 21 | 28 | 0.023202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
25 | LV_1502-27_0_2_line_25 | NAYY 4x150 SE | 22 | 37 | 0.013609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
26 | LV_1502-27_0_2_line_26 | NAYY 4x150 SE | 23 | 25 | 0.0094632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1502-27_0_2_line_27 | NAYY 4x150 SE | 26 | 27 | 0.013714 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1502-27_0_2_line_28 | NAYY 4x150 SE | 27 | 28 | 0.014984 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1502-27_0_2_line_29 | NAYY 4x150 SE | 28 | 29 | 0.01788 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
30 | LV_1502-27_0_2_line_30 | NAYY 4x150 SE | 30 | 31 | 0.0089137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1502-27_0_2_line_31 | NAYY 4x150 SE | 31 | 32 | 0.014218 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1502-27_0_2_line_32 | NAYY 4x150 SE | 31 | 33 | 0.031578 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1502-27_0_2_line_33 | NAYY 4x150 SE | 32 | 34 | 0.022552 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1502-27_0_2_line_34 | NAYY 4x150 SE | 34 | 35 | 0.016056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
35 | LV_1502-27_0_2_line_35 | NAYY 4x150 SE | 35 | 36 | 0.025475 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
36 | LV_1502-27_0_2_line_36 | NAYY 4x150 SE | 36 | 37 | 0.018347 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1502-27_0_2_trafo_30 | 0.25 MVA 20/0.4 kV | 38 | 29 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2674670.6351 | 1202879.3714 | 2674678.3103 | 1202885.5274
1 | 2674670.6351 | 1202879.3714 | 2674670.6351 | 1202879.3714 | 2674664.8086 | 1202868.4246
2 | 2674678.3103 | 1202885.5274 | 2674683.8024 | 1202889.9325
3 | 2674652.5074 | 1202845.3128 | 2674664.8086 | 1202868.4246
4 | 2674694.4058 | 1202895.5808 | 2674687.3918 | 1202892.8114 | 2674683.8024 | 1202889.9325
5 | 2674649.9003 | 1202840.1881 | 2674652.5074 | 1202845.3128
6 | 2674694.4058 | 1202895.5808 | 2674700.9228 | 1202898.154
7 | 2674649.9003 | 1202840.1881 | 2674658.4252 | 1202833.9797
8 | 2674707.4832 | 1202900.7444 | 2674700.9228 | 1202898.154
9 | 2674665.895 | 1202822.0768 | 2674665.3515 | 1202823.5487 | 2674658.4252 | 1202833.9797
10 | 2674718.0593 | 1202906.292 | 2674714.29 | 1202903.432 | 2674707.4832 | 1202900.7444
11 | 2674665.895 | 1202822.0768 | 2674685.1169 | 1202837.4043 | 2674686.9183 | 1202834.2875
12 | 2674671.8217 | 1202793.5999 | 2674669.8301 | 1202803.1587 | 2674668.6279 | 1202814.7064 | 2674665.895 | 1202822.0768
13 | 2674780.6389 | 1202798.9833 | 2674789.8929 | 1202811.2948
14 | 2674798.5092 | 1202822.758 | 2674789.8929 | 1202811.2948
15 | 2674759.8189 | 1202775.956 | 2674769.9287 | 1202784.2798
16 | 2674759.8189 | 1202775.956 | 2674762.2158 | 1202767.3973
17 | 2674759.8189 | 1202775.956 | 2674754.86 | 1202787.8786
18 | 2674798.5092 | 1202822.758 | 2674785.496 | 1202817.1316
19 | 2674747.6776 | 1202801.1197 | 2674752.4355 | 1202793.7079 | 2674754.86 | 1202787.8786
20 | 2674770.0595 | 1202810.4574 | 2674785.496 | 1202817.1316
21 | 2674747.6776 | 1202801.1197 | 2674747.222 | 1202802.6107
22 | 2674747.6776 | 1202801.1197 | 2674761.6471 | 1202806.8202
23 | 2674761.6471 | 1202806.8202 | 2674770.0595 | 1202810.4574
24 | 2674740.4408 | 1202824.7993 | 2674747.222 | 1202802.6107
25 | 2674761.6471 | 1202806.8202 | 2674756.5689 | 1202819.4463
26 | 2674686.9183 | 1202834.2875 | 2674691.6538 | 1202826.0944
27 | 2674713.55 | 1202814.7791 | 2674726.4003 | 1202819.5675
28 | 2674740.4408 | 1202824.7993 | 2674726.4003 | 1202819.5675
29 | 2674740.4408 | 1202824.7993 | 2674735.2132 | 1202841.8976
30 | 2674718.0593 | 1202906.292 | 2674718.3894 | 1202912.7557 | 2674717.8233 | 1202915.1308
31 | 2674718.0593 | 1202906.292 | 2674725.3748 | 1202900.0352 | 2674726.5262 | 1202895.5898
32 | 2674718.0593 | 1202906.292 | 2674719.7782 | 1202892.3827 | 2674724.9132 | 1202875.587
33 | 2674732.2284 | 1202873.7725 | 2674731.9798 | 1202874.5354 | 2674726.5262 | 1202895.5898
34 | 2674737.2021 | 1202858.5062 | 2674732.2284 | 1202873.7725
35 | 2674748.4357 | 1202835.8226 | 2674740.1868 | 1202849.3447 | 2674737.2021 | 1202858.5062
36 | 2674748.4357 | 1202835.8226 | 2674752.9756 | 1202828.3806 | 2674756.5689 | 1202819.4463

## bus_geodata
| x | y | coords
0 | 2674670.6351 | 1202879.3714
1 | 2674678.3103 | 1202885.5274
2 | 2674664.8086 | 1202868.4246
3 | 2674683.8024 | 1202889.9325
4 | 2674652.5074 | 1202845.3128
5 | 2674694.4058 | 1202895.5808
6 | 2674649.9003 | 1202840.1881
7 | 2674700.9228 | 1202898.154
8 | 2674658.4252 | 1202833.9797
9 | 2674707.4832 | 1202900.7444
10 | 2674665.895 | 1202822.0768
11 | 2674780.6389 | 1202798.9833
12 | 2674789.8929 | 1202811.2948
13 | 2674769.9287 | 1202784.2798
14 | 2674759.8189 | 1202775.956
15 | 2674798.5092 | 1202822.758
16 | 2674762.2158 | 1202767.3973
17 | 2674754.86 | 1202787.8786
18 | 2674785.496 | 1202817.1316
19 | 2674747.6776 | 1202801.1197
20 | 2674770.0595 | 1202810.4574
21 | 2674747.222 | 1202802.6107
22 | 2674761.6471 | 1202806.8202
23 | 2674686.9183 | 1202834.2875
24 | 2674671.8217 | 1202793.5999
25 | 2674691.6538 | 1202826.0944
26 | 2674713.55 | 1202814.7791
27 | 2674726.4003 | 1202819.5675
28 | 2674740.4408 | 1202824.7993
29 | 2674735.2132 | 1202841.8976
30 | 2674717.8233 | 1202915.1308
31 | 2674718.0593 | 1202906.292
32 | 2674726.5262 | 1202895.5898
33 | 2674724.9132 | 1202875.587
34 | 2674732.2284 | 1202873.7725
35 | 2674737.2021 | 1202858.5062
36 | 2674748.4357 | 1202835.8226
37 | 2674756.5689 | 1202819.4463
38 | 2674740.4408 | 1202824.7993

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97658 | -0.16456 | 0.012257 | 0.0030719
1 | 0.97715 | -0.16044 | 0.0026737 | 0.00067009
2 | 0.97608 | -0.16816 | 0.0032851 | 0.00082334
3 | 0.97759 | -0.15731 | 0.003933 | 0.0009857
4 | 0.97514 | -0.17486 | 0 | 0
5 | 0.97842 | -0.1514 | 0.0055512 | 0.0013913
6 | 0.97493 | -0.17634 | 0 | 0
7 | 0.97895 | -0.1476 | 0.012091 | 0.0030304
8 | 0.97456 | -0.17904 | 0.0041276 | 0.0010345
9 | 0.97961 | -0.14288 | 0.006268 | 0.0015709
10 | 0.97414 | -0.18205 | 0 | 0
11 | 0.9909 | -0.06333 | 0.0074003 | 0.0018547
12 | 0.99107 | -0.062172 | 0.0050922 | 0.0012762
13 | 0.99351 | -0.045088 | 0.0047913 | 0.0012008
14 | 0.9936 | -0.044454 | 0 | 0
15 | 0.99132 | -0.060352 | 0 | 0
16 | 0.99352 | -0.045021 | 0.0063082 | 0.001581
17 | 0.9938 | -0.043005 | 0.0052716 | 0.0013212
18 | 0.99158 | -0.058553 | 0.0072108 | 0.0018072
19 | 0.99416 | -0.040504 | 0 | 0
20 | 0.99206 | -0.05519 | 0.0085103 | 0.0021329
21 | 0.99436 | -0.039127 | 0.0056575 | 0.0014179
22 | 0.99243 | -0.052569 | 0 | 0
23 | 0.97351 | -0.18659 | 0.010426 | 0.0026129
24 | 0.97393 | -0.18358 | 0.0049877 | 0.00125
25 | 0.97344 | -0.18708 | 0.0048795 | 0.0012229
26 | 0.99665 | -0.023269 | 0.014688 | 0.0036813
27 | 0.99693 | -0.021245 | 0.0065504 | 0.0016417
28 | 0.99739 | -0.018051 | 0 | 0
29 | 1 | 0 | -0.2055 | -0.051694
30 | 0.98064 | -0.13561 | 0.0168 | 0.0042105
31 | 0.98085 | -0.13406 | 0 | 0
32 | 0.98281 | -0.12019 | 0.003718 | 0.00093182
33 | 0.98054 | -0.13633 | 0.0069182 | 0.0017339
34 | 0.98603 | -0.097443 | 0.011406 | 0.0028585
35 | 0.9873 | -0.088443 | 0.0074672 | 0.0018715
36 | 0.98947 | -0.073242 | 0.0082714 | 0.002073
37 | 0.99114 | -0.061563 | 0.0051801 | 0.0012983
38 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.040033 | -0.010041 | 0.040056 | 0.01005 | 2.2846e-05 | 8.6637e-06 | 0.061001 | 0.061001 | 0.061001 | 0.97658 | -0.16456 | 0.97715 | -0.16044 | 22.5929
1 | 0.027776 | 0.006969 | -0.027762 | -0.0069638 | 1.3862e-05 | 5.1765e-06 | 0.042325 | 0.042325 | 0.042325 | 0.97658 | -0.16456 | 0.97608 | -0.16816 | 15.6759
2 | -0.042729 | -0.01072 | 0.042748 | 0.010727 | 1.8603e-05 | 7.0667e-06 | 0.065072 | 0.065072 | 0.065072 | 0.97715 | -0.16044 | 0.97759 | -0.15731 | 24.1009
3 | 0.024477 | 0.0061405 | -0.024454 | -0.006132 | 2.275e-05 | 8.4232e-06 | 0.037317 | 0.037317 | 0.037317 | 0.97608 | -0.16816 | 0.97514 | -0.17486 | 13.821
4 | -0.046681 | -0.011712 | 0.046719 | 0.011727 | 3.8258e-05 | 1.4562e-05 | 0.071059 | 0.071059 | 0.071059 | 0.97759 | -0.15731 | 0.97842 | -0.1514 | 26.3181
5 | 0.024454 | 0.006132 | -0.024449 | -0.0061302 | 4.9938e-06 | 1.849e-06 | 0.037317 | 0.037317 | 0.037317 | 0.97514 | -0.17486 | 0.97493 | -0.17634 | 13.821
6 | -0.05227 | -0.013118 | 0.052298 | 0.013129 | 2.7634e-05 | 1.054e-05 | 0.079501 | 0.079501 | 0.079501 | 0.97842 | -0.1514 | 0.97895 | -0.1476 | 29.4449
7 | 0.024449 | 0.0061302 | -0.02444 | -0.0061268 | 9.164e-06 | 3.3931e-06 | 0.037317 | 0.037317 | 0.037317 | 0.97493 | -0.17634 | 0.97456 | -0.17904 | 13.8211
8 | -0.064389 | -0.016159 | 0.064432 | 0.016175 | 4.2166e-05 | 1.6129e-05 | 0.09788 | 0.09788 | 0.09788 | 0.97895 | -0.1476 | 0.97961 | -0.14288 | 36.252
9 | 0.020312 | 0.0050923 | -0.020304 | -0.0050893 | 8.4574e-06 | 3.0774e-06 | 0.031015 | 0.031015 | 0.031015 | 0.97456 | -0.17904 | 0.97414 | -0.18205 | 11.4869
10 | -0.0707 | -0.017746 | 0.070786 | 0.017779 | 8.6732e-05 | 3.3207e-05 | 0.1074 | 0.1074 | 0.1074 | 0.97961 | -0.14288 | 0.98085 | -0.13406 | 39.7782
11 | 0.015315 | 0.0038392 | -0.015305 | -0.0038358 | 9.6254e-06 | 3.3514e-06 | 0.023394 | 0.023394 | 0.023394 | 0.97414 | -0.18205 | 0.97351 | -0.18659 | 8.6646
12 | 0.0049888 | 0.0012501 | -0.0049877 | -0.00125 | 1.0595e-06 | 4.3576e-08 | 0.0076204 | 0.0076205 | 0.0076205 | 0.97414 | -0.18205 | 0.97393 | -0.18358 | 2.8224
13 | -0.0074003 | -0.0018547 | 0.0074014 | 0.0018549 | 1.1869e-06 | 2.5805e-07 | 0.011113 | 0.011113 | 0.011113 | 0.9909 | -0.06333 | 0.99107 | -0.062172 | 4.1158
14 | -0.012494 | -0.0031312 | 0.012497 | 0.0031322 | 3.1487e-06 | 1.0262e-06 | 0.018758 | 0.018758 | 0.018758 | 0.99107 | -0.062172 | 0.99132 | -0.060352 | 6.9475
15 | -0.0047913 | -0.0012008 | 0.0047917 | 0.0012008 | 4.2081e-07 | -7.7445e-09 | 0.0071762 | 0.0071761 | 0.0071762 | 0.99351 | -0.045088 | 0.9936 | -0.044454 | 2.6578
16 | 0.0063087 | 0.0015811 | -0.0063082 | -0.001581 | 4.9506e-07 | 7.5302e-08 | 0.0094479 | 0.0094479 | 0.0094479 | 0.9936 | -0.044454 | 0.99352 | -0.045021 | 3.4992
17 | -0.0111 | -0.0027819 | 0.011103 | 0.0027826 | 2.2268e-06 | 6.8917e-07 | 0.016624 | 0.016624 | 0.016624 | 0.9936 | -0.044454 | 0.9938 | -0.043005 | 6.157
18 | -0.012497 | -0.0031322 | 0.0125 | 0.0031332 | 3.1129e-06 | 1.0144e-06 | 0.018758 | 0.018758 | 0.018758 | 0.99132 | -0.060352 | 0.99158 | -0.058553 | 6.9475
19 | -0.016374 | -0.0041038 | 0.01638 | 0.0041057 | 5.6715e-06 | 1.9854e-06 | 0.024517 | 0.024517 | 0.024517 | 0.9938 | -0.043005 | 0.99416 | -0.040504 | 9.0804
20 | -0.019711 | -0.0049404 | 0.01972 | 0.0049437 | 9.1815e-06 | 3.3143e-06 | 0.029579 | 0.029579 | 0.029579 | 0.99158 | -0.058553 | 0.99206 | -0.05519 | 10.9552
21 | -0.1767 | -0.044529 | 0.17673 | 0.044542 | 3.4047e-05 | 1.3055e-05 | 0.26456 | 0.26456 | 0.26456 | 0.99416 | -0.040504 | 0.99436 | -0.039127 | 48.9933
22 | 0.16032 | 0.040423 | -0.16005 | -0.04032 | 0.00027057 | 0.00010368 | 0.24005 | 0.24005 | 0.24005 | 0.99416 | -0.040504 | 0.99243 | -0.052569 | 44.4531
23 | -0.02823 | -0.0070766 | 0.02824 | 0.0070804 | 1.0254e-05 | 3.8255e-06 | 0.042344 | 0.042344 | 0.042344 | 0.99206 | -0.05519 | 0.99243 | -0.052569 | 15.6829
24 | -0.18239 | -0.04596 | 0.18293 | 0.046167 | 0.00053963 | 0.00020695 | 0.27303 | 0.27303 | 0.27303 | 0.99436 | -0.039127 | 0.99739 | -0.018051 | 50.5611
25 | 0.13181 | 0.033239 | -0.13164 | -0.033176 | 0.00016596 | 6.348e-05 | 0.1977 | 0.1977 | 0.1977 | 0.99243 | -0.052569 | 0.99114 | -0.061563 | 36.6117
26 | 0.0048798 | 0.0012229 | -0.0048795 | -0.0012229 | 3.2852e-07 | 8.7031e-09 | 0.0074588 | 0.0074588 | 0.0074588 | 0.97351 | -0.18659 | 0.97344 | -0.18708 | 2.7625
27 | -0.014688 | -0.0036813 | 0.014693 | 0.0036827 | 4.1154e-06 | 1.4041e-06 | 0.02193 | 0.02193 | 0.02193 | 0.99665 | -0.023269 | 0.99693 | -0.021245 | 8.1223
28 | -0.021243 | -0.0053244 | 0.021252 | 0.0053278 | 9.3997e-06 | 3.4198e-06 | 0.031707 | 0.031707 | 0.031707 | 0.99693 | -0.021245 | 0.99739 | -0.018051 | 11.7434
29 | -0.20418 | -0.051495 | 0.2047 | 0.051694 | 0.00051804 | 0.00019878 | 0.30474 | 0.30474 | 0.30474 | 0.99739 | -0.018051 | 1 | 0 | 56.4327
30 | -0.0168 | -0.0042105 | 0.016804 | 0.0042118 | 3.6147e-06 | 1.2778e-06 | 0.025493 | 0.025492 | 0.025493 | 0.98064 | -0.13561 | 0.98085 | -0.13406 | 9.4417
31 | -0.09451 | -0.023725 | 0.094693 | 0.023795 | 0.00018242 | 6.9984e-05 | 0.14339 | 0.14339 | 0.14339 | 0.98085 | -0.13406 | 0.98281 | -0.12019 | 53.1082
32 | 0.0069203 | 0.0017343 | -0.0069182 | -0.0017339 | 2.1719e-06 | 4.369e-07 | 0.010499 | 0.010499 | 0.010499 | 0.98085 | -0.13406 | 0.98054 | -0.13633 | 3.8884
33 | -0.098411 | -0.024727 | 0.098723 | 0.024847 | 0.00031251 | 0.00011991 | 0.14902 | 0.14902 | 0.14902 | 0.98281 | -0.12019 | 0.98603 | -0.097443 | 55.1931
34 | -0.11013 | -0.027706 | 0.11027 | 0.027759 | 0.00013843 | 5.2832e-05 | 0.16623 | 0.16623 | 0.16623 | 0.98603 | -0.097443 | 0.9873 | -0.088443 | 30.784
35 | -0.11773 | -0.02963 | 0.11798 | 0.029726 | 0.00025038 | 9.5648e-05 | 0.17749 | 0.17749 | 0.17749 | 0.9873 | -0.088443 | 0.98947 | -0.073242 | 32.8681
36 | -0.12626 | -0.031799 | 0.12646 | 0.031878 | 0.00020649 | 7.8947e-05 | 0.18993 | 0.18993 | 0.18993 | 0.98947 | -0.073242 | 0.99114 | -0.061563 | 35.1715

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.22139 | 0.055675

## res_load
| p_mw | q_mvar
0 | 0.012257 | 0.0030719
1 | 0.0026737 | 0.00067009
2 | 0.0032851 | 0.00082334
3 | 0.003933 | 0.0009857
4 | 0.0055512 | 0.0013913
5 | 0.012091 | 0.0030304
6 | 0.0041276 | 0.0010345
7 | 0.006268 | 0.0015709
8 | 0.0074003 | 0.0018547
9 | 0.0050922 | 0.0012762
10 | 0.0047913 | 0.0012008
11 | 0.0063082 | 0.001581
12 | 0.0052716 | 0.0013212
13 | 0.0072108 | 0.0018072
14 | 0.0085103 | 0.0021329
15 | 0.0056575 | 0.0014179
16 | 0.010426 | 0.0026129
17 | 0.0049877 | 0.00125
18 | 0.0048795 | 0.0012229
19 | 0.014688 | 0.0036813
20 | 0.0065504 | 0.0016417
21 | 0.015885 | 0.0039812
22 | 0.0168 | 0.0042105
23 | 0.003718 | 0.00093182
24 | 0.0069182 | 0.0017339
25 | 0.011406 | 0.0028585
26 | 0.0074672 | 0.0018715
27 | 0.0082714 | 0.002073
28 | 0.0051801 | 0.0012983

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1