## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1503-11_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1503-11_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1503-11_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1503-11_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1503-11_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1503-11_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1503-11_0_3_node_84 | 0.4 | n |  | TRUE
7 | bus_LV_1503-11_0_3_node_85 | 0.4 | n |  | TRUE
8 | bus_LV_1503-11_0_3_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1503-11_0_3_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_1503-11_0_3_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1503-11_0_3_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_1503-11_0_3_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_1503-11_0_3_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_1503-11_0_3_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_1503-11_0_3_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_1503-11_0_3_node_98 | 0.4 | n |  | TRUE
17 | bus_LV_1503-11_0_3_node_23 | 0.4 | n |  | TRUE
18 | bus_LV_1503-11_0_3_node_20 | 0.4 | n |  | TRUE
19 | bus_LV_1503-11_0_3_node_99 | 0.4 | n |  | TRUE
20 | bus_LV_1503-11_0_3_node_22 | 0.4 | n |  | TRUE
21 | bus_LV_1503-11_0_3_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_1503-11_0_3_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_1503-11_0_3_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_1503-11_0_3_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_1503-11_0_3_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_1503-11_0_3_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_1503-11_0_3_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_1503-11_0_3_node_80 | 0.4 | n |  | TRUE
29 | bus_LV_1503-11_0_3_node_81 | 0.4 | n |  | TRUE
30 | bus_LV_1503-11_0_3_node_27 | 0.4 | n |  | TRUE
31 | bus_LV_1503-11_0_3_node_101 | 0.4 | n |  | TRUE
32 | bus_LV_1503-11_0_3_node_100 | 0.4 | n |  | TRUE
33 | bus_LV_1503-11_0_3_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_1503-11_0_3_node_24 | 0.4 | n |  | TRUE
35 | bus_LV_1503-11_0_3_node_25 | 0.4 | n |  | TRUE
36 | bus_LV_1503-11_0_3_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_1503-11_0_3_node_46 | 0.4 | n |  | TRUE
38 | bus_LV_1503-11_0_3_node_47 | 0.4 | n |  | TRUE
39 | bus_LV_1503-11_0_3_node_75 | 0.4 | n |  | TRUE
40 | bus_LV_1503-11_0_3_node_42 | 0.4 | n |  | TRUE
41 | bus_LV_1503-11_0_3_node_112 | 0.4 | n |  | TRUE
42 | bus_LV_1503-11_0_3_node_29 | 0.4 | n |  | TRUE
43 | bus_LV_1503-11_0_3_node_30 | 0.4 | n |  | TRUE
44 | bus_LV_1503-11_0_3_node_32 | 0.4 | n |  | TRUE
45 | bus_LV_1503-11_0_3_node_33 | 0.4 | n |  | TRUE
46 | bus_LV_1503-11_0_3_node_34 | 0.4 | n |  | TRUE
47 | bus_LV_1503-11_0_3_node_35 | 0.4 | n |  | TRUE
48 | bus_LV_1503-11_0_3_node_36 | 0.4 | n |  | TRUE
49 | bus_LV_1503-11_0_3_node_37 | 0.4 | n |  | TRUE
50 | bus_LV_1503-11_0_3_node_52 | 0.4 | n |  | TRUE
51 | bus_LV_1503-11_0_3_node_39 | 0.4 | n |  | TRUE
52 | bus_LV_1503-11_0_3_node_56 | 0.4 | n |  | TRUE
53 | bus_LV_1503-11_0_3_node_51 | 0.4 | n |  | TRUE
54 | bus_LV_1503-11_0_3_node_38 | 0.4 | n |  | TRUE
55 | bus_LV_1503-11_0_3_node_40 | 0.4 | n |  | TRUE
56 | bus_LV_1503-11_0_3_node_41 | 0.4 | n |  | TRUE
57 | bus_LV_1503-11_0_3_node_43 | 0.4 | n |  | TRUE
58 | bus_LV_1503-11_0_3_node_44 | 0.4 | n |  | TRUE
59 | bus_LV_1503-11_0_3_node_45 | 0.4 | n |  | TRUE
60 | bus_LV_1503-11_0_3_node_48 | 0.4 | n |  | TRUE
61 | bus_LV_1503-11_0_3_node_49 | 0.4 | n |  | TRUE
62 | bus_LV_1503-11_0_3_node_74 | 0.4 | n |  | TRUE
63 | bus_LV_1503-11_0_3_node_71 | 0.4 | n |  | TRUE
64 | bus_LV_1503-11_0_3_node_69 | 0.4 | n |  | TRUE
65 | bus_LV_1503-11_0_3_node_50 | 0.4 | n |  | TRUE
66 | bus_LV_1503-11_0_3_node_53 | 0.4 | n |  | TRUE
67 | bus_LV_1503-11_0_3_node_54 | 0.4 | n |  | TRUE
68 | bus_LV_1503-11_0_3_node_55 | 0.4 | n |  | TRUE
69 | bus_LV_1503-11_0_3_node_67 | 0.4 | n |  | TRUE
70 | bus_LV_1503-11_0_3_node_64 | 0.4 | n |  | TRUE
71 | bus_LV_1503-11_0_3_node_58 | 0.4 | n |  | TRUE
72 | bus_LV_1503-11_0_3_node_104 | 0.4 | n |  | TRUE
73 | bus_LV_1503-11_0_3_node_92 | 0.4 | n |  | TRUE
74 | bus_LV_1503-11_0_3_node_63 | 0.4 | n |  | TRUE
75 | bus_LV_1503-11_0_3_node_57 | 0.4 | n |  | TRUE
76 | bus_LV_1503-11_0_3_node_59 | 0.4 | n |  | TRUE
77 | bus_LV_1503-11_0_3_node_60 | 0.4 | n |  | TRUE
78 | bus_LV_1503-11_0_3_node_61 | 0.4 | n |  | TRUE
79 | bus_LV_1503-11_0_3_node_62 | 0.4 | n |  | TRUE
80 | bus_LV_1503-11_0_3_node_76 | 0.4 | n |  | TRUE
81 | bus_LV_1503-11_0_3_node_82 | 0.4 | n |  | TRUE
82 | bus_LV_1503-11_0_3_node_65 | 0.4 | n |  | TRUE
83 | bus_LV_1503-11_0_3_node_66 | 0.4 | n |  | TRUE
84 | bus_LV_1503-11_0_3_node_68 | 0.4 | n |  | TRUE
85 | bus_LV_1503-11_0_3_node_88 | 0.4 | n |  | TRUE
86 | bus_LV_1503-11_0_3_node_77 | 0.4 | n |  | TRUE
87 | bus_LV_1503-11_0_3_node_91 | 0.4 | n |  | TRUE
88 | bus_LV_1503-11_0_3_node_89 | 0.4 | n |  | TRUE
89 | bus_LV_1503-11_0_3_node_106 | 0.4 | n |  | TRUE
90 | bus_LV_1503-11_0_3_node_70 | 0.4 | n |  | TRUE
91 | bus_LV_1503-11_0_3_node_105 | 0.4 | n |  | TRUE
92 | bus_LV_1503-11_0_3_node_72 | 0.4 | n |  | TRUE
93 | bus_LV_1503-11_0_3_node_73 | 0.4 | n |  | TRUE
94 | bus_LV_1503-11_0_3_node_102 | 0.4 | n |  | TRUE
95 | bus_LV_1503-11_0_3_node_83 | 0.4 | n |  | TRUE
96 | bus_LV_1503-11_0_3_node_103 | 0.4 | n |  | TRUE
97 | bus_LV_1503-11_0_3_node_78 | 0.4 | n |  | TRUE
98 | bus_LV_1503-11_0_3_node_79 | 0.4 | n |  | TRUE
99 | bus_LV_1503-11_0_3_node_113 | 0.4 | n |  | TRUE
100 | bus_LV_1503-11_0_3_node_97 | 0.4 | n |  | TRUE
101 | bus_LV_1503-11_0_3_node_95 | 0.4 | n |  | TRUE
102 | bus_LV_1503-11_0_3_node_86 | 0.4 | n |  | TRUE
103 | bus_LV_1503-11_0_3_node_87 | 0.4 | n |  | TRUE
104 | bus_LV_1503-11_0_3_node_107 | 0.4 | n |  | TRUE
105 | bus_LV_1503-11_0_3_node_90 | 0.4 | n |  | TRUE
106 | bus_LV_1503-11_0_3_node_93 | 0.4 | n |  | TRUE
107 | bus_LV_1503-11_0_3_node_94 | 0.4 | n |  | TRUE
108 | bus_LV_1503-11_0_3_node_96 | 0.4 | n |  | TRUE
109 | bus_LV_1503-11_0_3_node_110 | 0.4 | n |  | TRUE
110 | bus_LV_1503-11_0_3_node_108 | 0.4 | n |  | TRUE
111 | bus_LV_1503-11_0_3_node_109 | 0.4 | n |  | TRUE
112 | bus_LV_1503-11_0_3_node_111 | 0.4 | n |  | TRUE
113 | bus_MV_136_1_node_103 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1503-11_0_3_load_0 | 0 | 0.00041947 | 0.00010513 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1503-11_0_3_load_3 | 3 | 0.00053029 | 0.0001329 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1503-11_0_3_load_4 | 4 | 0.00044592 | 0.00011176 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1503-11_0_3_load_5 | 5 | 0.00022448 | 5.626e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1503-11_0_3_load_84 | 6 | 0.00043244 | 0.00010838 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1503-11_0_3_load_85 | 7 | 0.00093916 | 0.00023537 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1503-11_0_3_load_6 | 8 | 0.0058459 | 0.0014651 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1503-11_0_3_load_7 | 9 | 0.0010973 | 0.000275 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1503-11_0_3_load_8 | 10 | 0.0014347 | 0.00035958 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1503-11_0_3_load_9 | 11 | 0.0014929 | 0.00037417 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1503-11_0_3_load_11 | 13 | 0.0021274 | 0.00053317 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1503-11_0_3_load_13 | 15 | 0.0032032 | 0.0008028 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1503-11_0_3_load_98 | 16 | 0.0022699 | 0.00056889 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1503-11_0_3_load_23 | 17 | 0.0049677 | 0.001245 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1503-11_0_3_load_20 | 18 | 0.0026373 | 0.00066098 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1503-11_0_3_load_99 | 19 | 0.0036378 | 0.00091173 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1503-11_0_3_load_22 | 20 | 0.0041637 | 0.0010435 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1503-11_0_3_load_14 | 22 | 0.0038751 | 0.0009712 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1503-11_0_3_load_15 | 23 | 0.0020263 | 0.00050783 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1503-11_0_3_load_16 | 24 | 0.0019079 | 0.00047816 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1503-11_0_3_load_18 | 25 | 0.0019086 | 0.00047835 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1503-11_0_3_load_21 | 27 | 0.0045569 | 0.0011421 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1503-11_0_3_load_80 | 28 | 0.0006723 | 0.0001685 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1503-11_0_3_load_81 | 29 | 0.002663 | 0.00066741 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1503-11_0_3_load_27 | 30 | 0.0037112 | 0.00093011 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1503-11_0_3_load_101 | 31 | 0.0028287 | 0.00070894 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1503-11_0_3_load_100 | 32 | 0.0032491 | 0.00081429 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1503-11_0_3_load_28 | 33 | 0.0018101 | 0.00045365 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1503-11_0_3_load_24 | 34 | 0.0021476 | 0.00053823 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1503-11_0_3_load_47 | 38 | 0.0021476 | 0.00053823 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1503-11_0_3_load_75 | 39 | 0.0013599 | 0.00034083 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1503-11_0_3_load_112 | 41 | 0.0027339 | 0.00068518 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1503-11_0_3_load_29 | 42 | 0.0049176 | 0.0012325 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1503-11_0_3_load_30 | 43 | 0.0074506 | 0.0018673 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1503-11_0_3_load_33 | 45 | 0.0041732 | 0.0010459 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1503-11_0_3_load_35 | 47 | 0.0026689 | 0.00066888 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1503-11_0_3_load_36 | 48 | 0.0084825 | 0.0021259 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1503-11_0_3_load_37 | 49 | 0.0068056 | 0.0017056 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1503-11_0_3_load_56 | 52 | 0.017148 | 0.0042978 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1503-11_0_3_load_38 | 54 | 0.0020341 | 0.0005098 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1503-11_0_3_load_41 | 56 | 0.0020314 | 0.00050913 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1503-11_0_3_load_43 | 57 | 0.0013152 | 0.00032962 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1503-11_0_3_load_44 | 58 | 0.0012388 | 0.00031047 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1503-11_0_3_load_45 | 59 | 0.0022595 | 0.00056628 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1503-11_0_3_load_48 | 60 | 0.003344 | 0.00083808 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1503-11_0_3_load_74 | 62 | 0.0019637 | 0.00049215 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1503-11_0_3_load_71 | 63 | 0.0019778 | 0.00049568 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1503-11_0_3_load_69 | 64 | 0.0016707 | 0.00041871 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1503-11_0_3_load_50 | 65 | 0.0063631 | 0.0015947 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1503-11_0_3_load_55 | 68 | 0.00011059 | 2.7716e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1503-11_0_3_load_67 | 69 | 7.063e-05 | 1.7702e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1503-11_0_3_load_64 | 70 | 0.00015589 | 3.907e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1503-11_0_3_load_58 | 71 | 0.00033866 | 8.4877e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1503-11_0_3_load_104 | 72 | 0.00028974 | 7.2615e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1503-11_0_3_load_63 | 74 | 0.00011364 | 2.8482e-05 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1503-11_0_3_load_57 | 75 | 9.9467e-05 | 2.4929e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1503-11_0_3_load_59 | 76 | 0.00030722 | 7.6995e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1503-11_0_3_load_60 | 77 | 0.00014062 | 3.5243e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1503-11_0_3_load_61 | 78 | 0.00093169 | 0.0002335 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1503-11_0_3_load_62 | 79 | 8.6633e-05 | 2.1712e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1503-11_0_3_load_76 | 80 | 0.00043839 | 0.00010987 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1503-11_0_3_load_82 | 81 | 0.0010072 | 0.00025242 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1503-11_0_3_load_65 | 82 | 0.00095357 | 0.00023899 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1503-11_0_3_load_66 | 83 | 0.00026019 | 6.521e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1503-11_0_3_load_68 | 84 | 8.9258e-05 | 2.237e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1503-11_0_3_load_88 | 85 | 0.00014772 | 3.7021e-05 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1503-11_0_3_load_77 | 86 | 0.00014654 | 3.6727e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1503-11_0_3_load_89 | 88 | 0.00016577 | 4.1546e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1503-11_0_3_load_106 | 89 | 0.00011578 | 2.9016e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1503-11_0_3_load_70 | 90 | 0.0015695 | 0.00039336 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1503-11_0_3_load_105 | 91 | 0.00073091 | 0.00018318 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1503-11_0_3_load_72 | 92 | 0.00050288 | 0.00012603 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1503-11_0_3_load_73 | 93 | 0.00027395 | 6.8659e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1503-11_0_3_load_102 | 94 | 0.00048411 | 0.00012133 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1503-11_0_3_load_83 | 95 | 0.0020286 | 0.0005084 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1503-11_0_3_load_78 | 97 | 8.7157e-05 | 2.1844e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1503-11_0_3_load_79 | 98 | 0.00012743 | 3.1937e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1503-11_0_3_load_113 | 99 | 0.00037796 | 9.4725e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1503-11_0_3_load_97 | 100 | 0.0001776 | 4.451e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1503-11_0_3_load_95 | 101 | 8.3083e-05 | 2.0823e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1503-11_0_3_load_86 | 102 | 0.0007129 | 0.00017867 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1503-11_0_3_load_107 | 104 | 0.00011516 | 2.8861e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1503-11_0_3_load_90 | 105 | 0.00014922 | 3.7397e-05 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1503-11_0_3_load_93 | 106 | 0.00024615 | 6.1691e-05 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1503-11_0_3_load_108 | 110 | 0.00013993 | 3.507e-05 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1503-11_0_3_load_109 | 111 | 0.00036301 | 9.098e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 38 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1503-11_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0082277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1503-11_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.038295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1503-11_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.037136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1503-11_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.024351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1503-11_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.041772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1503-11_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.0071259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1503-11_0_3_line_6 | NAYY 4x150 SE | 6 | 7 | 0.012109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1503-11_0_3_line_7 | NAYY 4x150 SE | 7 | 102 | 0.032253 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1503-11_0_3_line_8 | NAYY 4x150 SE | 8 | 9 | 0.02147 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1503-11_0_3_line_9 | NAYY 4x150 SE | 8 | 10 | 0.004649 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1503-11_0_3_line_10 | NAYY 4x150 SE | 9 | 11 | 0.0021832 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1503-11_0_3_line_11 | NAYY 4x150 SE | 10 | 12 | 0.057752 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1503-11_0_3_line_12 | NAYY 4x150 SE | 11 | 13 | 0.012413 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1503-11_0_3_line_13 | NAYY 4x150 SE | 12 | 14 | 0.073086 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1503-11_0_3_line_14 | NAYY 4x150 SE | 12 | 15 | 0.022196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1503-11_0_3_line_15 | NAYY 4x150 SE | 13 | 16 | 0.021483 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1503-11_0_3_line_16 | NAYY 4x150 SE | 14 | 17 | 0.077733 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1503-11_0_3_line_17 | NAYY 4x150 SE | 15 | 18 | 0.0095355 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1503-11_0_3_line_18 | NAYY 4x150 SE | 16 | 19 | 0.029814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1503-11_0_3_line_19 | NAYY 4x150 SE | 17 | 20 | 0.024391 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1503-11_0_3_line_20 | NAYY 4x150 SE | 18 | 21 | 0.010265 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1503-11_0_3_line_21 | NAYY 4x150 SE | 19 | 103 | 0.063925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1503-11_0_3_line_22 | NAYY 4x150 SE | 20 | 34 | 0.034309 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1503-11_0_3_line_23 | NAYY 4x150 SE | 21 | 26 | 0.036763 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1503-11_0_3_line_24 | NAYY 4x150 SE | 21 | 23 | 0.015013 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1503-11_0_3_line_25 | NAYY 4x150 SE | 22 | 23 | 0.0051465 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1503-11_0_3_line_26 | NAYY 4x150 SE | 22 | 24 | 0.024431 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1503-11_0_3_line_27 | NAYY 4x150 SE | 24 | 25 | 7.6046e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1503-11_0_3_line_28 | NAYY 4x150 SE | 25 | 27 | 0.0044213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1503-11_0_3_line_29 | NAYY 4x150 SE | 26 | 28 | 0.062987 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1503-11_0_3_line_30 | NAYY 4x150 SE | 26 | 29 | 0.031981 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1503-11_0_3_line_31 | NAYY 4x150 SE | 27 | 30 | 0.024314 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1503-11_0_3_line_32 | NAYY 4x150 SE | 28 | 31 | 0.01054 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1503-11_0_3_line_33 | NAYY 4x150 SE | 29 | 32 | 0.0013384 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1503-11_0_3_line_34 | NAYY 4x150 SE | 30 | 33 | 0.013831 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1503-11_0_3_line_35 | NAYY 4x150 SE | 33 | 42 | 0.0061204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1503-11_0_3_line_36 | NAYY 4x150 SE | 34 | 35 | 0.017398 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1503-11_0_3_line_37 | NAYY 4x150 SE | 35 | 36 | 0.012068 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
38 | LV_1503-11_0_3_line_38 | NAYY 4x150 SE | 36 | 37 | 0.012147 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1503-11_0_3_line_39 | NAYY 4x150 SE | 36 | 38 | 0.028668 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
40 | LV_1503-11_0_3_line_40 | NAYY 4x150 SE | 37 | 39 | 0.033586 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1503-11_0_3_line_41 | NAYY 4x150 SE | 37 | 40 | 0.010017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1503-11_0_3_line_42 | NAYY 4x150 SE | 38 | 41 | 0.011092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1503-11_0_3_line_43 | NAYY 4x150 SE | 39 | 62 | 0.02992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1503-11_0_3_line_44 | NAYY 4x150 SE | 40 | 51 | 0.016623 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1503-11_0_3_line_45 | NAYY 4x150 SE | 40 | 48 | 0.061652 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1503-11_0_3_line_46 | NAYY 4x150 SE | 43 | 44 | 0.027284 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1503-11_0_3_line_47 | NAYY 4x150 SE | 44 | 45 | 0.026019 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1503-11_0_3_line_48 | NAYY 4x150 SE | 44 | 46 | 0.003966 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1503-11_0_3_line_49 | NAYY 4x150 SE | 45 | 47 | 0.061323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1503-11_0_3_line_50 | NAYY 4x150 SE | 46 | 48 | 0.0092752 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1503-11_0_3_line_51 | NAYY 4x150 SE | 46 | 49 | 0.012568 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1503-11_0_3_line_52 | NAYY 4x150 SE | 49 | 50 | 0.019962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1503-11_0_3_line_53 | NAYY 4x150 SE | 50 | 52 | 0.022774 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1503-11_0_3_line_54 | NAYY 4x150 SE | 50 | 53 | 0.015099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1503-11_0_3_line_55 | NAYY 4x150 SE | 51 | 56 | 0.012995 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1503-11_0_3_line_56 | NAYY 4x150 SE | 51 | 54 | 0.03593 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1503-11_0_3_line_57 | NAYY 4x150 SE | 53 | 65 | 0.032864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1503-11_0_3_line_58 | NAYY 4x150 SE | 54 | 55 | 0.011209 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1503-11_0_3_line_59 | NAYY 4x150 SE | 55 | 57 | 0.079569 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1503-11_0_3_line_60 | NAYY 4x150 SE | 55 | 58 | 0.045585 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1503-11_0_3_line_61 | NAYY 4x150 SE | 56 | 59 | 0.0047838 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1503-11_0_3_line_62 | NAYY 4x150 SE | 60 | 61 | 0.015928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1503-11_0_3_line_63 | NAYY 4x150 SE | 61 | 62 | 0.037486 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1503-11_0_3_line_64 | NAYY 4x150 SE | 61 | 63 | 0.055224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1503-11_0_3_line_65 | NAYY 4x150 SE | 63 | 64 | 0.0027786 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1503-11_0_3_line_66 | NAYY 4x150 SE | 64 | 90 | 0.01283 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1503-11_0_3_line_67 | NAYY 4x150 SE | 66 | 67 | 0.10122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1503-11_0_3_line_68 | NAYY 4x150 SE | 66 | 68 | 0.13465 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1503-11_0_3_line_69 | NAYY 4x150 SE | 67 | 69 | 0.04328 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1503-11_0_3_line_70 | NAYY 4x150 SE | 67 | 70 | 0.11999 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1503-11_0_3_line_71 | NAYY 4x150 SE | 67 | 71 | 0.19582 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1503-11_0_3_line_72 | NAYY 4x150 SE | 68 | 72 | 0.016139 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1503-11_0_3_line_73 | NAYY 4x150 SE | 69 | 73 | 0.11379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1503-11_0_3_line_74 | NAYY 4x150 SE | 70 | 74 | 0.011278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1503-11_0_3_line_75 | NAYY 4x150 SE | 71 | 77 | 0.0090666 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1503-11_0_3_line_76 | NAYY 4x150 SE | 71 | 75 | 0.047438 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1503-11_0_3_line_77 | NAYY 4x150 SE | 73 | 86 | 0.078392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1503-11_0_3_line_78 | NAYY 4x150 SE | 73 | 87 | 0.14574 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1503-11_0_3_line_79 | NAYY 4x150 SE | 74 | 82 | 0.0511 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1503-11_0_3_line_80 | NAYY 4x150 SE | 75 | 76 | 0.098123 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1503-11_0_3_line_81 | NAYY 4x150 SE | 76 | 78 | 0.041602 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1503-11_0_3_line_82 | NAYY 4x150 SE | 78 | 79 | 0.0066539 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1503-11_0_3_line_83 | NAYY 4x150 SE | 79 | 80 | 0.0094724 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1503-11_0_3_line_84 | NAYY 4x150 SE | 80 | 81 | 0.016908 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1503-11_0_3_line_85 | NAYY 4x150 SE | 81 | 95 | 0.013037 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1503-11_0_3_line_86 | NAYY 4x150 SE | 82 | 83 | 0.036784 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1503-11_0_3_line_87 | NAYY 4x150 SE | 83 | 84 | 0.033297 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1503-11_0_3_line_88 | NAYY 4x150 SE | 84 | 85 | 0.15412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1503-11_0_3_line_89 | NAYY 4x150 SE | 85 | 88 | 0.022647 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1503-11_0_3_line_90 | NAYY 4x150 SE | 85 | 89 | 0.13162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1503-11_0_3_line_91 | NAYY 4x150 SE | 86 | 97 | 0.15155 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1503-11_0_3_line_92 | NAYY 4x150 SE | 87 | 105 | 0.074231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1503-11_0_3_line_93 | NAYY 4x150 SE | 89 | 104 | 0.11017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1503-11_0_3_line_94 | NAYY 4x150 SE | 90 | 91 | 0.16695 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1503-11_0_3_line_95 | NAYY 4x150 SE | 91 | 92 | 0.12904 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1503-11_0_3_line_96 | NAYY 4x150 SE | 91 | 96 | 0.12393 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1503-11_0_3_line_97 | NAYY 4x150 SE | 92 | 93 | 0.012847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1503-11_0_3_line_98 | NAYY 4x150 SE | 93 | 94 | 0.095116 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1503-11_0_3_line_99 | NAYY 4x150 SE | 95 | 96 | 0.045235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1503-11_0_3_line_100 | NAYY 4x150 SE | 97 | 98 | 0.00088406 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1503-11_0_3_line_101 | NAYY 4x150 SE | 98 | 99 | 0.30696 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1503-11_0_3_line_102 | NAYY 4x150 SE | 100 | 101 | 0.027583 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1503-11_0_3_line_103 | NAYY 4x150 SE | 101 | 107 | 0.07978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1503-11_0_3_line_104 | NAYY 4x150 SE | 102 | 103 | 0.012894 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1503-11_0_3_line_105 | NAYY 4x150 SE | 104 | 110 | 0.013633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1503-11_0_3_line_106 | NAYY 4x150 SE | 104 | 111 | 0.064205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1503-11_0_3_line_107 | NAYY 4x150 SE | 106 | 107 | 0.055078 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1503-11_0_3_line_108 | NAYY 4x150 SE | 107 | 108 | 0.09652 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1503-11_0_3_line_109 | NAYY 4x150 SE | 108 | 109 | 0.1165 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1503-11_0_3_line_110 | NAYY 4x150 SE | 109 | 112 | 0.052495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_1503-11_0_3_line_111 | NAYY 4x150 SE | 111 | 112 | 0.011198 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1503-11_0_3_trafo_47 | 0.25 MVA 20/0.4 kV | 113 | 38 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2672572.3515 | 1197197.5778 | 2672579.1372 | 1197192.925
1 | 2672572.3515 | 1197197.5778 | 2672536.085 | 1197210.1789
2 | 2672608.7746 | 1197205.3357 | 2672572.3515 | 1197197.5778
3 | 2672536.085 | 1197210.1789 | 2672527.7321 | 1197233.0523
4 | 2672536.085 | 1197210.1789 | 2672542.0767 | 1197195.9985 | 2672555.8835 | 1197173.5228
5 | 2672525.2877 | 1197239.7458 | 2672527.7321 | 1197233.0523
6 | 2672525.2877 | 1197239.7458 | 2672521.134 | 1197251.1203
7 | 2672508.6565 | 1197280.8503 | 2672518.5463 | 1197258.2063 | 2672521.134 | 1197251.1203
8 | 2672460.8919 | 1197436.6266 | 2672460.8919 | 1197436.6266 | 2672466.1539 | 1197430.4533 | 2672469.8574 | 1197424.0387 | 2672471.675 | 1197418.3712
9 | 2672460.8919 | 1197436.6266 | 2672456.6816 | 1197438.598
10 | 2672471.675 | 1197418.3712 | 2672472.3417 | 1197416.2923
11 | 2672451.3445 | 1197487.7975 | 2672452.6891 | 1197481.8101 | 2672453.8371 | 1197473.8192 | 2672453.8239 | 1197468.627 | 2672445.1627 | 1197448.5766 | 2672446.7967 | 1197443.2265 | 2672456.6816 | 1197438.598
12 | 2672475.3361 | 1197404.2616 | 2672473.6968 | 1197412.0669 | 2672472.3417 | 1197416.2923
13 | 2672451.3445 | 1197487.7975 | 2672434.1227 | 1197558.8208
14 | 2672451.3445 | 1197487.7975 | 2672431.1781 | 1197478.5249
15 | 2672475.3361 | 1197404.2616 | 2672479.7517 | 1197383.237
16 | 2672434.1227 | 1197558.8208 | 2672377.1876 | 1197532.9714 | 2672363.8776 | 1197525.6207
17 | 2672423.8942 | 1197472.5811 | 2672428.5219 | 1197477.3036 | 2672431.1781 | 1197478.5249
18 | 2672479.7517 | 1197383.237 | 2672485.8794 | 1197354.06
19 | 2672342.5265 | 1197513.8293 | 2672342.5265 | 1197513.8293 | 2672363.8776 | 1197525.6207
20 | 2672418.2779 | 1197464.0382 | 2672422.6232 | 1197471.2841 | 2672423.8942 | 1197472.5811
21 | 2672503.4956 | 1197292.6669 | 2672495.0268 | 1197318.9246 | 2672488.959 | 1197339.3968 | 2672485.8794 | 1197354.06
22 | 2672342.5265 | 1197513.8293 | 2672335.4536 | 1197511.6758 | 2672317.1798 | 1197507.3411 | 2672309.1196 | 1197506.2447
23 | 2672412.0062 | 1197427.8181 | 2672418.2779 | 1197464.0382
24 | 2672418.2779 | 1197464.0382 | 2672410.4923 | 1197466.0118 | 2672403.5206 | 1197466.3667
25 | 2672398.3808 | 1197466.6284 | 2672403.5206 | 1197466.3667
26 | 2672398.3808 | 1197466.6284 | 2672373.9815 | 1197467.8706
27 | 2672373.9055 | 1197467.8745 | 2672373.9815 | 1197467.8706
28 | 2672369.49 | 1197468.0993 | 2672373.9055 | 1197467.8745
29 | 2672412.0062 | 1197427.8181 | 2672417.5239 | 1197417.512 | 2672411.5525 | 1197390.4456 | 2672403.3854 | 1197374.8595 | 2672399.6969 | 1197370.1489
30 | 2672412.0062 | 1197427.8181 | 2672381.2907 | 1197418.9091
31 | 2672369.49 | 1197468.0993 | 2672345.2079 | 1197469.3356
32 | 2672393.199 | 1197361.8505 | 2672399.6969 | 1197370.1489
33 | 2672380.0053 | 1197418.5362 | 2672381.2907 | 1197418.9091
34 | 2672331.3949 | 1197470.0388 | 2672345.2079 | 1197469.3356
35 | 2672325.2824 | 1197470.35 | 2672331.3949 | 1197470.0388
36 | 2672291.88 | 1197503.8998 | 2672309.1196 | 1197506.2447
37 | 2672279.7806 | 1197503.5867 | 2672291.88 | 1197503.8998
38 | 2672279.7806 | 1197503.5867 | 2672273.3418 | 1197504.4205 | 2672268.3429 | 1197507.1284
39 | 2672279.7806 | 1197503.5867 | 2672284.9739 | 1197494.8887 | 2672292.9682 | 1197478.1641
40 | 2672268.3429 | 1197507.1284 | 2672266.7589 | 1197499.538 | 2672271.7755 | 1197474.1973
41 | 2672260.8367 | 1197513.7195 | 2672267.0241 | 1197507.8462 | 2672268.3429 | 1197507.1284
42 | 2672295.6956 | 1197467.4127 | 2672292.9682 | 1197478.1641
43 | 2672271.7755 | 1197474.1973 | 2672272.4457 | 1197470.8116 | 2672272.0785 | 1197444.346
44 | 2672245.89 | 1197506.3567 | 2672260.8367 | 1197513.7195
45 | 2672260.8367 | 1197513.7195 | 2672258.9497 | 1197517.9659 | 2672255.7277 | 1197531.2017 | 2672244.3911 | 1197573.0769
46 | 2672243.936 | 1197584.2024 | 2672253.7736 | 1197593.9271 | 2672261.3739 | 1197605.0254
47 | 2672243.936 | 1197584.2024 | 2672240.7234 | 1197590.3673 | 2672238.6694 | 1197595.8347 | 2672235.5499 | 1197608.6886
48 | 2672243.936 | 1197584.2024 | 2672240.8897 | 1197581.6529
49 | 2672214.1559 | 1197666.1262 | 2672221.552 | 1197644.5797 | 2672231.3359 | 1197620.2942 | 2672235.1263 | 1197610.4341 | 2672235.5499 | 1197608.6886
50 | 2672240.8897 | 1197581.6529 | 2672244.0396 | 1197574.3755 | 2672244.3911 | 1197573.0769
51 | 2672240.8897 | 1197581.6529 | 2672234.1136 | 1197577.6353 | 2672229.7486 | 1197575.9191
52 | 2672210.7065 | 1197570.1259 | 2672220.8396 | 1197572.4163 | 2672229.7486 | 1197575.9191
53 | 2672210.7065 | 1197570.1259 | 2672219.0916 | 1197560.1211 | 2672225.2924 | 1197552.636
54 | 2672195.9398 | 1197566.7789 | 2672210.7065 | 1197570.1259
55 | 2672245.89 | 1197506.3567 | 2672244.3093 | 1197503.5359 | 2672244.8825 | 1197493.7909
56 | 2672245.89 | 1197506.3567 | 2672238.8044 | 1197506.5156 | 2672210.379 | 1197501.6271
57 | 2672195.9398 | 1197566.7789 | 2672190.7101 | 1197591.7531 | 2672188.0945 | 1197598.6194
58 | 2672199.8921 | 1197498.1184 | 2672204.455 | 1197500.6084 | 2672210.379 | 1197501.6271
59 | 2672199.8921 | 1197498.1184 | 2672191.3762 | 1197497.5042 | 2672172.1483 | 1197496.4826 | 2672156.1811 | 1197492.2429 | 2672121.3288 | 1197486.9287
60 | 2672177.88 | 1197458.9513 | 2672181.4089 | 1197470.7455 | 2672196.2545 | 1197495.3284 | 2672199.8921 | 1197498.1184
61 | 2672244.8825 | 1197493.7909 | 2672245.1634 | 1197489.0154
62 | 2672242.0592 | 1197435.1006 | 2672244.6146 | 1197450.8225
63 | 2672242.0592 | 1197435.1006 | 2672266.1539 | 1197434.2912 | 2672270.823 | 1197436.1932 | 2672272.0184 | 1197440.01 | 2672272.0785 | 1197444.346
64 | 2672242.0592 | 1197435.1006 | 2672240.3652 | 1197424.6405 | 2672239.1098 | 1197380.031
65 | 2672239.0316 | 1197377.2534 | 2672239.1098 | 1197380.031
66 | 2672239.0316 | 1197377.2534 | 2672238.6707 | 1197364.4281
67 | 2671828.5422 | 1197459.1123 | 2671851.7209 | 1197462.2482 | 2671862.9332 | 1197465.407 | 2671890.56 | 1197488.8199 | 2671902.1518 | 1197496.5083 | 2671917.6766 | 1197501.4424
68 | 2671917.6766 | 1197501.4424 | 2671915.6492 | 1197507.8886 | 2671916.8946 | 1197511.9949 | 2671930.3477 | 1197527.0436 | 2671943.8813 | 1197535.4003 | 2671968.8453 | 1197546.4851 | 2671975.9241 | 1197551.3177 | 2671980.5905 | 1197559.1341 | 2671982.5637 | 1197574.9119 | 2671988.0982 | 1197582.7388 | 2672001.1861 | 1197593.6402
69 | 2671828.5422 | 1197459.1123 | 2671785.356 | 1197456.2588
70 | 2671828.5422 | 1197459.1123 | 2671831.1889 | 1197466.4152 | 2671844.003 | 1197480.1552 | 2671847.3645 | 1197488.823 | 2671849.44 | 1197513.8631 | 2671854.4991 | 1197525.1418 | 2671866.1672 | 1197547.3954 | 2671873.5024 | 1197567.6296
71 | 2671828.5422 | 1197459.1123 | 2671824.1003 | 1197263.3408
72 | 2672013.5871 | 1197603.9696 | 2672001.1861 | 1197593.6402
73 | 2671682.4041 | 1197413.9873 | 2671751.4286 | 1197454.017 | 2671785.356 | 1197456.2588
74 | 2671876.4242 | 1197578.5138 | 2671874.1661 | 1197569.4604 | 2671873.5024 | 1197567.6296
75 | 2671815.3422 | 1197261.9348 | 2671818.547 | 1197263.3741 | 2671824.1003 | 1197263.3408
76 | 2671869.9551 | 1197251.1879 | 2671867.5199 | 1197251.7998 | 2671824.1003 | 1197263.3408
77 | 2671682.4041 | 1197413.9873 | 2671638.8237 | 1197348.8259
78 | 2671717.2716 | 1197541.8381 | 2671723.5397 | 1197516.498 | 2671723.7707 | 1197509.9412 | 2671721.5569 | 1197503.3662 | 2671689.9953 | 1197468.2111 | 2671681.1589 | 1197452.3956 | 2671678.7229 | 1197438.9361 | 2671677.4334 | 1197418.7973 | 2671682.4041 | 1197413.9873
79 | 2671876.4242 | 1197578.5138 | 2671877.5232 | 1197582.92 | 2671875.0914 | 1197594.4867 | 2671872.2614 | 1197613.2084 | 2671873.0189 | 1197628.9956
80 | 2671869.9551 | 1197251.1879 | 2671926.717 | 1197236.9247 | 2671936.0519 | 1197232.8123 | 2671943.7984 | 1197225.8679 | 2671949.4462 | 1197217.9866 | 2671952.9503 | 1197209.3754
81 | 2671970.1711 | 1197172.5752 | 2671961.9926 | 1197181.2265 | 2671957.9597 | 1197189.7276 | 2671953.3945 | 1197208.2838 | 2671952.9503 | 1197209.3754
82 | 2671975.8571 | 1197169.1193 | 2671970.1711 | 1197172.5752 | 2671970.1711 | 1197172.5752
83 | 2671975.8571 | 1197169.1193 | 2671975.8571 | 1197169.1193 | 2671985.0701 | 1197166.9178 | 2671985.0701 | 1197166.9178
84 | 2671985.0701 | 1197166.9178 | 2672001.9727 | 1197166.4986
85 | 2672014.4423 | 1197169.8043 | 2672004.6829 | 1197166.4313 | 2672001.9727 | 1197166.4986
86 | 2671873.0189 | 1197628.9956 | 2671874.3382 | 1197656.4929 | 2671877.9362 | 1197663.218 | 2671878.9803 | 1197664.4672
87 | 2671900.3344 | 1197690.0145 | 2671878.9803 | 1197664.4672
88 | 2671900.3344 | 1197690.0145 | 2671800.0848 | 1197807.0796
89 | 2671800.0848 | 1197807.0796 | 2671803.0386 | 1197814.3429 | 2671807.4413 | 1197828.4797
90 | 2671672.0751 | 1197837.6922 | 2671800.0848 | 1197807.0796
91 | 2671638.8237 | 1197348.8259 | 2671638.8237 | 1197348.8259 | 2671609.3708 | 1197360.0799 | 2671584.9166 | 1197363.5448 | 2671526.1895 | 1197354.6035 | 2671493.2799 | 1197340.2123
92 | 2671717.2716 | 1197541.8381 | 2671720.4966 | 1197546.0237 | 2671722.7087 | 1197560.3589 | 2671730.3268 | 1197588.8119 | 2671731.5822 | 1197598.4439 | 2671731.7899 | 1197613.7158
93 | 2671571.4976 | 1197792.7211 | 2671672.0751 | 1197837.6922
94 | 2672238.6707 | 1197364.4281 | 2672167.1319 | 1197213.5844
95 | 2672167.1319 | 1197213.5844 | 2672231.7434 | 1197101.8852
96 | 2672055.9397 | 1197158.8663 | 2672167.1319 | 1197213.5844
97 | 2672234.0237 | 1197090.2841 | 2672235.3959 | 1197093.3469 | 2672234.9823 | 1197096.6884 | 2672231.7434 | 1197101.8852
98 | 2672234.0237 | 1197090.2841 | 2672234.0237 | 1197090.2841 | 2672227.4715 | 1197087.859 | 2672226.0823 | 1197086.2079 | 2672226.5021 | 1197080.4651 | 2672228.2846 | 1197069.1131 | 2672230.1505 | 1197050.8579 | 2672229.2888 | 1197044.6326 | 2672226.4858 | 1197042.7198 | 2672223.5332 | 1197043.7404 | 2672220.7826 | 1197047.5761 | 2672214.1238 | 1197063.4386 | 2672209.1148 | 1197069.4707 | 2672205.3353 | 1197070.837 | 2672201.5495 | 1197070.9106
99 | 2672055.9397 | 1197158.8663 | 2672043.241 | 1197167.1294 | 2672030.018 | 1197172.1287 | 2672020.8481 | 1197172.0182 | 2672014.4423 | 1197169.8043
100 | 2671492.4699 | 1197339.8581 | 2671493.2799 | 1197340.2123
101 | 2671492.4699 | 1197339.8581 | 2671391.4101 | 1197050.0096
102 | 2671545.4525 | 1197489.5598 | 2671546.1695 | 1197483.7426 | 2671551.3868 | 1197481.8594 | 2671556.7759 | 1197483.436 | 2671560.1718 | 1197493.4354
103 | 2671590.1564 | 1197566.4745 | 2671587.1734 | 1197559.8792 | 2671577.0665 | 1197523.5808 | 2671571.1848 | 1197509.0683 | 2671560.749 | 1197495.135 | 2671560.1718 | 1197493.4354
104 | 2672503.4956 | 1197292.6669 | 2672508.6565 | 1197280.8503
105 | 2671571.4976 | 1197792.7211 | 2671563.7348 | 1197781.5136
106 | 2671571.4976 | 1197792.7211 | 2671571.4976 | 1197792.7211 | 2671560.9044 | 1197800.877 | 2671555.9294 | 1197802.9076 | 2671551.0042 | 1197800.1359 | 2671545.0973 | 1197789.0252 | 2671542.5056 | 1197787.9268 | 2671533.9827 | 1197786.6575 | 2671531.4771 | 1197786.0049 | 2671528.2598 | 1197784.3543 | 2671522.1727 | 1197776.9424
107 | 2671590.1564 | 1197566.4745 | 2671594.4327 | 1197566.837 | 2671597.9293 | 1197568.7022 | 2671602.149 | 1197573.7891 | 2671611.6349 | 1197585.6209 | 2671617.5504 | 1197589.6609 | 2671628.3518 | 1197594.671 | 2671634.3189 | 1197595.0427
108 | 2671594.4264 | 1197660.8381 | 2671594.3994 | 1197655.4567 | 2671592.4192 | 1197648.451 | 2671590.5073 | 1197638.9224 | 2671590.637 | 1197628.0952 | 2671593.3803 | 1197616.5433 | 2671595.0225 | 1197607.2573 | 2671594.9922 | 1197596.4282 | 2671590.5903 | 1197581.1218 | 2671588.4294 | 1197570.1227 | 2671590.1564 | 1197566.4745
109 | 2671594.4264 | 1197660.8381 | 2671495.1451 | 1197721.7983
110 | 2671513.7976 | 1197769.5835 | 2671510.4609 | 1197763.2731 | 2671499.8464 | 1197741.3775 | 2671494.4811 | 1197732.0966 | 2671494.8184 | 1197726.186 | 2671495.1451 | 1197721.7983
111 | 2671513.7976 | 1197769.5835 | 2671520.3848 | 1197774.7654 | 2671522.1727 | 1197776.9424

## bus_geodata
| x | y | coords
0 | 2672579.1372 | 1197192.925
1 | 2672572.3515 | 1197197.5778
2 | 2672536.085 | 1197210.1789
3 | 2672608.7746 | 1197205.3357
4 | 2672527.7321 | 1197233.0523
5 | 2672555.8835 | 1197173.5228
6 | 2672525.2877 | 1197239.7458
7 | 2672521.134 | 1197251.1203
8 | 2672460.8919 | 1197436.6266
9 | 2672471.675 | 1197418.3712
10 | 2672456.6816 | 1197438.598
11 | 2672472.3417 | 1197416.2923
12 | 2672451.3445 | 1197487.7975
13 | 2672475.3361 | 1197404.2616
14 | 2672434.1227 | 1197558.8208
15 | 2672431.1781 | 1197478.5249
16 | 2672479.7517 | 1197383.237
17 | 2672363.8776 | 1197525.6207
18 | 2672423.8942 | 1197472.5811
19 | 2672485.8794 | 1197354.06
20 | 2672342.5265 | 1197513.8293
21 | 2672418.2779 | 1197464.0382
22 | 2672398.3808 | 1197466.6284
23 | 2672403.5206 | 1197466.3667
24 | 2672373.9815 | 1197467.8706
25 | 2672373.9056 | 1197467.8745
26 | 2672412.0062 | 1197427.8181
27 | 2672369.49 | 1197468.0993
28 | 2672399.6969 | 1197370.1489
29 | 2672381.2907 | 1197418.9091
30 | 2672345.2079 | 1197469.3356
31 | 2672393.199 | 1197361.8505
32 | 2672380.0053 | 1197418.5362
33 | 2672331.3949 | 1197470.0388
34 | 2672309.1196 | 1197506.2447
35 | 2672291.88 | 1197503.8998
36 | 2672279.7806 | 1197503.5867
37 | 2672268.3429 | 1197507.1284
38 | 2672292.9682 | 1197478.1641
39 | 2672271.7755 | 1197474.1973
40 | 2672260.8367 | 1197513.7195
41 | 2672295.6956 | 1197467.4127
42 | 2672325.2824 | 1197470.35
43 | 2672261.3739 | 1197605.0254
44 | 2672243.936 | 1197584.2024
45 | 2672235.5499 | 1197608.6886
46 | 2672240.8897 | 1197581.6529
47 | 2672214.1559 | 1197666.1262
48 | 2672244.3911 | 1197573.0769
49 | 2672229.7486 | 1197575.9191
50 | 2672210.7065 | 1197570.1259
51 | 2672245.89 | 1197506.3567
52 | 2672225.2924 | 1197552.636
53 | 2672195.9398 | 1197566.7789
54 | 2672210.379 | 1197501.6271
55 | 2672199.8921 | 1197498.1184
56 | 2672244.8825 | 1197493.7909
57 | 2672121.3288 | 1197486.9287
58 | 2672177.88 | 1197458.9513
59 | 2672245.1634 | 1197489.0154
60 | 2672244.6146 | 1197450.8225
61 | 2672242.0592 | 1197435.1006
62 | 2672272.0785 | 1197444.346
63 | 2672239.1098 | 1197380.031
64 | 2672239.0316 | 1197377.2534
65 | 2672188.0945 | 1197598.6194
66 | 2671917.6766 | 1197501.4424
67 | 2671828.5422 | 1197459.1123
68 | 2672001.1861 | 1197593.6402
69 | 2671785.356 | 1197456.2588
70 | 2671873.5024 | 1197567.6296
71 | 2671824.1003 | 1197263.3408
72 | 2672013.5871 | 1197603.9696
73 | 2671682.4041 | 1197413.9873
74 | 2671876.4242 | 1197578.5138
75 | 2671869.9551 | 1197251.1879
76 | 2671952.9503 | 1197209.3754
77 | 2671815.3422 | 1197261.9348
78 | 2671970.1711 | 1197172.5752
79 | 2671975.8571 | 1197169.1193
80 | 2671985.0701 | 1197166.9178
81 | 2672001.9727 | 1197166.4986
82 | 2671873.0189 | 1197628.9956
83 | 2671878.9803 | 1197664.4672
84 | 2671900.3344 | 1197690.0145
85 | 2671800.0848 | 1197807.0796
86 | 2671638.8237 | 1197348.8259
87 | 2671717.2716 | 1197541.8381
88 | 2671807.4413 | 1197828.4797
89 | 2671672.0751 | 1197837.6922
90 | 2672238.6707 | 1197364.4281
91 | 2672167.1319 | 1197213.5844
92 | 2672231.7434 | 1197101.8852
93 | 2672234.0237 | 1197090.2841
94 | 2672201.5495 | 1197070.9106
95 | 2672014.4423 | 1197169.8043
96 | 2672055.9397 | 1197158.8663
97 | 2671493.2799 | 1197340.2123
98 | 2671492.4699 | 1197339.8581
99 | 2671391.4101 | 1197050.0096
100 | 2671545.4525 | 1197489.5598
101 | 2671560.1718 | 1197493.4354
102 | 2672508.6565 | 1197280.8503
103 | 2672503.4956 | 1197292.6669
104 | 2671571.4976 | 1197792.7211
105 | 2671731.7899 | 1197613.7158
106 | 2671634.3189 | 1197595.0427
107 | 2671590.1564 | 1197566.4745
108 | 2671594.4264 | 1197660.8381
109 | 2671495.1451 | 1197721.7983
110 | 2671563.7348 | 1197781.5136
111 | 2671522.1727 | 1197776.9424
112 | 2671513.7976 | 1197769.5835
113 | 2672295.6956 | 1197467.4127

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97063 | -0.2065 | 0.00041947 | 0.00010513
1 | 0.97064 | -0.20647 | 0 | 0
2 | 0.97069 | -0.20608 | 0 | 0
3 | 0.97061 | -0.20668 | 0.00053029 | 0.0001329
4 | 0.97073 | -0.20577 | 0.00044592 | 0.00011176
5 | 0.97068 | -0.20618 | 0.00022448 | 5.626e-05
6 | 0.97075 | -0.20565 | 0.00043244 | 0.00010838
7 | 0.97079 | -0.20539 | 0.00093916 | 0.00023537
8 | 0.97268 | -0.19171 | 0.0058459 | 0.0014651
9 | 0.97223 | -0.19497 | 0.0010973 | 0.000275
10 | 0.97282 | -0.19072 | 0.0014347 | 0.00035958
11 | 0.97218 | -0.19527 | 0.0014929 | 0.00037417
12 | 0.97465 | -0.17756 | 0 | 0
13 | 0.97197 | -0.19682 | 0.0021274 | 0.00053317
14 | 0.98125 | -0.13054 | 0 | 0
15 | 0.97334 | -0.1869 | 0.0032032 | 0.0008028
16 | 0.97167 | -0.199 | 0.0022699 | 0.00056889
17 | 0.98827 | -0.081221 | 0.0049677 | 0.001245
18 | 0.97283 | -0.1906 | 0.0026373 | 0.00066098
19 | 0.97135 | -0.20133 | 0.0036378 | 0.00091173
20 | 0.99065 | -0.064655 | 0.0041637 | 0.0010435
21 | 0.97232 | -0.1943 | 0 | 0
22 | 0.9716 | -0.19945 | 0.0038751 | 0.0009712
23 | 0.97177 | -0.19822 | 0.0020263 | 0.00050783
24 | 0.97092 | -0.20432 | 0.0019079 | 0.00047816
25 | 0.97092 | -0.20433 | 0.0019086 | 0.00047835
26 | 0.97181 | -0.19796 | 0 | 0
27 | 0.97083 | -0.20503 | 0.0045569 | 0.0011421
28 | 0.97148 | -0.20029 | 0.0006723 | 0.0001685
29 | 0.97153 | -0.19996 | 0.002663 | 0.00066741
30 | 0.97045 | -0.20772 | 0.0037112 | 0.00093011
31 | 0.97144 | -0.20061 | 0.0028287 | 0.00070894
32 | 0.97152 | -0.2 | 0.0032491 | 0.00081429
33 | 0.97032 | -0.20871 | 0.0018101 | 0.00045365
34 | 0.9942 | -0.040043 | 0.0021476 | 0.00053823
35 | 0.99606 | -0.027253 | 0 | 0
36 | 0.9967 | -0.022828 | 0 | 0
37 | 0.9952 | -0.033351 | 0 | 0
38 | 1 | 0 | -0.16492 | -0.041445
39 | 0.99405 | -0.041509 | 0.0013599 | 0.00034083
40 | 0.99431 | -0.039617 | 0 | 0
41 | 0.99996 | -0.00030272 | 0.0027339 | 0.00068518
42 | 0.97027 | -0.20903 | 0.0049176 | 0.0012325
43 | 0.98861 | -0.079709 | 0.0074506 | 0.0018673
44 | 0.9889 | -0.077634 | 0 | 0
45 | 0.98865 | -0.079453 | 0.0041732 | 0.0010459
46 | 0.98899 | -0.077055 | 0 | 0
47 | 0.98841 | -0.081126 | 0.0026689 | 0.00066888
48 | 0.98958 | -0.072833 | 0.0084825 | 0.0021259
49 | 0.98844 | -0.080946 | 0.0068056 | 0.0017056
50 | 0.98776 | -0.085745 | 0 | 0
51 | 0.99409 | -0.04111 | 0 | 0
52 | 0.9872 | -0.089742 | 0.017148 | 0.0042978
53 | 0.98762 | -0.086728 | 0 | 0
54 | 0.99386 | -0.042781 | 0.0020341 | 0.0005098
55 | 0.99382 | -0.043072 | 0 | 0
56 | 0.99401 | -0.041674 | 0.0020314 | 0.00050913
57 | 0.99367 | -0.044132 | 0.0013152 | 0.00032962
58 | 0.99373 | -0.043643 | 0.0012388 | 0.00031047
59 | 0.994 | -0.041783 | 0.0022595 | 0.00056628
60 | 0.9919 | -0.056799 | 0.003344 | 0.00083808
61 | 0.99198 | -0.056258 | 0 | 0
62 | 0.99308 | -0.048379 | 0.0019637 | 0.00049215
63 | 0.99062 | -0.066015 | 0.0019778 | 0.00049568
64 | 0.99056 | -0.066451 | 0.0016707 | 0.00041871
65 | 0.98732 | -0.088869 | 0.0063631 | 0.0015947
66 | 0.98184 | -0.13031 | 0 | 0
67 | 0.9819 | -0.12988 | 0 | 0
68 | 0.98177 | -0.13088 | 0.00011059 | 2.7716e-05
69 | 0.98184 | -0.13034 | 7.063e-05 | 1.7702e-05
70 | 0.98136 | -0.13389 | 0.00015589 | 3.907e-05
71 | 0.98318 | -0.12033 | 0.00033866 | 8.4877e-05
72 | 0.98176 | -0.13093 | 0.00028974 | 7.2615e-05
73 | 0.9817 | -0.13148 | 0 | 0
74 | 0.98131 | -0.13425 | 0.00011364 | 2.8482e-05
75 | 0.98352 | -0.11778 | 9.9467e-05 | 2.4929e-05
76 | 0.98424 | -0.1124 | 0.00030722 | 7.6995e-05
77 | 0.98317 | -0.12034 | 0.00014062 | 3.5243e-05
78 | 0.98456 | -0.10999 | 0.00093169 | 0.0002335
79 | 0.98462 | -0.10954 | 8.6633e-05 | 2.1712e-05
80 | 0.98471 | -0.10889 | 0.00043839 | 0.00010987
81 | 0.98488 | -0.10765 | 0.0010072 | 0.00025242
82 | 0.9811 | -0.13582 | 0.00095357 | 0.00023899
83 | 0.981 | -0.13658 | 0.00026019 | 6.521e-05
84 | 0.98092 | -0.13718 | 8.9258e-05 | 2.237e-05
85 | 0.98057 | -0.13979 | 0.00014772 | 3.7021e-05
86 | 0.98161 | -0.13212 | 0.00014654 | 3.6727e-05
87 | 0.98166 | -0.13173 | 0 | 0
88 | 0.98056 | -0.13983 | 0.00016577 | 4.1546e-05
89 | 0.98033 | -0.14158 | 0.00011578 | 2.9016e-05
90 | 0.99031 | -0.068245 | 0.0015695 | 0.00039336
91 | 0.98744 | -0.088975 | 0.00073091 | 0.00018318
92 | 0.98721 | -0.090663 | 0.00050288 | 0.00012603
93 | 0.98719 | -0.090764 | 0.00027395 | 6.8659e-05
94 | 0.98713 | -0.09124 | 0.00048411 | 0.00012133
95 | 0.98503 | -0.10657 | 0.0020286 | 0.0005084
96 | 0.98567 | -0.10186 | 0 | 0
97 | 0.98148 | -0.13311 | 8.7157e-05 | 2.1844e-05
98 | 0.98148 | -0.13311 | 0.00012743 | 3.1937e-05
99 | 0.98131 | -0.13436 | 0.00037796 | 9.4725e-05
100 | 0.97983 | -0.14535 | 0.0001776 | 4.451e-05
101 | 0.97984 | -0.1453 | 8.3083e-05 | 2.0823e-05
102 | 0.97093 | -0.20436 | 0.0007129 | 0.00017867
103 | 0.971 | -0.20385 | 0 | 0
104 | 0.98015 | -0.14293 | 0.00011516 | 2.8861e-05
105 | 0.98165 | -0.13184 | 0.00014922 | 3.7397e-05
106 | 0.97985 | -0.14522 | 0.00024615 | 6.1691e-05
107 | 0.97987 | -0.14507 | 0 | 0
108 | 0.97994 | -0.14455 | 0 | 0
109 | 0.98002 | -0.1439 | 0 | 0
110 | 0.98015 | -0.14295 | 0.00013993 | 3.507e-05
111 | 0.98007 | -0.14353 | 0.00036301 | 9.098e-05
112 | 0.98006 | -0.1436 | 0 | 0
113 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00041947 | -0.00010513 | 0.00041947 | 0.00010503 | 2.123e-09 | -1.0088e-07 | 0.00064307 | 0.00064303 | 0.00064307 | 0.97063 | -0.2065 | 0.97064 | -0.20647 | 0.23817
1 | -0.00094978 | -0.00023748 | 0.00094983 | 0.00023703 | 5.0641e-08 | -4.5388e-07 | 0.0014558 | 0.0014557 | 0.0014558 | 0.97064 | -0.20647 | 0.97069 | -0.20608 | 0.5392
2 | 0.00053031 | 0.00013245 | -0.00053029 | -0.0001329 | 1.5313e-08 | -4.5311e-07 | 0.00081281 | 0.00081298 | 0.00081298 | 0.97064 | -0.20647 | 0.97061 | -0.20668 | 0.3011
3 | -0.0011743 | -0.00029277 | 0.0011744 | 0.00029249 | 4.9207e-08 | -2.821e-07 | 0.0017996 | 0.0017995 | 0.0017996 | 0.97069 | -0.20608 | 0.97073 | -0.20577 | 0.66652
4 | 0.00022448 | 5.5745e-05 | -0.00022448 | -5.626e-05 | 3.085e-09 | -5.1517e-07 | 0.00034394 | 0.00034412 | 0.00034412 | 0.97069 | -0.20608 | 0.97068 | -0.20618 | 0.12745
5 | -0.0016203 | -0.00040425 | 0.0016203 | 0.00040417 | 2.7415e-08 | -7.7552e-08 | 0.002483 | 0.002483 | 0.002483 | 0.97073 | -0.20577 | 0.97075 | -0.20565 | 0.91964
6 | -0.0020527 | -0.00051255 | 0.0020528 | 0.00051243 | 7.4778e-08 | -1.2095e-07 | 0.0031459 | 0.0031458 | 0.0031459 | 0.97075 | -0.20565 | 0.97079 | -0.20539 | 1.1651
7 | -0.002992 | -0.0007478 | 0.0029924 | 0.00074757 | 4.2314e-07 | -2.3609e-07 | 0.0045853 | 0.0045852 | 0.0045853 | 0.97079 | -0.20539 | 0.97093 | -0.20436 | 1.6983
8 | 0.014347 | 0.0035934 | -0.014341 | -0.0035912 | 6.4535e-06 | 2.2157e-06 | 0.021947 | 0.021947 | 0.021947 | 0.97268 | -0.19171 | 0.97223 | -0.19497 | 8.1287
9 | -0.020193 | -0.0050586 | 0.020196 | 0.0050596 | 2.7682e-06 | 1.007e-06 | 0.030891 | 0.03089 | 0.030891 | 0.97268 | -0.19171 | 0.97282 | -0.19072 | 11.4409
10 | 0.013243 | 0.0033162 | -0.013243 | -0.003316 | 5.5964e-07 | 1.8817e-07 | 0.020268 | 0.020268 | 0.020268 | 0.97223 | -0.19497 | 0.97218 | -0.19527 | 7.5067
11 | -0.02163 | -0.0054191 | 0.02167 | 0.0054336 | 3.9447e-05 | 1.4453e-05 | 0.033085 | 0.033085 | 0.033085 | 0.97282 | -0.19072 | 0.97465 | -0.17756 | 12.2537
12 | 0.01175 | 0.0029419 | -0.011747 | -0.0029411 | 2.5049e-06 | 8.0953e-07 | 0.017983 | 0.017983 | 0.017983 | 0.97218 | -0.19527 | 0.97197 | -0.19682 | 6.6604
13 | -0.06177 | -0.015498 | 0.062175 | 0.015653 | 0.00040564 | 0.0001551 | 0.094311 | 0.094311 | 0.094311 | 0.97465 | -0.17756 | 0.98125 | -0.13054 | 34.9301
14 | 0.0401 | 0.010064 | -0.040048 | -0.010045 | 5.1921e-05 | 1.9693e-05 | 0.061226 | 0.061227 | 0.061227 | 0.97465 | -0.17756 | 0.97334 | -0.1869 | 22.6765
15 | 0.0096199 | 0.0024079 | -0.009617 | -0.002407 | 2.9072e-06 | 8.5195e-07 | 0.014726 | 0.014726 | 0.014726 | 0.97197 | -0.19682 | 0.97167 | -0.199 | 5.4542
16 | -0.062175 | -0.015653 | 0.062607 | 0.015818 | 0.00043143 | 0.00016495 | 0.094311 | 0.094311 | 0.094311 | 0.98125 | -0.13054 | 0.98827 | -0.081221 | 34.93
17 | 0.036845 | 0.0092418 | -0.036826 | -0.0092346 | 1.888e-05 | 7.1431e-06 | 0.05633 | 0.05633 | 0.05633 | 0.97334 | -0.1869 | 0.97283 | -0.1906 | 20.8628
18 | 0.007347 | 0.0018381 | -0.0073447 | -0.0018376 | 2.3546e-06 | 5.3646e-07 | 0.01125 | 0.01125 | 0.01125 | 0.97167 | -0.199 | 0.97135 | -0.20133 | 4.1668
19 | -0.067574 | -0.017063 | 0.067732 | 0.017123 | 0.0001577 | 6.0339e-05 | 0.10179 | 0.10179 | 0.10179 | 0.98827 | -0.081221 | 0.99065 | -0.064655 | 37.7001
20 | 0.034188 | 0.0085736 | -0.034171 | -0.008567 | 1.7517e-05 | 6.6101e-06 | 0.052296 | 0.052296 | 0.052296 | 0.97283 | -0.1906 | 0.97232 | -0.1943 | 19.3688
21 | 0.0037068 | 0.00092588 | -0.0037056 | -0.00092617 | 1.2858e-06 | -2.9645e-07 | 0.0056774 | 0.0056777 | 0.0056777 | 0.97135 | -0.20133 | 0.971 | -0.20385 | 2.1029
22 | -0.071896 | -0.018167 | 0.072146 | 0.018262 | 0.00024992 | 9.5678e-05 | 0.10804 | 0.10804 | 0.10804 | 0.99065 | -0.064655 | 0.9942 | -0.040043 | 40.0164
23 | 0.0094207 | 0.0023603 | -0.009416 | -0.0023589 | 4.7682e-06 | 1.3782e-06 | 0.014417 | 0.014417 | 0.014417 | 0.97232 | -0.1943 | 0.97181 | -0.19796 | 5.3397
24 | 0.02475 | 0.0062067 | -0.024737 | -0.0062017 | 1.3441e-05 | 4.9835e-06 | 0.037879 | 0.037879 | 0.037879 | 0.97232 | -0.1943 | 0.97177 | -0.19822 | 14.0292
25 | -0.022707 | -0.0056925 | 0.02271 | 0.0056939 | 3.8838e-06 | 1.43e-06 | 0.034776 | 0.034776 | 0.034776 | 0.9716 | -0.19945 | 0.97177 | -0.19822 | 12.88
26 | 0.018831 | 0.0047213 | -0.018819 | -0.0047167 | 1.2681e-05 | 4.5749e-06 | 0.028841 | 0.028841 | 0.028841 | 0.9716 | -0.19945 | 0.97092 | -0.20432 | 10.682
27 | 0.016911 | 0.0042386 | -0.016911 | -0.0042385 | 3.1873e-08 | 1.1319e-08 | 0.025917 | 0.025917 | 0.025917 | 0.97092 | -0.20432 | 0.97092 | -0.20433 | 9.599
28 | 0.015002 | 0.0037602 | -0.015001 | -0.0037597 | 1.4585e-06 | 5.0627e-07 | 0.022992 | 0.022992 | 0.022992 | 0.97092 | -0.20433 | 0.97083 | -0.20503 | 8.5157
29 | 0.0035022 | 0.000877 | -0.0035011 | -0.00087735 | 1.1302e-06 | -3.4545e-07 | 0.0053623 | 0.0053626 | 0.0053626 | 0.97181 | -0.19796 | 0.97148 | -0.20029 | 1.9861
30 | 0.0059137 | 0.0014819 | -0.0059121 | -0.0014817 | 1.6363e-06 | 2.332e-07 | 0.0090549 | 0.009055 | 0.009055 | 0.97181 | -0.19796 | 0.97153 | -0.19996 | 3.3537
31 | 0.010444 | 0.0026176 | -0.01044 | -0.0026164 | 3.8878e-06 | 1.1948e-06 | 0.016008 | 0.016008 | 0.016008 | 0.97083 | -0.20503 | 0.97045 | -0.20772 | 5.9289
32 | 0.0028288 | 0.00070885 | -0.0028287 | -0.00070894 | 1.2347e-07 | -8.3006e-08 | 0.0043328 | 0.0043329 | 0.0043329 | 0.97148 | -0.20029 | 0.97144 | -0.20061 | 1.6048
33 | 0.0032491 | 0.00081428 | -0.0032491 | -0.00081429 | 2.0682e-08 | -8.6183e-09 | 0.0049764 | 0.0049764 | 0.0049764 | 0.97153 | -0.19996 | 0.97152 | -0.2 | 1.8431
34 | 0.0067289 | 0.0016863 | -0.0067279 | -0.0016861 | 9.1872e-07 | 1.8249e-07 | 0.010317 | 0.010318 | 0.010318 | 0.97045 | -0.20772 | 0.97032 | -0.20871 | 3.8213
35 | 0.0049179 | 0.0012325 | -0.0049176 | -0.0012325 | 2.1722e-07 | 7.9516e-09 | 0.0075417 | 0.0075417 | 0.0075417 | 0.97032 | -0.20871 | 0.97027 | -0.20903 | 2.7932
36 | -0.074293 | -0.018801 | 0.074428 | 0.018852 | 0.00013439 | 5.1461e-05 | 0.11126 | 0.11126 | 0.11126 | 0.9942 | -0.040043 | 0.99606 | -0.027253 | 41.2068
37 | -0.074428 | -0.018852 | 0.074474 | 0.01887 | 4.6607e-05 | 1.7612e-05 | 0.11126 | 0.11126 | 0.11126 | 0.99606 | -0.027253 | 0.9967 | -0.022828 | 20.6034
38 | 0.086394 | 0.021692 | -0.086268 | -0.021644 | 0.00012612 | 4.8351e-05 | 0.129 | 0.129 | 0.129 | 0.9967 | -0.022828 | 0.9952 | -0.033351 | 47.776
39 | -0.16087 | -0.040562 | 0.16138 | 0.040759 | 0.00051628 | 0.00019782 | 0.24025 | 0.24025 | 0.24025 | 0.9967 | -0.022828 | 1 | 0 | 44.4913
40 | 0.023917 | 0.0059725 | -0.02389 | -0.0059627 | 2.679e-05 | 9.8678e-06 | 0.035753 | 0.035753 | 0.035753 | 0.9952 | -0.033351 | 0.99405 | -0.041509 | 13.2418
41 | 0.062351 | 0.015671 | -0.062297 | -0.01565 | 5.4344e-05 | 2.0771e-05 | 0.093243 | 0.093243 | 0.093243 | 0.9952 | -0.033351 | 0.99431 | -0.039617 | 34.5343
42 | 0.002734 | 0.00068508 | -0.0027339 | -0.00068518 | 1.1455e-07 | -1.0145e-07 | 0.0040682 | 0.0040683 | 0.0040683 | 1 | 0 | 0.99996 | -0.00030272 | 1.5068
43 | 0.02253 | 0.0056218 | -0.022509 | -0.0056141 | 2.1225e-05 | 7.7759e-06 | 0.033717 | 0.033717 | 0.033717 | 0.99405 | -0.041509 | 0.99308 | -0.048379 | 12.4879
44 | 0.0088827 | 0.002224 | -0.0088808 | -0.0022235 | 1.8328e-06 | 4.8935e-07 | 0.013292 | 0.013293 | 0.013293 | 0.99431 | -0.039617 | 0.99409 | -0.04111 | 4.9232
45 | 0.053414 | 0.013426 | -0.053168 | -0.013332 | 0.00024591 | 9.3783e-05 | 0.07995 | 0.07995 | 0.07995 | 0.99431 | -0.039617 | 0.98958 | -0.072833 | 29.6112
46 | -0.0074506 | -0.0018673 | 0.0074528 | 0.0018678 | 2.1411e-06 | 4.7356e-07 | 0.011214 | 0.011214 | 0.011214 | 0.98861 | -0.079709 | 0.9889 | -0.077634 | 4.1535
47 | 0.0068444 | 0.0017146 | -0.0068427 | -0.0017142 | 1.722e-06 | 3.2858e-07 | 0.010299 | 0.010299 | 0.010299 | 0.9889 | -0.077634 | 0.98865 | -0.079453 | 3.8143
48 | -0.014297 | -0.0035823 | 0.014298 | 0.0035827 | 1.1453e-06 | 3.8962e-07 | 0.021513 | 0.021513 | 0.021513 | 0.9889 | -0.077634 | 0.98899 | -0.077055 | 7.9677
49 | 0.0026695 | 0.00066833 | -0.0026689 | -0.00066888 | 6.1769e-07 | -5.4859e-07 | 0.0040176 | 0.0040179 | 0.0040179 | 0.98865 | -0.079453 | 0.98841 | -0.081126 | 1.4881
50 | -0.04466 | -0.011197 | 0.044686 | 0.011206 | 2.6133e-05 | 9.9321e-06 | 0.067195 | 0.067195 | 0.067195 | 0.98899 | -0.077055 | 0.98958 | -0.072833 | 24.8872
51 | 0.030361 | 0.0076138 | -0.030345 | -0.0076077 | 1.6366e-05 | 6.1335e-06 | 0.045683 | 0.045683 | 0.045683 | 0.98899 | -0.077055 | 0.98844 | -0.080946 | 16.9195
52 | 0.023539 | 0.0059021 | -0.023524 | -0.0058963 | 1.5643e-05 | 5.7607e-06 | 0.035437 | 0.035438 | 0.035438 | 0.98844 | -0.080946 | 0.98776 | -0.085745 | 13.125
53 | 0.017158 | 0.0043011 | -0.017148 | -0.0042978 | 9.4944e-06 | 3.3604e-06 | 0.025848 | 0.025848 | 0.025848 | 0.98776 | -0.085745 | 0.9872 | -0.089742 | 9.5733
54 | 0.0063658 | 0.0015952 | -0.006365 | -0.001595 | 8.6647e-07 | 1.4002e-07 | 0.0095898 | 0.0095899 | 0.0095899 | 0.98776 | -0.085745 | 0.98762 | -0.086728 | 3.5518
55 | 0.0042913 | 0.0010753 | -0.004291 | -0.0010754 | 3.3458e-07 | -3.9782e-08 | 0.0064234 | 0.0064234 | 0.0064234 | 0.99409 | -0.04111 | 0.99401 | -0.041674 | 2.3791
56 | 0.0045895 | 0.0011482 | -0.0045885 | -0.0011483 | 1.0579e-06 | -5.8814e-08 | 0.0068692 | 0.0068693 | 0.0068693 | 0.99409 | -0.04111 | 0.99386 | -0.042781 | 2.5442
57 | 0.006365 | 0.001595 | -0.0063631 | -0.0015947 | 1.8859e-06 | 3.0495e-07 | 0.0095899 | 0.00959 | 0.00959 | 0.98762 | -0.086728 | 0.98732 | -0.088869 | 3.5519
58 | 0.0025544 | 0.00063847 | -0.0025543 | -0.00063858 | 1.0227e-07 | -1.0591e-07 | 0.0038238 | 0.0038239 | 0.0038239 | 0.99386 | -0.042781 | 0.99382 | -0.043072 | 1.4163
59 | 0.0013154 | 0.00032866 | -0.0013152 | -0.00032962 | 1.9256e-07 | -9.568e-07 | 0.0019691 | 0.0019695 | 0.0019695 | 0.99382 | -0.043072 | 0.99367 | -0.044132 | 0.72945
60 | 0.0012389 | 0.00030992 | -0.0012388 | -0.00031047 | 9.7864e-08 | -5.5298e-07 | 0.0018547 | 0.0018549 | 0.0018549 | 0.99382 | -0.043072 | 0.99373 | -0.043643 | 0.68702
61 | 0.0022595 | 0.00056623 | -0.0022595 | -0.00056628 | 3.4152e-08 | -4.8874e-08 | 0.0033824 | 0.0033825 | 0.0033825 | 0.99401 | -0.041674 | 0.994 | -0.041783 | 1.2528
62 | -0.003344 | -0.00083808 | 0.0033442 | 0.00083797 | 2.5012e-07 | -1.0941e-07 | 0.0050165 | 0.0050164 | 0.0050165 | 0.9919 | -0.056799 | 0.99198 | -0.056258 | 1.858
63 | -0.020523 | -0.0051139 | 0.020545 | 0.0051219 | 2.2154e-05 | 8.0362e-06 | 0.030775 | 0.030775 | 0.030775 | 0.99198 | -0.056258 | 0.99308 | -0.048379 | 11.3982
64 | 0.017179 | 0.0042759 | -0.017156 | -0.0042678 | 2.2864e-05 | 8.0821e-06 | 0.025759 | 0.025759 | 0.025759 | 0.99198 | -0.056258 | 0.99062 | -0.066015 | 9.5403
65 | 0.015178 | 0.0037721 | -0.015177 | -0.0037718 | 9.0038e-07 | 3.1053e-07 | 0.022788 | 0.022788 | 0.022788 | 0.99062 | -0.066015 | 0.99056 | -0.066451 | 8.44
66 | 0.013507 | 0.0033531 | -0.013503 | -0.003352 | 3.2923e-06 | 1.1011e-06 | 0.020278 | 0.020278 | 0.020278 | 0.99056 | -0.066451 | 0.99031 | -0.068245 | 7.5105
67 | -0.00040036 | -9.8437e-05 | 0.00040038 | 9.7166e-05 | 2.3185e-08 | -1.2713e-06 | 0.00060608 | 0.00060564 | 0.00060608 | 0.98184 | -0.13031 | 0.9819 | -0.12988 | 0.22448
68 | 0.00040036 | 9.8437e-05 | -0.00040033 | -0.00010013 | 3.0895e-08 | -1.6909e-06 | 0.00060608 | 0.00060669 | 0.00060669 | 0.98184 | -0.13031 | 0.98177 | -0.13088 | 0.2247
69 | 0.00095932 | 0.00022892 | -0.00095927 | -0.00022944 | 5.6772e-08 | -5.2557e-07 | 0.0014498 | 0.00145 | 0.00145 | 0.9819 | -0.12988 | 0.98184 | -0.13034 | 0.53702
70 | 0.0031307 | 0.00077018 | -0.003129 | -0.00077105 | 1.6819e-06 | -8.6999e-07 | 0.0047393 | 0.0047398 | 0.0047398 | 0.9819 | -0.12988 | 0.98136 | -0.13389 | 1.7555
71 | -0.0044904 | -0.0010963 | 0.0044961 | 0.0010959 | 5.6406e-06 | -3.1064e-07 | 0.0067947 | 0.0067938 | 0.0067947 | 0.9819 | -0.12988 | 0.98318 | -0.12033 | 2.5165
72 | 0.00028974 | 7.2412e-05 | -0.00028974 | -7.2615e-05 | 1.9419e-09 | -2.0334e-07 | 0.00043907 | 0.00043915 | 0.00043915 | 0.98177 | -0.13088 | 0.98176 | -0.13093 | 0.16265
73 | 0.00088864 | 0.00021174 | -0.00088851 | -0.00021313 | 1.2811e-07 | -1.3897e-06 | 0.0013429 | 0.0013434 | 0.0013434 | 0.98184 | -0.13034 | 0.9817 | -0.13148 | 0.49756
74 | 0.0029731 | 0.00073198 | -0.002973 | -0.00073206 | 1.4273e-07 | -8.7593e-08 | 0.0045034 | 0.0045035 | 0.0045035 | 0.98136 | -0.13389 | 0.98131 | -0.13425 | 1.668
75 | 0.00014062 | 3.5129e-05 | -0.00014062 | -3.5243e-05 | 2.5622e-10 | -1.1488e-07 | 0.00021279 | 0.00021283 | 0.00021283 | 0.98318 | -0.12033 | 0.98317 | -0.12034 | 0.078826
76 | -0.0049753 | -0.001216 | 0.004977 | 0.001216 | 1.6735e-06 | 4.1871e-08 | 0.0075191 | 0.0075189 | 0.0075191 | 0.98318 | -0.12033 | 0.98352 | -0.11778 | 2.7849
77 | 0.00073928 | 0.00017851 | -0.00073922 | -0.00017948 | 6.1183e-08 | -9.6752e-07 | 0.0011182 | 0.0011185 | 0.0011185 | 0.9817 | -0.13148 | 0.98161 | -0.13212 | 0.41428
78 | 0.00014922 | 3.4619e-05 | -0.00014922 | -3.646e-05 | 4.6259e-09 | -1.8408e-06 | 0.00022523 | 0.00022586 | 0.00022586 | 0.9817 | -0.13148 | 0.98166 | -0.13173 | 0.08365
79 | 0.0028593 | 0.00070358 | -0.0028587 | -0.000704 | 5.9819e-07 | -4.1536e-07 | 0.0043312 | 0.0043314 | 0.0043314 | 0.98131 | -0.13425 | 0.9811 | -0.13582 | 1.6042
80 | -0.0050765 | -0.0012409 | 0.0050801 | 0.0012411 | 3.6013e-06 | 1.3898e-07 | 0.0076694 | 0.007669 | 0.0076694 | 0.98352 | -0.11778 | 0.98424 | -0.1124 | 2.8405
81 | -0.0053873 | -0.0013181 | 0.005389 | 0.0013182 | 1.7173e-06 | 1.316e-07 | 0.0081334 | 0.0081333 | 0.0081334 | 0.98424 | -0.1124 | 0.98456 | -0.10999 | 3.0124
82 | -0.0063207 | -0.0015517 | 0.0063211 | 0.0015518 | 3.7799e-07 | 6.0755e-08 | 0.0095413 | 0.0095413 | 0.0095413 | 0.98456 | -0.10999 | 0.98462 | -0.10954 | 3.5338
83 | -0.0064077 | -0.0015735 | 0.0064083 | 0.0015736 | 5.5296e-07 | 9.2189e-08 | 0.0096722 | 0.0096722 | 0.0096722 | 0.98462 | -0.10954 | 0.98471 | -0.10889 | 3.5823
84 | -0.0068467 | -0.0016834 | 0.0068478 | 0.0016836 | 1.1268e-06 | 2.1827e-07 | 0.010335 | 0.010335 | 0.010335 | 0.98471 | -0.10889 | 0.98488 | -0.10765 | 3.8276
85 | -0.0078549 | -0.0019361 | 0.0078561 | 0.0019363 | 1.1435e-06 | 2.739e-07 | 0.011856 | 0.011856 | 0.011856 | 0.98488 | -0.10765 | 0.98503 | -0.10657 | 4.3912
86 | 0.0019052 | 0.00046501 | -0.001905 | -0.0004654 | 1.9107e-07 | -3.9097e-07 | 0.0028851 | 0.0028853 | 0.0028853 | 0.9811 | -0.13582 | 0.981 | -0.13658 | 1.0686
87 | 0.0016448 | 0.00040019 | -0.0016447 | -0.00040056 | 1.2889e-07 | -3.7077e-07 | 0.0024906 | 0.0024908 | 0.0024908 | 0.981 | -0.13658 | 0.98092 | -0.13718 | 0.92251
88 | 0.0015554 | 0.00037819 | -0.0015549 | -0.00037993 | 5.3371e-07 | -1.7396e-06 | 0.0023554 | 0.0023561 | 0.0023561 | 0.98092 | -0.13718 | 0.98057 | -0.13979 | 0.87262
89 | 0.00016577 | 4.1261e-05 | -0.00016577 | -4.1546e-05 | 8.9393e-10 | -2.8534e-07 | 0.00025146 | 0.00025156 | 0.00025156 | 0.98057 | -0.13979 | 0.98056 | -0.13983 | 0.09317
90 | 0.0012414 | 0.00030165 | -0.0012411 | -0.0003032 | 2.9051e-07 | -1.5482e-06 | 0.0018805 | 0.001881 | 0.001881 | 0.98057 | -0.13979 | 0.98033 | -0.14158 | 0.69668
91 | 0.00059268 | 0.00014275 | -0.00059261 | -0.00014464 | 7.6046e-08 | -1.8863e-06 | 0.00089641 | 0.00089707 | 0.00089707 | 0.98161 | -0.13212 | 0.98148 | -0.13311 | 0.33225
92 | 0.00014922 | 3.646e-05 | -0.00014922 | -3.7397e-05 | 2.3663e-09 | -9.3755e-07 | 0.00022586 | 0.00022619 | 0.00022619 | 0.98166 | -0.13173 | 0.98165 | -0.13184 | 0.083773
93 | 0.0011253 | 0.00027418 | -0.0011251 | -0.00027549 | 1.9998e-07 | -1.3119e-06 | 0.0017053 | 0.0017058 | 0.0017058 | 0.98033 | -0.14158 | 0.98015 | -0.14293 | 0.63177
94 | 0.011934 | 0.0029587 | -0.0119 | -0.0029479 | 3.3455e-05 | 1.0726e-05 | 0.01792 | 0.017921 | 0.017921 | 0.99031 | -0.068245 | 0.98744 | -0.088975 | 6.6374
95 | 0.0012613 | 0.00031312 | -0.001261 | -0.00031466 | 2.9065e-07 | -1.5385e-06 | 0.0018996 | 0.0019002 | 0.0019002 | 0.98744 | -0.088975 | 0.98721 | -0.090663 | 0.70377
96 | 0.0099081 | 0.0024516 | -0.0098909 | -0.0024466 | 1.7214e-05 | 5.0385e-06 | 0.01492 | 0.01492 | 0.01492 | 0.98744 | -0.088975 | 0.98567 | -0.10186 | 5.5261
97 | 0.00075811 | 0.00018862 | -0.00075809 | -0.00018878 | 1.0459e-08 | -1.6023e-07 | 0.0011422 | 0.0011423 | 0.0011423 | 0.98721 | -0.090663 | 0.98719 | -0.090764 | 0.42306
98 | 0.00048414 | 0.00012013 | -0.00048411 | -0.00012133 | 3.1589e-08 | -1.2039e-06 | 0.00072933 | 0.00072976 | 0.00072976 | 0.98719 | -0.090764 | 0.98713 | -0.09124 | 0.27028
99 | -0.0098846 | -0.0024447 | 0.0098909 | 0.0024466 | 6.2838e-06 | 1.8407e-06 | 0.014921 | 0.01492 | 0.014921 | 0.98503 | -0.10657 | 0.98567 | -0.10186 | 5.5261
100 | 0.00050545 | 0.0001228 | -0.00050545 | -0.00012281 | 3.2272e-10 | -1.1049e-08 | 0.00076494 | 0.00076494 | 0.00076494 | 0.98148 | -0.13311 | 0.98148 | -0.13311 | 0.28331
101 | 0.00037802 | 9.087e-05 | -0.00037796 | -9.4725e-05 | 6.2764e-08 | -3.8545e-06 | 0.00057175 | 0.00057311 | 0.00057311 | 0.98148 | -0.13311 | 0.98131 | -0.13436 | 0.21226
102 | -0.0001776 | -4.451e-05 | 0.0001776 | 4.4163e-05 | 1.2514e-09 | -3.4694e-07 | 0.0002697 | 0.00026958 | 0.0002697 | 0.97983 | -0.14535 | 0.97984 | -0.1453 | 0.099891
103 | -0.00026068 | -6.4985e-05 | 0.00026069 | 6.3983e-05 | 7.79e-09 | -1.0019e-06 | 0.00039575 | 0.0003954 | 0.00039575 | 0.97984 | -0.1453 | 0.97987 | -0.14507 | 0.14658
104 | -0.0037053 | -0.00092623 | 0.0037056 | 0.00092617 | 2.5938e-07 | -5.9723e-08 | 0.0056778 | 0.0056777 | 0.0056778 | 0.97093 | -0.20436 | 0.971 | -0.20385 | 2.1029
105 | 0.00013993 | 3.4898e-05 | -0.00013993 | -3.507e-05 | 3.8382e-10 | -1.7168e-07 | 0.00021238 | 0.00021244 | 0.00021244 | 0.98015 | -0.14293 | 0.98015 | -0.14295 | 0.07868
106 | 0.00087003 | 0.00021173 | -0.00086996 | -0.00021252 | 6.9675e-08 | -7.8236e-07 | 0.0013186 | 0.0013189 | 0.0013189 | 0.98015 | -0.14293 | 0.98007 | -0.14353 | 0.48847
107 | -0.00024615 | -6.1691e-05 | 0.00024615 | 6.0999e-05 | 4.7992e-09 | -6.9192e-07 | 0.00037381 | 0.00037356 | 0.00037381 | 0.97985 | -0.14522 | 0.97987 | -0.14507 | 0.13845
108 | -0.00050684 | -0.00012498 | 0.00050688 | 0.00012378 | 3.5593e-08 | -1.2022e-06 | 0.00076896 | 0.00076853 | 0.00076896 | 0.97987 | -0.14507 | 0.97994 | -0.14455 | 0.2848
109 | -0.00050688 | -0.00012378 | 0.00050692 | 0.00012233 | 4.291e-08 | -1.4514e-06 | 0.00076853 | 0.00076802 | 0.00076853 | 0.97994 | -0.14455 | 0.98002 | -0.1439 | 0.28464
110 | -0.00050692 | -0.00012233 | 0.00050694 | 0.00012167 | 1.9316e-08 | -6.5405e-07 | 0.00076802 | 0.00076779 | 0.00076802 | 0.98002 | -0.1439 | 0.98006 | -0.1436 | 0.28445
111 | 0.00050694 | 0.00012154 | -0.00050694 | -0.00012167 | 4.119e-09 | -1.3953e-07 | 0.00076774 | 0.00076779 | 0.00076779 | 0.98007 | -0.14353 | 0.98006 | -0.1436 | 0.28437

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.16707 | 0.041983

## res_load
| p_mw | q_mvar
0 | 0.00041947 | 0.00010513
1 | 0.00053029 | 0.0001329
2 | 0.00044592 | 0.00011176
3 | 0.00022448 | 5.626e-05
4 | 0.00043244 | 0.00010838
5 | 0.00093916 | 0.00023537
6 | 0.0058459 | 0.0014651
7 | 0.0010973 | 0.000275
8 | 0.0014347 | 0.00035958
9 | 0.0014929 | 0.00037417
10 | 0.0021274 | 0.00053317
11 | 0.0032032 | 0.0008028
12 | 0.0022699 | 0.00056889
13 | 0.0049677 | 0.001245
14 | 0.0026373 | 0.00066098
15 | 0.0036378 | 0.00091173
16 | 0.0041637 | 0.0010435
17 | 0.0038751 | 0.0009712
18 | 0.0020263 | 0.00050783
19 | 0.0019079 | 0.00047816
20 | 0.0019086 | 0.00047835
21 | 0.0045569 | 0.0011421
22 | 0.0006723 | 0.0001685
23 | 0.002663 | 0.00066741
24 | 0.0037112 | 0.00093011
25 | 0.0028287 | 0.00070894
26 | 0.0032491 | 0.00081429
27 | 0.0018101 | 0.00045365
28 | 0.0021476 | 0.00053823
29 | 0.0021476 | 0.00053823
30 | 0.0013599 | 0.00034083
31 | 0.0027339 | 0.00068518
32 | 0.0049176 | 0.0012325
33 | 0.0074506 | 0.0018673
34 | 0.0041732 | 0.0010459
35 | 0.0026689 | 0.00066888
36 | 0.0084825 | 0.0021259
37 | 0.0068056 | 0.0017056
38 | 0.017148 | 0.0042978
39 | 0.0020341 | 0.0005098
40 | 0.0020314 | 0.00050913
41 | 0.0013152 | 0.00032962
42 | 0.0012388 | 0.00031047
43 | 0.0022595 | 0.00056628
44 | 0.003344 | 0.00083808
45 | 0.0019637 | 0.00049215
46 | 0.0019778 | 0.00049568
47 | 0.0016707 | 0.00041871
48 | 0.0063631 | 0.0015947
49 | 0.00011059 | 2.7716e-05
50 | 7.063e-05 | 1.7702e-05
51 | 0.00015589 | 3.907e-05
52 | 0.00033866 | 8.4877e-05
53 | 0.00028974 | 7.2615e-05
54 | 0.00011364 | 2.8482e-05
55 | 9.9467e-05 | 2.4929e-05
56 | 0.00030722 | 7.6995e-05
57 | 0.00014062 | 3.5243e-05
58 | 0.00093169 | 0.0002335
59 | 8.6633e-05 | 2.1712e-05
60 | 0.00043839 | 0.00010987
61 | 0.0010072 | 0.00025242
62 | 0.00095357 | 0.00023899
63 | 0.00026019 | 6.521e-05
64 | 8.9258e-05 | 2.237e-05
65 | 0.00014772 | 3.7021e-05
66 | 0.00014654 | 3.6727e-05
67 | 0.00016577 | 4.1546e-05
68 | 0.00011578 | 2.9016e-05
69 | 0.0015695 | 0.00039336
70 | 0.00073091 | 0.00018318
71 | 0.00050288 | 0.00012603
72 | 0.00027395 | 6.8659e-05
73 | 0.00048411 | 0.00012133
74 | 0.0020286 | 0.0005084
75 | 8.7157e-05 | 2.1844e-05
76 | 0.00012743 | 3.1937e-05
77 | 0.00037796 | 9.4725e-05
78 | 0.0001776 | 4.451e-05
79 | 8.3083e-05 | 2.0823e-05
80 | 0.0007129 | 0.00017867
81 | 0.00011516 | 2.8861e-05
82 | 0.00014922 | 3.7397e-05
83 | 0.00024615 | 6.1691e-05
84 | 0.00013993 | 3.507e-05
85 | 0.00036301 | 9.098e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1