## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1504-4_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1504-4_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1504-4_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1504-4_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1504-4_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1504-4_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1504-4_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1504-4_0_4_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_1504-4_0_4_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_1504-4_0_4_node_52 | 0.4 | n |  | TRUE
10 | bus_LV_1504-4_0_4_node_53 | 0.4 | n |  | TRUE
11 | bus_LV_1504-4_0_4_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_1504-4_0_4_node_54 | 0.4 | n |  | TRUE
13 | bus_LV_1504-4_0_4_node_49 | 0.4 | n |  | TRUE
14 | bus_LV_1504-4_0_4_node_48 | 0.4 | n |  | TRUE
15 | bus_LV_1504-4_0_4_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_1504-4_0_4_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_1504-4_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_1504-4_0_4_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_1504-4_0_4_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_1504-4_0_4_node_30 | 0.4 | n |  | TRUE
21 | bus_LV_1504-4_0_4_node_32 | 0.4 | n |  | TRUE
22 | bus_LV_1504-4_0_4_node_24 | 0.4 | n |  | TRUE
23 | bus_LV_1504-4_0_4_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_1504-4_0_4_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_1504-4_0_4_node_35 | 0.4 | n |  | TRUE
26 | bus_LV_1504-4_0_4_node_25 | 0.4 | n |  | TRUE
27 | bus_LV_1504-4_0_4_node_27 | 0.4 | n |  | TRUE
28 | bus_LV_1504-4_0_4_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_1504-4_0_4_node_18 | 0.4 | n |  | TRUE
30 | bus_LV_1504-4_0_4_node_19 | 0.4 | n |  | TRUE
31 | bus_LV_1504-4_0_4_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_1504-4_0_4_node_21 | 0.4 | n |  | TRUE
33 | bus_LV_1504-4_0_4_node_22 | 0.4 | n |  | TRUE
34 | bus_LV_1504-4_0_4_node_23 | 0.4 | n |  | TRUE
35 | bus_LV_1504-4_0_4_node_28 | 0.4 | n |  | TRUE
36 | bus_LV_1504-4_0_4_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_1504-4_0_4_node_29 | 0.4 | n |  | TRUE
38 | bus_LV_1504-4_0_4_node_31 | 0.4 | n |  | TRUE
39 | bus_LV_1504-4_0_4_node_45 | 0.4 | n |  | TRUE
40 | bus_LV_1504-4_0_4_node_44 | 0.4 | n |  | TRUE
41 | bus_LV_1504-4_0_4_node_33 | 0.4 | n |  | TRUE
42 | bus_LV_1504-4_0_4_node_34 | 0.4 | n |  | TRUE
43 | bus_LV_1504-4_0_4_node_47 | 0.4 | n |  | TRUE
44 | bus_LV_1504-4_0_4_node_46 | 0.4 | n |  | TRUE
45 | bus_LV_1504-4_0_4_node_50 | 0.4 | n |  | TRUE
46 | bus_LV_1504-4_0_4_node_51 | 0.4 | n |  | TRUE
47 | bus_LV_1504-4_0_4_node_42 | 0.4 | n |  | TRUE
48 | bus_LV_1504-4_0_4_node_36 | 0.4 | n |  | TRUE
49 | bus_LV_1504-4_0_4_node_37 | 0.4 | n |  | TRUE
50 | bus_LV_1504-4_0_4_node_38 | 0.4 | n |  | TRUE
51 | bus_LV_1504-4_0_4_node_39 | 0.4 | n |  | TRUE
52 | bus_LV_1504-4_0_4_node_40 | 0.4 | n |  | TRUE
53 | bus_LV_1504-4_0_4_node_41 | 0.4 | n |  | TRUE
54 | bus_MV_142_0_node_145 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1504-4_0_4_load_0 | 0 | 0.012908 | 0.003235 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1504-4_0_4_load_1 | 1 | 0.0083255 | 0.0020866 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1504-4_0_4_load_2 | 2 | 0.012003 | 0.0030082 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1504-4_0_4_load_3 | 3 | 0.0059301 | 0.0014862 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1504-4_0_4_load_7 | 7 | 0.013955 | 0.0034974 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1504-4_0_4_load_8 | 8 | 0.0021292 | 0.00053363 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1504-4_0_4_load_53 | 10 | 0.0020481 | 0.0005133 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1504-4_0_4_load_54 | 12 | 0.0029248 | 0.00073303 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1504-4_0_4_load_48 | 14 | 0.00056945 | 0.00014272 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1504-4_0_4_load_10 | 15 | 0.003443 | 0.0008629 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1504-4_0_4_load_11 | 16 | 0.0019541 | 0.00048976 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1504-4_0_4_load_12 | 17 | 0.0018387 | 0.00046082 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1504-4_0_4_load_13 | 18 | 0.0014782 | 0.00037048 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1504-4_0_4_load_14 | 19 | 0.001366 | 0.00034235 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1504-4_0_4_load_24 | 22 | 0.0022566 | 0.00056556 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1504-4_0_4_load_15 | 23 | 0.0021709 | 0.00054407 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1504-4_0_4_load_16 | 24 | 0.0014083 | 0.00035295 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1504-4_0_4_load_35 | 25 | 0.0017555 | 0.00043997 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1504-4_0_4_load_25 | 26 | 0.0017641 | 0.00044213 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1504-4_0_4_load_27 | 27 | 0.0013205 | 0.00033095 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1504-4_0_4_load_17 | 28 | 0.0013069 | 0.00032755 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1504-4_0_4_load_18 | 29 | 0.00039295 | 9.8483e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1504-4_0_4_load_19 | 30 | 0.0014018 | 0.00035132 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1504-4_0_4_load_20 | 31 | 0.0016191 | 0.00040579 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1504-4_0_4_load_21 | 32 | 0.0022915 | 0.00057431 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1504-4_0_4_load_23 | 34 | 0.0010579 | 0.00026513 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1504-4_0_4_load_28 | 35 | 0.00094672 | 0.00023727 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1504-4_0_4_load_26 | 36 | 0.0014427 | 0.00036157 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1504-4_0_4_load_29 | 37 | 0.00061457 | 0.00015403 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1504-4_0_4_load_31 | 38 | 0.0040021 | 0.001003 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1504-4_0_4_load_45 | 39 | 0.0043564 | 0.0010918 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1504-4_0_4_load_44 | 40 | 0.004358 | 0.0010922 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1504-4_0_4_load_33 | 41 | 0.0016317 | 0.00040894 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1504-4_0_4_load_34 | 42 | 0.0016897 | 0.00042348 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1504-4_0_4_load_47 | 43 | 0.0032936 | 0.00082546 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1504-4_0_4_load_46 | 44 | 0.0018994 | 0.00047603 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1504-4_0_4_load_50 | 45 | 0.0043322 | 0.0010857 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1504-4_0_4_load_51 | 46 | 0.00099449 | 0.00024924 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1504-4_0_4_load_42 | 47 | 0.0015078 | 0.00037788 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1504-4_0_4_load_36 | 48 | 0.0047658 | 0.0011944 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1504-4_0_4_load_37 | 49 | 0.0043564 | 0.0010918 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1504-4_0_4_load_38 | 50 | 0.004358 | 0.0010922 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1504-4_0_4_load_39 | 51 | 0.0026671 | 0.00066843 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1504-4_0_4_load_40 | 52 | 0.0070614 | 0.0017698 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1504-4_0_4_load_41 | 53 | 0.0036704 | 0.00091988 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 42 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1504-4_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.00069205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1504-4_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.030005 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1504-4_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.023316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1504-4_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.012152 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1504-4_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.017898 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1504-4_0_4_line_5 | NAYY 4x150 SE | 4 | 6 | 0.002983 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1504-4_0_4_line_6 | NAYY 4x150 SE | 4 | 7 | 0.082995 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1504-4_0_4_line_7 | NAYY 4x150 SE | 5 | 8 | 0.086908 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_1504-4_0_4_line_8 | NAYY 4x150 SE | 6 | 9 | 0.003059 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1504-4_0_4_line_9 | NAYY 4x150 SE | 6 | 10 | 0.040094 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1504-4_0_4_line_10 | NAYY 4x150 SE | 8 | 11 | 0.094946 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
11 | LV_1504-4_0_4_line_11 | NAYY 4x150 SE | 9 | 12 | 0.010424 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1504-4_0_4_line_12 | NAYY 4x150 SE | 11 | 13 | 0.056587 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
13 | LV_1504-4_0_4_line_13 | NAYY 4x150 SE | 13 | 14 | 0.040004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
14 | LV_1504-4_0_4_line_14 | NAYY 4x150 SE | 14 | 41 | 0.076281 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
15 | LV_1504-4_0_4_line_15 | NAYY 4x150 SE | 14 | 43 | 0.0027876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1504-4_0_4_line_16 | NAYY 4x150 SE | 15 | 16 | 0.012786 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1504-4_0_4_line_17 | NAYY 4x150 SE | 15 | 17 | 0.0051634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1504-4_0_4_line_18 | NAYY 4x150 SE | 16 | 18 | 0.0011706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1504-4_0_4_line_19 | NAYY 4x150 SE | 17 | 19 | 0.018416 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1504-4_0_4_line_20 | NAYY 4x150 SE | 18 | 23 | 0.02622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1504-4_0_4_line_21 | NAYY 4x150 SE | 19 | 24 | 0.015373 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1504-4_0_4_line_22 | NAYY 4x150 SE | 20 | 21 | 0.1116 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
23 | LV_1504-4_0_4_line_23 | NAYY 4x150 SE | 20 | 22 | 0.52165 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
24 | LV_1504-4_0_4_line_24 | NAYY 4x150 SE | 21 | 41 | 0.11125 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
25 | LV_1504-4_0_4_line_25 | NAYY 4x150 SE | 21 | 42 | 0.05222 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
26 | LV_1504-4_0_4_line_26 | NAYY 4x150 SE | 22 | 26 | 0.018721 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1504-4_0_4_line_27 | NAYY 4x150 SE | 22 | 23 | 0.028318 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1504-4_0_4_line_28 | NAYY 4x150 SE | 24 | 25 | 0.0012 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1504-4_0_4_line_29 | NAYY 4x150 SE | 25 | 27 | 0.014979 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1504-4_0_4_line_30 | NAYY 4x150 SE | 27 | 36 | 0.011651 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1504-4_0_4_line_31 | NAYY 4x150 SE | 28 | 29 | 0.0054967 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1504-4_0_4_line_32 | NAYY 4x150 SE | 28 | 30 | 0.013701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1504-4_0_4_line_33 | NAYY 4x150 SE | 29 | 31 | 0.0065308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1504-4_0_4_line_34 | NAYY 4x150 SE | 30 | 32 | 0.0012333 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1504-4_0_4_line_35 | NAYY 4x150 SE | 31 | 33 | 0.12198 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1504-4_0_4_line_36 | NAYY 4x150 SE | 32 | 34 | 0.015472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1504-4_0_4_line_37 | NAYY 4x150 SE | 33 | 35 | 0.078488 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1504-4_0_4_line_38 | NAYY 4x150 SE | 34 | 36 | 0.015407 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1504-4_0_4_line_39 | NAYY 4x150 SE | 37 | 38 | 0.041243 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1504-4_0_4_line_40 | NAYY 4x150 SE | 37 | 39 | 0.17179 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1504-4_0_4_line_41 | NAYY 4x150 SE | 39 | 40 | 0.0080881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1504-4_0_4_line_42 | NAYY 4x150 SE | 40 | 53 | 0.016682 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1504-4_0_4_line_43 | NAYY 4x150 SE | 42 | 45 | 0.016596 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1504-4_0_4_line_44 | NAYY 4x150 SE | 43 | 44 | 0.019103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1504-4_0_4_line_45 | NAYY 4x150 SE | 44 | 47 | 0.034996 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1504-4_0_4_line_46 | NAYY 4x150 SE | 45 | 46 | 0.026191 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1504-4_0_4_line_47 | NAYY 4x150 SE | 47 | 52 | 0.0059139 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1504-4_0_4_line_48 | NAYY 4x150 SE | 48 | 49 | 0.011321 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1504-4_0_4_line_49 | NAYY 4x150 SE | 48 | 50 | 0.010406 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1504-4_0_4_line_50 | NAYY 4x150 SE | 49 | 51 | 0.010491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1504-4_0_4_line_51 | NAYY 4x150 SE | 50 | 52 | 0.01527 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1504-4_0_4_line_52 | NAYY 4x150 SE | 51 | 53 | 0.021894 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1504-4_0_4_trafo_34 | 0.25 MVA 20/0.4 kV | 54 | 42 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2681272.8655 | 1201406.0427 | 2681272.3945 | 1201405.5357
1 | 2681272.8655 | 1201406.0427 | 2681273.1263 | 1201406.3233 | 2681286.5967 | 1201417.747 | 2681296.3443 | 1201424.6766
2 | 2681257.7224 | 1201387.5635 | 2681261.1975 | 1201393.4863 | 2681272.3945 | 1201405.5357
3 | 2681306.8506 | 1201430.7641 | 2681297.8377 | 1201425.7383 | 2681296.3443 | 1201424.6766
4 | 2681252.3484 | 1201370.8184 | 2681252.7261 | 1201376.6272 | 2681254.911 | 1201382.7719 | 2681257.7224 | 1201387.5635
5 | 2681309.4413 | 1201432.2558 | 2681306.8506 | 1201430.7641
6 | 2681234.9456 | 1201411.7632 | 2681251.0661 | 1201426.4694 | 2681257.6941 | 1201431.1069 | 2681262.8918 | 1201432.8898 | 2681296.5966 | 1201438.0625 | 2681300.1956 | 1201437.6223 | 2681303.5555 | 1201436.2894 | 2681306.8506 | 1201430.7641
7 | 2681252.3484 | 1201370.8184 | 2681264.9409 | 1201371.8013 | 2681277.7291 | 1201373.5097 | 2681293.7811 | 1201373.1166 | 2681308.9751 | 1201368.0868 | 2681330.731 | 1201357.465 | 2681335.3774 | 1201355.3534
8 | 2681309.4413 | 1201432.2558 | 2681312.1 | 1201433.7819
9 | 2681309.4413 | 1201432.2558 | 2681312.7672 | 1201428.9434 | 2681325.759 | 1201415.1337 | 2681336.7916 | 1201402.9452
10 | 2681423.9215 | 1201346.2269 | 2681412.0631 | 1201339.4055 | 2681404.4038 | 1201336.7106 | 2681396.9647 | 1201335.1749 | 2681383.0487 | 1201335.7858 | 2681369.0678 | 1201340.0426 | 2681335.3774 | 1201355.3534
11 | 2681312.1 | 1201433.7819 | 2681309.5153 | 1201436.882 | 2681305.2534 | 1201441.6395
12 | 2681399.1314 | 1201316.3926 | 2681416.8066 | 1201318.6681 | 2681423.4395 | 1201320.7154 | 2681427.6299 | 1201323.7966 | 2681430.4432 | 1201328.5046 | 2681431.9002 | 1201332.7493 | 2681431.7726 | 1201336.5277 | 2681430.2827 | 1201340.2765 | 2681427.6578 | 1201344.0876 | 2681423.9215 | 1201346.2269
13 | 2681399.1314 | 1201316.3926 | 2681395.505 | 1201316.043 | 2681384.7811 | 1201314.2291 | 2681370.1268 | 1201312.5952 | 2681359.3878 | 1201312.5188
14 | 2681359.3878 | 1201312.5188 | 2681356.9009 | 1201236.2782
15 | 2681356.6093 | 1201312.6784 | 2681358.169 | 1201312.5102 | 2681359.3878 | 1201312.5188
16 | 2681382.7951 | 1200542.5066 | 2681387.9839 | 1200542.2533 | 2681395.4634 | 1200543.5504
17 | 2681400.5509 | 1200544.4327 | 2681395.4634 | 1200543.5504
18 | 2681382.7951 | 1200542.5066 | 2681381.6258 | 1200542.5637
19 | 2681418.3954 | 1200548.7597 | 2681410.9447 | 1200546.2352 | 2681400.5509 | 1200544.4327
20 | 2681381.6258 | 1200542.5637 | 2681363.5898 | 1200543.4442 | 2681357.7903 | 1200549.1875
21 | 2681418.3954 | 1200548.7597 | 2681432.955 | 1200553.6928
22 | 2681336.4607 | 1201171.4925 | 2681330.0469 | 1201158.3747 | 2681338.3297 | 1201144.3675 | 2681358.731 | 1201120.9193 | 2681361.6964 | 1201113.3549 | 2681358.5268 | 1201106.8521 | 2681352.3304 | 1201099.0073 | 2681342.2336 | 1201076.8337
23 | 2681342.2336 | 1201076.8337 | 2681331.9332 | 1200555.2887
24 | 2681356.9009 | 1201236.2782 | 2681375.9018 | 1201221.1718 | 2681384.4335 | 1201213.4831 | 2681387.8925 | 1201206.0033 | 2681386.2249 | 1201198.776 | 2681383.8508 | 1201190.8832 | 2681379.481 | 1201186.432 | 2681336.4607 | 1201171.4925
25 | 2681336.4607 | 1201171.4925 | 2681318.9421 | 1201177.8025 | 2681293.2378 | 1201186.525 | 2681287.6162 | 1201189.6989
26 | 2681313.2125 | 1200555.4025 | 2681331.9332 | 1200555.2887
27 | 2681357.7903 | 1200549.1875 | 2681351.7513 | 1200555.1682 | 2681331.9332 | 1200555.2887
28 | 2681432.955 | 1200553.6928 | 2681434.0915 | 1200554.0779
29 | 2681448.937 | 1200555.2865 | 2681436.3472 | 1200554.8422 | 2681434.0915 | 1200554.0779
30 | 2681448.937 | 1200555.2865 | 2681451.7491 | 1200555.3857 | 2681459.5126 | 1200551.1634
31 | 2681501.2753 | 1200533.9718 | 2681506.6744 | 1200532.9404
32 | 2681487.8172 | 1200536.5427 | 2681501.2753 | 1200533.9718
33 | 2681513.0892 | 1200531.715 | 2681506.6744 | 1200532.9404
34 | 2681487.8172 | 1200536.5427 | 2681486.6059 | 1200536.7741
35 | 2681627.7697 | 1200504.0547 | 2681626.7141 | 1200508.8766 | 2681610.8485 | 1200517.7433 | 2681575.0197 | 1200520.556 | 2681533.8246 | 1200527.754 | 2681513.0892 | 1200531.715
36 | 2681473.0371 | 1200543.785 | 2681482.9796 | 1200537.4668 | 2681486.6059 | 1200536.7741
37 | 2681627.7697 | 1200504.0547 | 2681633.8438 | 1200506.3835 | 2681681.2708 | 1200517.2828 | 2681701.1335 | 1200529.4998
38 | 2681459.5126 | 1200551.1634 | 2681472.7884 | 1200543.943 | 2681473.0371 | 1200543.785
39 | 2681138.1567 | 1201171.9084 | 2681166.5668 | 1201171.3383 | 2681179.3233 | 1201169.9952
40 | 2681205.5517 | 1201339.7739 | 2681179.3233 | 1201169.9952
41 | 2681205.5517 | 1201339.7739 | 2681213.5996 | 1201338.9687
42 | 2681213.5996 | 1201338.9687 | 2681230.1991 | 1201337.3079
43 | 2681287.6162 | 1201189.6989 | 2681282.9887 | 1201192.3115 | 2681276.0996 | 1201201.2456 | 2681276.0996 | 1201201.2456
44 | 2681356.6093 | 1201312.6784 | 2681344.5305 | 1201313.981 | 2681337.7383 | 1201315.4747
45 | 2681304.4582 | 1201326.2464 | 2681314.2923 | 1201323.0752 | 2681334.8185 | 1201316.1168 | 2681337.7383 | 1201315.4747
46 | 2681276.0996 | 1201201.2456 | 2681269.1653 | 1201203.4416 | 2681262.64 | 1201203.5418 | 2681256.7063 | 1201202.1269 | 2681251.6542 | 1201198.3775
47 | 2681304.4582 | 1201326.2464 | 2681298.8296 | 1201328.0614
48 | 2681273.6887 | 1201332.9567 | 2681262.4237 | 1201334.0838
49 | 2681273.6887 | 1201332.9567 | 2681281.8547 | 1201332.1397 | 2681284.0022 | 1201331.6642
50 | 2681262.4237 | 1201334.0838 | 2681251.9844 | 1201335.1283
51 | 2681284.0022 | 1201331.6642 | 2681295.667 | 1201329.0812 | 2681298.8296 | 1201328.0614
52 | 2681230.1991 | 1201337.3079 | 2681251.9844 | 1201335.1283

## bus_geodata
| x | y | coords
0 | 2681272.8655 | 1201406.0427
1 | 2681272.3945 | 1201405.5357
2 | 2681296.3443 | 1201424.6766
3 | 2681257.7224 | 1201387.5635
4 | 2681306.8506 | 1201430.7641
5 | 2681252.3484 | 1201370.8184
6 | 2681309.4413 | 1201432.2558
7 | 2681234.9456 | 1201411.7632
8 | 2681335.3774 | 1201355.3534
9 | 2681312.1 | 1201433.7819
10 | 2681336.7916 | 1201402.9452
11 | 2681423.9215 | 1201346.2269
12 | 2681305.2534 | 1201441.6395
13 | 2681399.1314 | 1201316.3926
14 | 2681359.3878 | 1201312.5188
15 | 2681395.4634 | 1200543.5504
16 | 2681382.7951 | 1200542.5066
17 | 2681400.5509 | 1200544.4327
18 | 2681381.6258 | 1200542.5637
19 | 2681418.3954 | 1200548.7597
20 | 2681342.2336 | 1201076.8337
21 | 2681336.4607 | 1201171.4925
22 | 2681331.9332 | 1200555.2887
23 | 2681357.7903 | 1200549.1875
24 | 2681432.955 | 1200553.6928
25 | 2681434.0915 | 1200554.0779
26 | 2681313.2125 | 1200555.4025
27 | 2681448.937 | 1200555.2865
28 | 2681501.2753 | 1200533.9718
29 | 2681506.6744 | 1200532.9404
30 | 2681487.8172 | 1200536.5427
31 | 2681513.0892 | 1200531.715
32 | 2681486.6059 | 1200536.7741
33 | 2681627.7697 | 1200504.0547
34 | 2681473.0371 | 1200543.785
35 | 2681701.1335 | 1200529.4998
36 | 2681459.5126 | 1200551.1634
37 | 2681179.3233 | 1201169.9952
38 | 2681138.1567 | 1201171.9084
39 | 2681205.5517 | 1201339.7739
40 | 2681213.5996 | 1201338.9687
41 | 2681356.9009 | 1201236.2782
42 | 2681287.6162 | 1201189.6989
43 | 2681356.6093 | 1201312.6784
44 | 2681337.7383 | 1201315.4747
45 | 2681276.0996 | 1201201.2456
46 | 2681251.6542 | 1201198.3775
47 | 2681304.4582 | 1201326.2464
48 | 2681273.6887 | 1201332.9567
49 | 2681262.4237 | 1201334.0838
50 | 2681284.0022 | 1201331.6642
51 | 2681251.9844 | 1201335.1283
52 | 2681298.8296 | 1201328.0614
53 | 2681230.1991 | 1201337.3079
54 | 2681336.4607 | 1201171.4925

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97384 | -0.18362 | 0.012908 | 0.003235
1 | 0.97388 | -0.1833 | 0.0083255 | 0.0020866
2 | 0.97248 | -0.1934 | 0.012003 | 0.0030082
3 | 0.97566 | -0.17052 | 0.0059301 | 0.0014862
4 | 0.97214 | -0.19583 | 0 | 0
5 | 0.97719 | -0.15963 | 0 | 0
6 | 0.97212 | -0.19599 | 0 | 0
7 | 0.97044 | -0.20809 | 0.013955 | 0.0034974
8 | 0.98089 | -0.13333 | 0.0021292 | 0.00053363
9 | 0.9721 | -0.19608 | 0 | 0
10 | 0.972 | -0.19686 | 0.0020481 | 0.0005133
11 | 0.98368 | -0.1136 | 0 | 0
12 | 0.97206 | -0.19641 | 0.0029248 | 0.00073303
13 | 0.98534 | -0.10189 | 0 | 0
14 | 0.98652 | -0.093634 | 0.00056945 | 0.00014272
15 | 0.98039 | -0.1376 | 0.003443 | 0.0008629
16 | 0.98079 | -0.13473 | 0.0019541 | 0.00048976
17 | 0.98025 | -0.13857 | 0.0018387 | 0.00046082
18 | 0.98083 | -0.13444 | 0.0014782 | 0.00037048
19 | 0.97981 | -0.1417 | 0.001366 | 0.00034235
20 | 0.99474 | -0.036318 | 0 | 0
21 | 0.99643 | -0.024567 | 0 | 0
22 | 0.9829 | -0.11966 | 0.0022566 | 0.00056556
23 | 0.98178 | -0.12763 | 0.0021709 | 0.00054407
24 | 0.97948 | -0.14409 | 0.0014083 | 0.00035295
25 | 0.97945 | -0.14426 | 0.0017555 | 0.00043997
26 | 0.98286 | -0.12 | 0.0017641 | 0.00044213
27 | 0.9792 | -0.1461 | 0.0013205 | 0.00033095
28 | 0.97854 | -0.1508 | 0.0013069 | 0.00032755
29 | 0.97852 | -0.15097 | 0.00039295 | 9.8483e-05
30 | 0.97863 | -0.15019 | 0.0014018 | 0.00035132
31 | 0.9785 | -0.15114 | 0.0016191 | 0.00040579
32 | 0.97864 | -0.15011 | 0.0022915 | 0.00057431
33 | 0.97833 | -0.15237 | 0 | 0
34 | 0.97882 | -0.14883 | 0.0010579 | 0.00026513
35 | 0.97822 | -0.15314 | 0.00094672 | 0.00023727
36 | 0.97902 | -0.14738 | 0.0014427 | 0.00036157
37 | 0.97866 | -0.14959 | 0.00061457 | 0.00015403
38 | 0.97842 | -0.15131 | 0.0040021 | 0.001003
39 | 0.97981 | -0.14131 | 0.0043564 | 0.0010918
40 | 0.97992 | -0.14055 | 0.004358 | 0.0010922
41 | 0.99052 | -0.065628 | 0.0016317 | 0.00040894
42 | 1 | 0 | -0.14979 | -0.037708
43 | 0.98633 | -0.094976 | 0.0032936 | 0.00082546
44 | 0.98512 | -0.10354 | 0.0018994 | 0.00047603
45 | 0.99987 | -0.00088294 | 0.0043322 | 0.0010857
46 | 0.99984 | -0.0011433 | 0.00099449 | 0.00024924
47 | 0.983 | -0.1186 | 0.0015078 | 0.00037788
48 | 0.98148 | -0.1294 | 0.0047658 | 0.0011944
49 | 0.98109 | -0.13223 | 0.0043564 | 0.0010918
50 | 0.98192 | -0.1263 | 0.004358 | 0.0010922
51 | 0.98079 | -0.13437 | 0.0026671 | 0.00066843
52 | 0.98265 | -0.12106 | 0.0070614 | 0.0017698
53 | 0.98024 | -0.13824 | 0.0036704 | 0.00091988
54 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.043911 | -0.011013 | 0.043913 | 0.011013 | 1.9442e-06 | 7.3918e-07 | 0.067099 | 0.067099 | 0.067099 | 0.97384 | -0.18362 | 0.97388 | -0.1833 | 24.8514
1 | 0.031003 | 0.0077776 | -0.030961 | -0.0077618 | 4.2023e-05 | 1.579e-05 | 0.047375 | 0.047376 | 0.047376 | 0.97384 | -0.18362 | 0.97248 | -0.1934 | 17.5465
2 | -0.052239 | -0.0131 | 0.052331 | 0.013135 | 9.2694e-05 | 3.5361e-05 | 0.079819 | 0.079819 | 0.079819 | 0.97388 | -0.1833 | 0.97566 | -0.17052 | 29.5627
3 | 0.018958 | 0.0047536 | -0.018952 | -0.0047513 | 6.3812e-06 | 2.3036e-06 | 0.029009 | 0.029009 | 0.029009 | 0.97248 | -0.1934 | 0.97214 | -0.19583 | 10.7442
4 | -0.058261 | -0.014622 | 0.05835 | 0.014655 | 8.8194e-05 | 3.3697e-05 | 0.088863 | 0.088863 | 0.088863 | 0.97566 | -0.17052 | 0.97719 | -0.15963 | 32.9124
5 | 0.0049735 | 0.0012458 | -0.0049734 | -0.0012458 | 1.0787e-07 | 4.5037e-09 | 0.0076125 | 0.0076125 | 0.0076125 | 0.97214 | -0.19583 | 0.97212 | -0.19599 | 2.8194
6 | 0.013978 | 0.0035055 | -0.013955 | -0.0034974 | 2.3711e-05 | 8.0924e-06 | 0.021397 | 0.021397 | 0.021397 | 0.97214 | -0.19583 | 0.97044 | -0.20809 | 7.9249
7 | -0.05835 | -0.014655 | 0.058564 | 0.014735 | 0.00021412 | 8.0168e-05 | 0.088863 | 0.088863 | 0.088863 | 0.97719 | -0.15963 | 0.98089 | -0.13333 | 16.4562
8 | 0.002925 | 0.00073293 | -0.002925 | -0.00073295 | 3.8264e-08 | -2.3208e-08 | 0.0044773 | 0.0044773 | 0.0044773 | 0.97212 | -0.19599 | 0.9721 | -0.19608 | 1.6582
9 | 0.0020483 | 0.0005129 | -0.0020481 | -0.0005133 | 2.4594e-07 | -4.0243e-07 | 0.0031352 | 0.0031354 | 0.0031354 | 0.97212 | -0.19599 | 0.972 | -0.19686 | 1.1613
10 | -0.060693 | -0.015269 | 0.06086 | 0.01533 | 0.00016749 | 6.0813e-05 | 0.092093 | 0.092091 | 0.092093 | 0.98089 | -0.13333 | 0.98368 | -0.1136 | 11.3695
11 | 0.002925 | 0.00073295 | -0.0029248 | -0.00073303 | 1.3039e-07 | -7.9072e-08 | 0.0044773 | 0.0044773 | 0.0044773 | 0.9721 | -0.19608 | 0.97206 | -0.19641 | 1.6583
12 | -0.06086 | -0.01533 | 0.06096 | 0.015366 | 9.9819e-05 | 3.6233e-05 | 0.092091 | 0.092091 | 0.092091 | 0.98368 | -0.1136 | 0.98534 | -0.10189 | 11.3693
13 | -0.06096 | -0.015366 | 0.061031 | 0.015392 | 7.0565e-05 | 2.561e-05 | 0.092091 | 0.09209 | 0.092091 | 0.98534 | -0.10189 | 0.98652 | -0.093634 | 11.3692
14 | -0.10875 | -0.027377 | 0.10917 | 0.027538 | 0.00042711 | 0.00016134 | 0.16407 | 0.16407 | 0.16407 | 0.98652 | -0.093634 | 0.99052 | -0.065628 | 20.2556
15 | 0.047145 | 0.011842 | -0.047137 | -0.011839 | 8.7987e-06 | 3.3485e-06 | 0.071121 | 0.071121 | 0.071121 | 0.98652 | -0.093634 | 0.98633 | -0.094976 | 26.3412
16 | -0.021615 | -0.0054164 | 0.021624 | 0.0054195 | 8.5873e-06 | 3.1415e-06 | 0.032807 | 0.032807 | 0.032807 | 0.98039 | -0.1376 | 0.98079 | -0.13473 | 12.1507
17 | 0.018172 | 0.0045535 | -0.01817 | -0.0045526 | 2.451e-06 | 8.776e-07 | 0.027581 | 0.027581 | 0.027581 | 0.98039 | -0.1376 | 0.98025 | -0.13857 | 10.2153
18 | -0.023578 | -0.0059093 | 0.023579 | 0.0059096 | 9.347e-07 | 3.4473e-07 | 0.035772 | 0.035772 | 0.035772 | 0.98079 | -0.13473 | 0.98083 | -0.13444 | 13.2488
19 | 0.016331 | 0.0040918 | -0.016324 | -0.0040893 | 7.0621e-06 | 2.4841e-06 | 0.02479 | 0.02479 | 0.02479 | 0.98025 | -0.13857 | 0.97981 | -0.1417 | 9.1815
20 | -0.025057 | -0.0062801 | 0.025081 | 0.0062888 | 2.3643e-05 | 8.7622e-06 | 0.038014 | 0.038014 | 0.038014 | 0.98083 | -0.13444 | 0.98178 | -0.12763 | 14.0793
21 | 0.014958 | 0.0037469 | -0.014953 | -0.0037452 | 4.9498e-06 | 1.7102e-06 | 0.022716 | 0.022716 | 0.022716 | 0.97981 | -0.1417 | 0.97948 | -0.14409 | 8.4132
22 | -0.031668 | -0.0079788 | 0.03172 | 0.0079945 | 5.2124e-05 | 1.5694e-05 | 0.047386 | 0.047385 | 0.047386 | 0.99474 | -0.036318 | 0.99643 | -0.024567 | 5.8502
23 | 0.031668 | 0.0079788 | -0.031303 | -0.0078516 | 0.0003655 | 0.00012719 | 0.047386 | 0.047391 | 0.047391 | 0.99474 | -0.036318 | 0.9829 | -0.11966 | 8.7762
24 | 0.11145 | 0.02819 | -0.1108 | -0.027947 | 0.00064164 | 0.00024246 | 0.16652 | 0.16652 | 0.16652 | 0.99643 | -0.024567 | 0.99052 | -0.065628 | 20.5581
25 | -0.14317 | -0.036184 | 0.14366 | 0.036373 | 0.00049697 | 0.0001891 | 0.2139 | 0.2139 | 0.2139 | 0.99643 | -0.024567 | 1 | 0 | 26.4079
26 | 0.0017642 | 0.00044192 | -0.0017641 | -0.00044213 | 8.3328e-08 | -2.0522e-07 | 0.0026707 | 0.0026708 | 0.0026708 | 0.9829 | -0.11966 | 0.98286 | -0.12 | 0.9892
27 | 0.027282 | 0.0068442 | -0.027252 | -0.0068329 | 3.0146e-05 | 1.1236e-05 | 0.041304 | 0.041304 | 0.041304 | 0.9829 | -0.11966 | 0.98178 | -0.12763 | 15.2979
28 | 0.013545 | 0.0033923 | -0.013544 | -0.0033922 | 3.1702e-07 | 1.0683e-07 | 0.020576 | 0.020576 | 0.020576 | 0.97948 | -0.14409 | 0.97945 | -0.14426 | 7.6209
29 | 0.011789 | 0.0029522 | -0.011786 | -0.0029512 | 2.998e-06 | 9.6461e-07 | 0.017909 | 0.017909 | 0.017909 | 0.97945 | -0.14426 | 0.9792 | -0.1461 | 6.6331
30 | 0.010465 | 0.0026203 | -0.010464 | -0.0026197 | 1.8387e-06 | 5.6064e-07 | 0.015903 | 0.015903 | 0.015903 | 0.9792 | -0.1461 | 0.97902 | -0.14738 | 5.8899
31 | 0.0029592 | 0.00073903 | -0.0029591 | -0.00073907 | 6.9424e-08 | -4.2348e-08 | 0.0044989 | 0.004499 | 0.004499 | 0.97854 | -0.1508 | 0.97852 | -0.15097 | 1.6663
32 | -0.0042661 | -0.0010666 | 0.0042665 | 0.0010665 | 3.597e-07 | -3.379e-08 | 0.0064863 | 0.0064863 | 0.0064863 | 0.97854 | -0.1508 | 0.97863 | -0.15019 | 2.4023
33 | 0.0025662 | 0.00064059 | -0.0025661 | -0.00064065 | 6.203e-08 | -5.8179e-08 | 0.0039014 | 0.0039014 | 0.0039014 | 0.97852 | -0.15097 | 0.9785 | -0.15114 | 1.445
34 | -0.0056683 | -0.0014179 | 0.0056683 | 0.0014179 | 5.7151e-08 | 6.4856e-09 | 0.0086177 | 0.0086177 | 0.0086177 | 0.97863 | -0.15019 | 0.97864 | -0.15011 | 3.1917
35 | 0.00094698 | 0.00023485 | -0.00094682 | -0.00023632 | 1.5772e-07 | -1.4713e-06 | 0.0014392 | 0.0014398 | 0.0014398 | 0.9785 | -0.15114 | 0.97833 | -0.15237 | 0.53324
36 | -0.0079598 | -0.0019922 | 0.0079613 | 0.0019925 | 1.414e-06 | 3.4939e-07 | 0.012102 | 0.012102 | 0.012102 | 0.97864 | -0.15011 | 0.97882 | -0.14883 | 4.4822
37 | 0.00094682 | 0.00023632 | -0.00094672 | -0.00023727 | 1.0155e-07 | -9.4639e-07 | 0.0014398 | 0.0014401 | 0.0014401 | 0.97833 | -0.15237 | 0.97822 | -0.15314 | 0.53337
38 | -0.0090191 | -0.0022577 | 0.0090209 | 0.0022582 | 1.8071e-06 | 5.0134e-07 | 0.01371 | 0.01371 | 0.01371 | 0.97882 | -0.14883 | 0.97902 | -0.14738 | 5.0778
39 | 0.0040031 | 0.0010029 | -0.0040021 | -0.001003 | 9.5338e-07 | -1.5142e-07 | 0.0060864 | 0.0060866 | 0.0060866 | 0.97866 | -0.14959 | 0.97842 | -0.15131 | 2.2543
40 | -0.0046176 | -0.0011569 | 0.0046229 | 0.0011568 | 5.2835e-06 | -1.2908e-07 | 0.0070208 | 0.0070201 | 0.0070208 | 0.97866 | -0.14959 | 0.97981 | -0.14131 | 2.6003
41 | -0.0089794 | -0.0022486 | 0.0089803 | 0.0022489 | 9.3844e-07 | 2.5906e-07 | 0.013636 | 0.013636 | 0.013636 | 0.97981 | -0.14131 | 0.97992 | -0.14055 | 5.0504
42 | -0.013338 | -0.0033411 | 0.013343 | 0.0033425 | 4.2702e-06 | 1.4322e-06 | 0.020254 | 0.020254 | 0.020254 | 0.97992 | -0.14055 | 0.98024 | -0.13824 | 7.5013
43 | 0.0053274 | 0.0013347 | -0.0053267 | -0.0013347 | 6.5075e-07 | 3.2588e-08 | 0.007927 | 0.0079271 | 0.0079271 | 1 | 0 | 0.99987 | -0.00088294 | 2.936
44 | 0.043843 | 0.011014 | -0.043791 | -0.010994 | 5.2166e-05 | 1.982e-05 | 0.066152 | 0.066152 | 0.066152 | 0.98633 | -0.094976 | 0.98512 | -0.10354 | 24.5009
45 | 0.041891 | 0.010518 | -0.041804 | -0.010485 | 8.7455e-05 | 3.3192e-05 | 0.063283 | 0.063284 | 0.063284 | 0.98512 | -0.10354 | 0.983 | -0.1186 | 23.4384
46 | 0.00099453 | 0.00024891 | -0.00099449 | -0.00024924 | 3.5799e-08 | -3.2974e-07 | 0.0014799 | 0.0014801 | 0.0014801 | 0.99987 | -0.00088294 | 0.99984 | -0.0011433 | 0.54817
47 | 0.040296 | 0.010107 | -0.040282 | -0.010102 | 1.3732e-05 | 5.2067e-06 | 0.061001 | 0.061001 | 0.061001 | 0.983 | -0.1186 | 0.98265 | -0.12106 | 22.593
48 | 0.024061 | 0.0060314 | -0.024051 | -0.006028 | 9.4007e-06 | 3.4726e-06 | 0.036479 | 0.036479 | 0.036479 | 0.98148 | -0.1294 | 0.98109 | -0.13223 | 13.5107
49 | -0.028827 | -0.0072259 | 0.028839 | 0.0072305 | 1.2403e-05 | 4.6388e-06 | 0.043704 | 0.043704 | 0.043704 | 0.98148 | -0.1294 | 0.98192 | -0.1263 | 16.1867
50 | 0.019695 | 0.0049362 | -0.019689 | -0.004934 | 5.8416e-06 | 2.1143e-06 | 0.029871 | 0.029871 | 0.029871 | 0.98109 | -0.13223 | 0.98079 | -0.13437 | 11.0635
51 | -0.033197 | -0.0083227 | 0.033221 | 0.0083318 | 2.4116e-05 | 9.0822e-06 | 0.050308 | 0.050308 | 0.050308 | 0.98192 | -0.1263 | 0.98265 | -0.12106 | 18.6327
52 | 0.017022 | 0.0042656 | -0.017013 | -0.0042624 | 9.1116e-06 | 3.2283e-06 | 0.025825 | 0.025825 | 0.025825 | 0.98079 | -0.13437 | 0.98024 | -0.13824 | 9.5649

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.15148 | 0.038132

## res_load
| p_mw | q_mvar
0 | 0.012908 | 0.003235
1 | 0.0083255 | 0.0020866
2 | 0.012003 | 0.0030082
3 | 0.0059301 | 0.0014862
4 | 0.013955 | 0.0034974
5 | 0.0021292 | 0.00053363
6 | 0.0020481 | 0.0005133
7 | 0.0029248 | 0.00073303
8 | 0.00056945 | 0.00014272
9 | 0.003443 | 0.0008629
10 | 0.0019541 | 0.00048976
11 | 0.0018387 | 0.00046082
12 | 0.0014782 | 0.00037048
13 | 0.001366 | 0.00034235
14 | 0.0022566 | 0.00056556
15 | 0.0021709 | 0.00054407
16 | 0.0014083 | 0.00035295
17 | 0.0017555 | 0.00043997
18 | 0.0017641 | 0.00044213
19 | 0.0013205 | 0.00033095
20 | 0.0013069 | 0.00032755
21 | 0.00039295 | 9.8483e-05
22 | 0.0014018 | 0.00035132
23 | 0.0016191 | 0.00040579
24 | 0.0022915 | 0.00057431
25 | 0.0010579 | 0.00026513
26 | 0.00094672 | 0.00023727
27 | 0.0014427 | 0.00036157
28 | 0.00061457 | 0.00015403
29 | 0.0040021 | 0.001003
30 | 0.0043564 | 0.0010918
31 | 0.004358 | 0.0010922
32 | 0.0016317 | 0.00040894
33 | 0.0016897 | 0.00042348
34 | 0.0032936 | 0.00082546
35 | 0.0018994 | 0.00047603
36 | 0.0043322 | 0.0010857
37 | 0.00099449 | 0.00024924
38 | 0.0015078 | 0.00037788
39 | 0.0047658 | 0.0011944
40 | 0.0043564 | 0.0010918
41 | 0.004358 | 0.0010922
42 | 0.0026671 | 0.00066843
43 | 0.0070614 | 0.0017698
44 | 0.0036704 | 0.00091988

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1