## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1505-10_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1505-10_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1505-10_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1505-10_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1505-10_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1505-10_0_2_node_12 | 0.4 | n |  | TRUE
6 | bus_LV_1505-10_0_2_node_30 | 0.4 | n |  | TRUE
7 | bus_LV_1505-10_0_2_node_17 | 0.4 | n |  | TRUE
8 | bus_LV_1505-10_0_2_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_1505-10_0_2_node_29 | 0.4 | n |  | TRUE
10 | bus_LV_1505-10_0_2_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_1505-10_0_2_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_1505-10_0_2_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1505-10_0_2_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_1505-10_0_2_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_1505-10_0_2_node_21 | 0.4 | n |  | TRUE
16 | bus_LV_1505-10_0_2_node_20 | 0.4 | n |  | TRUE
17 | bus_LV_1505-10_0_2_node_22 | 0.4 | n |  | TRUE
18 | bus_LV_1505-10_0_2_node_19 | 0.4 | n |  | TRUE
19 | bus_LV_1505-10_0_2_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_1505-10_0_2_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_1505-10_0_2_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_1505-10_0_2_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_1505-10_0_2_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_1505-10_0_2_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_1505-10_0_2_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_1505-10_0_2_node_24 | 0.4 | n |  | TRUE
27 | bus_LV_1505-10_0_2_node_25 | 0.4 | n |  | TRUE
28 | bus_LV_1505-10_0_2_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_1505-10_0_2_node_27 | 0.4 | n |  | TRUE
30 | bus_LV_1505-10_0_2_node_28 | 0.4 | n |  | TRUE
31 | bus_MV_142_1_node_161 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1505-10_0_2_load_0 | 0 | 0.012262 | 0.0030732 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1505-10_0_2_load_1 | 1 | 0.0042241 | 0.0010587 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1505-10_0_2_load_2 | 2 | 0.0056648 | 0.0014197 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1505-10_0_2_load_4 | 4 | 0.0064581 | 0.0016186 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1505-10_0_2_load_30 | 6 | 0.0064185 | 0.0016086 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1505-10_0_2_load_17 | 7 | 0.0050311 | 0.0012609 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1505-10_0_2_load_11 | 8 | 0.0003358 | 8.416e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1505-10_0_2_load_29 | 9 | 0.0085339 | 0.0021388 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1505-10_0_2_load_5 | 10 | 0.0045724 | 0.001146 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1505-10_0_2_load_6 | 11 | 0.0025255 | 0.00063295 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1505-10_0_2_load_7 | 12 | 0.0025897 | 0.00064905 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1505-10_0_2_load_8 | 13 | 0.0025897 | 0.00064905 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1505-10_0_2_load_9 | 14 | 0.0025897 | 0.00064905 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1505-10_0_2_load_21 | 15 | 0.0025898 | 0.00064905 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1505-10_0_2_load_20 | 16 | 0.0025241 | 0.0006326 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1505-10_0_2_load_22 | 17 | 0.0025255 | 0.00063295 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1505-10_0_2_load_19 | 18 | 0.0025897 | 0.00064905 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1505-10_0_2_load_10 | 19 | 0.00033541 | 8.4061e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1505-10_0_2_load_15 | 20 | 0.0023595 | 0.00059135 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1505-10_0_2_load_13 | 21 | 0.00032458 | 8.1348e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1505-10_0_2_load_14 | 22 | 0.0028587 | 0.00071645 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1505-10_0_2_load_16 | 23 | 0.0028266 | 0.00070842 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1505-10_0_2_load_18 | 24 | 0.0064635 | 0.0016199 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1505-10_0_2_load_23 | 25 | 0.0025898 | 0.00064905 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1505-10_0_2_load_24 | 26 | 0.0069852 | 0.0017507 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1505-10_0_2_load_25 | 27 | 0.0025898 | 0.00064905 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1505-10_0_2_load_26 | 28 | 0.0025291 | 0.00063386 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1505-10_0_2_load_27 | 29 | 0.0025898 | 0.00064905 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1505-10_0_2_load_28 | 30 | 0.0066477 | 0.0016661 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1505-10_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.010806 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1505-10_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.017764 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1505-10_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.045697 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1505-10_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.023665 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1505-10_0_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.047257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1505-10_0_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.026524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1505-10_0_2_line_6 | NAYY 4x150 SE | 5 | 7 | 0.038014 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1505-10_0_2_line_7 | NAYY 4x150 SE | 5 | 8 | 0.040793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1505-10_0_2_line_8 | NAYY 4x150 SE | 6 | 9 | 0.027517 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1505-10_0_2_line_9 | NAYY 4x150 SE | 7 | 20 | 0.011768 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1505-10_0_2_line_10 | NAYY 4x150 SE | 8 | 19 | 0.0012012 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1505-10_0_2_line_11 | NAYY 4x150 SE | 10 | 11 | 0.0046203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1505-10_0_2_line_12 | NAYY 4x150 SE | 10 | 12 | 0.0018733 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1505-10_0_2_line_13 | NAYY 4x150 SE | 11 | 13 | 0.00031168 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1505-10_0_2_line_14 | NAYY 4x150 SE | 12 | 14 | 0.010269 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1505-10_0_2_line_15 | NAYY 4x150 SE | 13 | 15 | 0.0096882 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1505-10_0_2_line_16 | NAYY 4x150 SE | 14 | 16 | 0.0032134 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1505-10_0_2_line_17 | NAYY 4x150 SE | 15 | 17 | 0.0046177 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1505-10_0_2_line_18 | NAYY 4x150 SE | 16 | 18 | 0.0035918 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1505-10_0_2_line_19 | NAYY 4x150 SE | 17 | 25 | 0.002187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1505-10_0_2_line_20 | NAYY 4x150 SE | 18 | 24 | 0.0063817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1505-10_0_2_line_21 | NAYY 4x150 SE | 20 | 21 | 0.0027732 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1505-10_0_2_line_22 | NAYY 4x150 SE | 21 | 22 | 0.0066422 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1505-10_0_2_line_23 | NAYY 4x150 SE | 22 | 23 | 0.0018758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1505-10_0_2_line_24 | NAYY 4x150 SE | 23 | 24 | 0.0057866 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1505-10_0_2_line_25 | NAYY 4x150 SE | 25 | 26 | 0.0038961 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1505-10_0_2_line_26 | NAYY 4x150 SE | 26 | 27 | 0.0060768 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1505-10_0_2_line_27 | NAYY 4x150 SE | 27 | 28 | 0.0060438 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1505-10_0_2_line_28 | NAYY 4x150 SE | 28 | 29 | 0.0007615 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1505-10_0_2_line_29 | NAYY 4x150 SE | 29 | 30 | 0.012735 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1505-10_0_2_trafo_7 | 0.25 MVA 20/0.4 kV | 31 | 12 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2
0 | 2673957.2243 | 1204056.0811 | 2673966.7158 | 1204061.2466
1 | 2673957.2243 | 1204056.0811 | 2673941.6215 | 1204047.5898
2 | 2674006.8539 | 1204083.0905 | 2673966.7158 | 1204061.2466
3 | 2673920.8358 | 1204036.2778 | 2673941.6215 | 1204047.5898
4 | 2674022.6537 | 1204038.5476 | 2674006.8539 | 1204083.0905
5 | 2673920.8358 | 1204036.2778 | 2673897.5379 | 1204023.5986
6 | 2674022.6537 | 1204038.5476 | 2673994.6238 | 1204012.8684
7 | 2674022.6537 | 1204038.5476 | 2674036.1362 | 1204000.0468
8 | 2673873.3682 | 1204010.445 | 2673897.5379 | 1204023.5986
9 | 2673994.6238 | 1204012.8684 | 2673985.9466 | 1204004.9189
10 | 2674036.1362 | 1204000.0468 | 2674036.5332 | 1203998.9132
11 | 2673950.3851 | 1203982.1946 | 2673946.3593 | 1203979.9274
12 | 2673950.3851 | 1203982.1946 | 2673952.0174 | 1203983.1138
13 | 2673946.3593 | 1203979.9274 | 2673946.0877 | 1203979.7744
14 | 2673960.9647 | 1203988.1526 | 2673952.0174 | 1203983.1138
15 | 2673946.0877 | 1203979.7744 | 2673937.6461 | 1203975.0205
16 | 2673960.9647 | 1203988.1526 | 2673963.7647 | 1203989.7294
17 | 2673933.6226 | 1203972.7546 | 2673937.6461 | 1203975.0205
18 | 2673963.7647 | 1203989.7294 | 2673966.8943 | 1203991.4919
19 | 2673931.717 | 1203971.6814 | 2673933.6226 | 1203972.7546
20 | 2673972.4549 | 1203994.6234 | 2673966.8943 | 1203991.4919
21 | 2673985.9466 | 1204004.9189 | 2673983.9018 | 1204003.0456
22 | 2673983.9018 | 1204003.0456 | 2673979.0043 | 1203998.5588
23 | 2673979.0043 | 1203998.5588 | 2673978.3043 | 1203997.9176 | 2673977.497 | 1203997.4629
24 | 2673972.4549 | 1203994.6234 | 2673977.497 | 1203997.4629
25 | 2673931.717 | 1203971.6814 | 2673928.3223 | 1203969.7696
26 | 2673923.0274 | 1203966.7878 | 2673928.3223 | 1203969.7696
27 | 2673923.0274 | 1203966.7878 | 2673917.7613 | 1203963.8221
28 | 2673917.7613 | 1203963.8221 | 2673917.0978 | 1203963.4484
29 | 2673917.0978 | 1203963.4484 | 2673906.0014 | 1203957.1994

## bus_geodata
| x | y | coords
0 | 2673957.2243 | 1204056.0811
1 | 2673966.7158 | 1204061.2466
2 | 2673941.6215 | 1204047.5898
3 | 2674006.8539 | 1204083.0905
4 | 2673920.8358 | 1204036.2778
5 | 2674022.6537 | 1204038.5476
6 | 2673897.5379 | 1204023.5986
7 | 2673994.6238 | 1204012.8684
8 | 2674036.1362 | 1204000.0468
9 | 2673873.3682 | 1204010.445
10 | 2673950.3851 | 1203982.1946
11 | 2673946.3593 | 1203979.9274
12 | 2673952.0174 | 1203983.1138
13 | 2673946.0877 | 1203979.7744
14 | 2673960.9647 | 1203988.1526
15 | 2673937.6461 | 1203975.0205
16 | 2673963.7647 | 1203989.7294
17 | 2673933.6226 | 1203972.7546
18 | 2673966.8943 | 1203991.4919
19 | 2674036.5332 | 1203998.9132
20 | 2673985.9466 | 1204004.9189
21 | 2673983.9018 | 1204003.0456
22 | 2673979.0043 | 1203998.5588
23 | 2673977.497 | 1203997.4629
24 | 2673972.4549 | 1203994.6234
25 | 2673931.717 | 1203971.6814
26 | 2673928.3223 | 1203969.7696
27 | 2673923.0274 | 1203966.7878
28 | 2673917.7613 | 1203963.8221
29 | 2673917.0978 | 1203963.4484
30 | 2673906.0014 | 1203957.1994
31 | 2674022.6537 | 1204038.5476

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98661 | -0.093795 | 0.012262 | 0.0030732
1 | 0.98722 | -0.089438 | 0.0042241 | 0.0010587
2 | 0.98591 | -0.098732 | 0.0056648 | 0.0014197
3 | 0.9901 | -0.069107 | 0 | 0
4 | 0.98518 | -0.10394 | 0.0064581 | 0.0016186
5 | 0.99308 | -0.048204 | 0 | 0
6 | 0.98461 | -0.10802 | 0.0064185 | 0.0016086
7 | 0.99551 | -0.031219 | 0.0050311 | 0.0012609
8 | 0.99304 | -0.048482 | 0.0003358 | 8.416e-05
9 | 0.98427 | -0.11044 | 0.0085339 | 0.0021388
10 | 0.9999 | -0.00072433 | 0.0045724 | 0.001146
11 | 0.99967 | -0.0023005 | 0.0025255 | 0.00063295
12 | 1 | 0 | -0.11206 | -0.027978
13 | 0.99966 | -0.002399 | 0.0025897 | 0.00064905
14 | 0.99894 | -0.0073695 | 0.0025897 | 0.00064905
15 | 0.99926 | -0.005211 | 0.0025898 | 0.00064905
16 | 0.99862 | -0.0095955 | 0.0025241 | 0.0006326
17 | 0.99908 | -0.0064325 | 0.0025255 | 0.00063295
18 | 0.99827 | -0.011995 | 0.0025897 | 0.00064905
19 | 0.99304 | -0.048486 | 0.00033541 | 8.4061e-05
20 | 0.99635 | -0.025383 | 0.0023595 | 0.00059135
21 | 0.99656 | -0.023943 | 0.00032458 | 8.1348e-05
22 | 0.99705 | -0.020475 | 0.0028587 | 0.00071645
23 | 0.9972 | -0.019443 | 0.0028266 | 0.00070842
24 | 0.99768 | -0.016096 | 0.0064635 | 0.0016199
25 | 0.99901 | -0.0069559 | 0.0025898 | 0.00064905
26 | 0.99889 | -0.0077876 | 0.0069852 | 0.0017507
27 | 0.99876 | -0.0086604 | 0.0025898 | 0.00064905
28 | 0.99866 | -0.0093721 | 0.0025291 | 0.00063386
29 | 0.99865 | -0.0094425 | 0.0025898 | 0.00064905
30 | 0.99853 | -0.01029 | 0.0066477 | 0.0016661
31 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.039383 | -0.0098751 | 0.039407 | 0.0098842 | 2.3791e-05 | 9.0124e-06 | 0.059399 | 0.059399 | 0.059399 | 0.98661 | -0.093795 | 0.98722 | -0.089438 | 21.9998
1 | 0.027121 | 0.0068019 | -0.027102 | -0.006795 | 1.8547e-05 | 6.9069e-06 | 0.040905 | 0.040906 | 0.040906 | 0.98661 | -0.093795 | 0.98591 | -0.098732 | 15.1502
2 | -0.043631 | -0.010943 | 0.043754 | 0.01099 | 0.00012333 | 4.685e-05 | 0.065766 | 0.065766 | 0.065766 | 0.98722 | -0.089438 | 0.9901 | -0.069107 | 24.3579
3 | 0.021437 | 0.0053753 | -0.021422 | -0.0053696 | 1.5459e-05 | 5.6443e-06 | 0.032356 | 0.032356 | 0.032356 | 0.98591 | -0.098732 | 0.98518 | -0.10394 | 11.9836
4 | -0.043754 | -0.01099 | 0.043882 | 0.011038 | 0.00012754 | 4.8445e-05 | 0.065766 | 0.065766 | 0.065766 | 0.9901 | -0.069107 | 0.99308 | -0.048204 | 24.3578
5 | 0.014964 | 0.0037511 | -0.014955 | -0.0037482 | 8.4549e-06 | 2.9143e-06 | 0.022602 | 0.022602 | 0.022602 | 0.98518 | -0.10394 | 0.98461 | -0.10802 | 8.371
6 | -0.044553 | -0.011206 | 0.044659 | 0.011246 | 0.00010576 | 4.0183e-05 | 0.066771 | 0.066771 | 0.066771 | 0.99308 | -0.048204 | 0.99551 | -0.031219 | 24.7302
7 | 0.00067123 | 0.00016769 | -0.00067121 | -0.00016821 | 2.5744e-08 | -5.1787e-07 | 0.0010056 | 0.0010058 | 0.0010058 | 0.99308 | -0.048204 | 0.99304 | -0.048482 | 0.3725
8 | 0.0085368 | 0.0021396 | -0.0085339 | -0.0021388 | 2.8581e-06 | 7.494e-07 | 0.012901 | 0.012902 | 0.012902 | 0.98461 | -0.10802 | 0.98427 | -0.11044 | 4.7784
9 | -0.04969 | -0.012507 | 0.04973 | 0.012522 | 4.0529e-05 | 1.5435e-05 | 0.074291 | 0.074291 | 0.074291 | 0.99551 | -0.031219 | 0.99635 | -0.025383 | 27.5153
10 | 0.00033541 | 8.4045e-05 | -0.00033541 | -8.4061e-05 | 1.8927e-10 | -1.5467e-08 | 0.00050258 | 0.00050259 | 0.00050259 | 0.99304 | -0.048482 | 0.99304 | -0.048486 | 0.18614
11 | 0.034193 | 0.0085733 | -0.034186 | -0.0085704 | 7.4657e-06 | 2.8108e-06 | 0.050887 | 0.050887 | 0.050887 | 0.9999 | -0.00072433 | 0.99967 | -0.0023005 | 18.847
12 | -0.038766 | -0.0097192 | 0.03877 | 0.0097207 | 3.8905e-06 | 1.4718e-06 | 0.057691 | 0.057691 | 0.057691 | 0.9999 | -0.00072433 | 1 | 0 | 21.3672
13 | 0.03166 | 0.0079375 | -0.03166 | -0.0079373 | 4.3196e-07 | 1.6205e-07 | 0.047128 | 0.047128 | 0.047128 | 0.99967 | -0.0023005 | 0.99966 | -0.002399 | 17.4547
14 | 0.072494 | 0.018257 | -0.072419 | -0.018229 | 7.4605e-05 | 2.8559e-05 | 0.1079 | 0.1079 | 0.1079 | 1 | 0 | 0.99894 | -0.0073695 | 39.9641
15 | 0.02907 | 0.0072883 | -0.029059 | -0.0072841 | 1.132e-05 | 4.227e-06 | 0.043273 | 0.043273 | 0.043273 | 0.99966 | -0.002399 | 0.99926 | -0.005211 | 16.027
16 | 0.069829 | 0.01758 | -0.069808 | -0.017571 | 2.1707e-05 | 8.3067e-06 | 0.10405 | 0.10405 | 0.10405 | 0.99894 | -0.0073695 | 0.99862 | -0.0095955 | 38.5354
17 | 0.026469 | 0.006635 | -0.026465 | -0.0066333 | 4.4768e-06 | 1.6614e-06 | 0.039416 | 0.039416 | 0.039416 | 0.99926 | -0.005211 | 0.99908 | -0.0064325 | 14.5987
18 | 0.067284 | 0.016939 | -0.067261 | -0.01693 | 2.2541e-05 | 8.6225e-06 | 0.10028 | 0.10028 | 0.10028 | 0.99862 | -0.0095955 | 0.99827 | -0.011995 | 37.1424
19 | 0.023939 | 0.0060004 | -0.023938 | -0.0059998 | 1.7349e-06 | 6.3863e-07 | 0.035655 | 0.035655 | 0.035655 | 0.99908 | -0.0064325 | 0.99901 | -0.0069559 | 13.2056
20 | 0.064671 | 0.016281 | -0.064634 | -0.016267 | 3.7025e-05 | 1.4157e-05 | 0.096424 | 0.096424 | 0.096424 | 0.99827 | -0.011995 | 0.99768 | -0.016096 | 35.7126
21 | -0.05209 | -0.013114 | 0.0521 | 0.013118 | 1.0478e-05 | 3.994e-06 | 0.077815 | 0.077815 | 0.077815 | 0.99635 | -0.025383 | 0.99656 | -0.023943 | 28.8205
22 | -0.052425 | -0.013199 | 0.05245 | 0.013209 | 2.5411e-05 | 9.6867e-06 | 0.0783 | 0.0783 | 0.0783 | 0.99656 | -0.023943 | 0.99705 | -0.020475 | 29
23 | -0.055309 | -0.013925 | 0.055317 | 0.013928 | 7.9797e-06 | 3.0446e-06 | 0.082566 | 0.082566 | 0.082566 | 0.99705 | -0.020475 | 0.9972 | -0.019443 | 30.5801
24 | -0.058144 | -0.014637 | 0.058171 | 0.014647 | 2.7195e-05 | 1.0384e-05 | 0.086784 | 0.086784 | 0.086784 | 0.9972 | -0.019443 | 0.99768 | -0.016096 | 32.1422
25 | 0.021348 | 0.0053507 | -0.021345 | -0.0053498 | 2.4581e-06 | 8.9441e-07 | 0.031798 | 0.031798 | 0.031798 | 0.99901 | -0.0069559 | 0.99889 | -0.0077876 | 11.7769
26 | 0.01436 | 0.0035992 | -0.014358 | -0.0035986 | 1.7352e-06 | 5.8786e-07 | 0.021392 | 0.021392 | 0.021392 | 0.99889 | -0.0077876 | 0.99876 | -0.0086604 | 7.923
27 | 0.011769 | 0.0029495 | -0.011767 | -0.0029491 | 1.1594e-06 | 3.6684e-07 | 0.017534 | 0.017534 | 0.017534 | 0.99876 | -0.0086604 | 0.99866 | -0.0093721 | 6.4939
28 | 0.0092383 | 0.0023153 | -0.0092382 | -0.0023153 | 9.0037e-08 | 2.4666e-08 | 0.013765 | 0.013765 | 0.013765 | 0.99866 | -0.0093721 | 0.99865 | -0.0094425 | 5.0982
29 | 0.0066485 | 0.0016662 | -0.0066477 | -0.0016661 | 7.7986e-07 | 1.3334e-07 | 0.0099064 | 0.0099065 | 0.0099065 | 0.99865 | -0.0094425 | 0.99853 | -0.01029 | 3.6691

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.11465 | 0.028627

## res_load
| p_mw | q_mvar
0 | 0.012262 | 0.0030732
1 | 0.0042241 | 0.0010587
2 | 0.0056648 | 0.0014197
3 | 0.0064581 | 0.0016186
4 | 0.0064185 | 0.0016086
5 | 0.0050311 | 0.0012609
6 | 0.0003358 | 8.416e-05
7 | 0.0085339 | 0.0021388
8 | 0.0045724 | 0.001146
9 | 0.0025255 | 0.00063295
10 | 0.0025897 | 0.00064905
11 | 0.0025897 | 0.00064905
12 | 0.0025897 | 0.00064905
13 | 0.0025898 | 0.00064905
14 | 0.0025241 | 0.0006326
15 | 0.0025255 | 0.00063295
16 | 0.0025897 | 0.00064905
17 | 0.00033541 | 8.4061e-05
18 | 0.0023595 | 0.00059135
19 | 0.00032458 | 8.1348e-05
20 | 0.0028587 | 0.00071645
21 | 0.0028266 | 0.00070842
22 | 0.0064635 | 0.0016199
23 | 0.0025898 | 0.00064905
24 | 0.0069852 | 0.0017507
25 | 0.0025898 | 0.00064905
26 | 0.0025291 | 0.00063386
27 | 0.0025898 | 0.00064905
28 | 0.0066477 | 0.0016661

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1