## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1505-32_1_2_node_12 | 0.4 | n |  | TRUE
1 | bus_LV_1505-32_1_2_node_13 | 0.4 | n |  | TRUE
2 | bus_LV_1505-32_1_2_node_14 | 0.4 | n |  | TRUE
3 | bus_LV_1505-32_1_2_node_15 | 0.4 | n |  | TRUE
4 | bus_LV_1505-32_1_2_node_16 | 0.4 | n |  | TRUE
5 | bus_LV_1505-32_1_2_node_31 | 0.4 | n |  | TRUE
6 | bus_LV_1505-32_1_2_node_17 | 0.4 | n |  | TRUE
7 | bus_LV_1505-32_1_2_node_36 | 0.4 | n |  | TRUE
8 | bus_LV_1505-32_1_2_node_37 | 0.4 | n |  | TRUE
9 | bus_LV_1505-32_1_2_node_47 | 0.4 | n |  | TRUE
10 | bus_LV_1505-32_1_2_node_48 | 0.4 | n |  | TRUE
11 | bus_LV_1505-32_1_2_node_49 | 0.4 | n |  | TRUE
12 | bus_LV_1505-32_1_2_node_51 | 0.4 | n |  | TRUE
13 | bus_LV_1505-32_1_2_node_55 | 0.4 | n |  | TRUE
14 | bus_LV_1505-32_1_2_node_50 | 0.4 | n |  | TRUE
15 | bus_LV_1505-32_1_2_node_30 | 0.4 | n |  | TRUE
16 | bus_LV_1505-32_1_2_node_18 | 0.4 | n |  | TRUE
17 | bus_LV_1505-32_1_2_node_19 | 0.4 | n |  | TRUE
18 | bus_LV_1505-32_1_2_node_23 | 0.4 | n |  | TRUE
19 | bus_LV_1505-32_1_2_node_24 | 0.4 | n |  | TRUE
20 | bus_LV_1505-32_1_2_node_25 | 0.4 | n |  | TRUE
21 | bus_LV_1505-32_1_2_node_46 | 0.4 | n |  | TRUE
22 | bus_LV_1505-32_1_2_node_43 | 0.4 | n |  | TRUE
23 | bus_LV_1505-32_1_2_node_33 | 0.4 | n |  | TRUE
24 | bus_LV_1505-32_1_2_node_54 | 0.4 | n |  | TRUE
25 | bus_LV_1505-32_1_2_node_45 | 0.4 | n |  | TRUE
26 | bus_LV_1505-32_1_2_node_44 | 0.4 | n |  | TRUE
27 | bus_LV_1505-32_1_2_node_41 | 0.4 | n |  | TRUE
28 | bus_MV_142_1_node_224 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1505-32_1_2_load_12 | 0 | 0.0034254 | 0.00085849 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1505-32_1_2_load_13 | 1 | 0.0052545 | 0.0013169 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1505-32_1_2_load_14 | 2 | 0.0037316 | 0.00093522 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1505-32_1_2_load_15 | 3 | 0.0048246 | 0.0012092 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1505-32_1_2_load_16 | 4 | 0.014497 | 0.0036332 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1505-32_1_2_load_31 | 5 | 0.0071621 | 0.001795 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1505-32_1_2_load_17 | 6 | 0.0056915 | 0.0014264 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1505-32_1_2_load_36 | 7 | 0.0059912 | 0.0015015 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1505-32_1_2_load_37 | 8 | 0.0067194 | 0.0016841 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1505-32_1_2_load_47 | 9 | 0.004867 | 0.0012198 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1505-32_1_2_load_55 | 13 | 0.00018135 | 4.5451e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1505-32_1_2_load_50 | 14 | 0.00018389 | 4.6087e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1505-32_1_2_load_30 | 15 | 0.0062503 | 0.0015665 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1505-32_1_2_load_18 | 16 | 0.0027645 | 0.00069285 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1505-32_1_2_load_19 | 17 | 0.0025372 | 0.00063589 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1505-32_1_2_load_23 | 18 | 0.0074567 | 0.0018688 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1505-32_1_2_load_24 | 19 | 0.0043674 | 0.0010946 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1505-32_1_2_load_25 | 20 | 0.0067942 | 0.0017028 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1505-32_1_2_load_43 | 22 | 0.00032205 | 8.0713e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1505-32_1_2_load_33 | 23 | 0.005879 | 0.0014734 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1505-32_1_2_load_54 | 24 | 0.0059027 | 0.0014794 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1505-32_1_2_load_44 | 26 | 0.0039643 | 0.00099354 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1505-32_1_2_load_41 | 27 | 0.00032066 | 8.0365e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 6 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1505-32_1_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.016579 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1505-32_1_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0017772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1505-32_1_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0089995 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1505-32_1_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.020903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1505-32_1_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.0084022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1505-32_1_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.0062203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1505-32_1_2_line_6 | NAYY 4x150 SE | 5 | 8 | 0.050843 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1505-32_1_2_line_7 | NAYY 4x150 SE | 5 | 15 | 0.0027583 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1505-32_1_2_line_8 | NAYY 4x150 SE | 6 | 16 | 0.013853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1505-32_1_2_line_9 | NAYY 4x150 SE | 7 | 8 | 0.037122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1505-32_1_2_line_10 | NAYY 4x150 SE | 9 | 10 | 0.045751 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1505-32_1_2_line_11 | NAYY 4x150 SE | 9 | 11 | 0.093429 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1505-32_1_2_line_12 | NAYY 4x150 SE | 10 | 21 | 0.051531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1505-32_1_2_line_13 | NAYY 4x150 SE | 11 | 15 | 0.11723 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1505-32_1_2_line_14 | NAYY 4x150 SE | 12 | 13 | 0.099235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1505-32_1_2_line_15 | NAYY 4x150 SE | 12 | 14 | 0.024042 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1505-32_1_2_line_16 | NAYY 4x150 SE | 13 | 22 | 0.15698 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1505-32_1_2_line_17 | NAYY 4x150 SE | 16 | 17 | 0.0041459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1505-32_1_2_line_18 | NAYY 4x150 SE | 17 | 18 | 0.012422 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1505-32_1_2_line_19 | NAYY 4x150 SE | 18 | 19 | 0.012829 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1505-32_1_2_line_20 | NAYY 4x150 SE | 19 | 20 | 0.017398 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1505-32_1_2_line_21 | NAYY 4x150 SE | 20 | 23 | 0.01775 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1505-32_1_2_line_22 | NAYY 4x150 SE | 21 | 24 | 0.015761 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1505-32_1_2_line_23 | NAYY 4x150 SE | 21 | 25 | 0.022783 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1505-32_1_2_line_24 | NAYY 4x150 SE | 22 | 26 | 0.11985 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1505-32_1_2_line_25 | NAYY 4x150 SE | 22 | 27 | 0.017506 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1505-32_1_2_line_26 | NAYY 4x150 SE | 25 | 26 | 0.03229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1505-32_1_2_trafo_17 | 0.25 MVA 20/0.4 kV | 28 | 6 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2674434.9522 | 1204629.4338 | 2674441.7967 | 1204631.6904 | 2674450.8139 | 1204634.2453
1 | 2674433.2644 | 1204628.8774 | 2674434.9522 | 1204629.4338
2 | 2674459.4725 | 1204636.6987 | 2674450.8139 | 1204634.2453
3 | 2674433.2644 | 1204628.8774 | 2674413.412 | 1204622.3323
4 | 2674467.6319 | 1204638.689 | 2674462.6068 | 1204637.5867 | 2674459.4725 | 1204636.6987
5 | 2674413.412 | 1204622.3323 | 2674407.5044 | 1204620.3847
6 | 2674467.6319 | 1204638.689 | 2674477.7182 | 1204588.8561
7 | 2674467.6319 | 1204638.689 | 2674470.3262 | 1204639.28
8 | 2674394.3232 | 1204616.1226 | 2674403.2084 | 1204618.9684 | 2674407.5044 | 1204620.3847
9 | 2674442.9365 | 1204577.2577 | 2674449.1883 | 1204580.7064 | 2674462.4802 | 1204586.7425 | 2674477.7182 | 1204588.8561
10 | 2674340.3432 | 1204742.4734 | 2674374.2483 | 1204748.1768 | 2674385.545 | 1204749.4638
11 | 2674478.6324 | 1204756.2157 | 2674470.9133 | 1204756.6086 | 2674463.5734 | 1204756.4837 | 2674436.7703 | 1204754.7486 | 2674409.9691 | 1204752.2464 | 2674385.545 | 1204749.4638
12 | 2674340.3432 | 1204742.4734 | 2674289.3133 | 1204734.3113
13 | 2674470.3262 | 1204639.28 | 2674478.6324 | 1204756.2157
14 | 2674299.6661 | 1205016.8044 | 2674280.3373 | 1204919.4702
15 | 2674299.6661 | 1205016.8044 | 2674292.0268 | 1205020.5895 | 2674282.6286 | 1205021.4509 | 2674278.8406 | 1205026.2056
16 | 2674160.2073 | 1204818.4259 | 2674280.3373 | 1204919.4702
17 | 2674390.3749 | 1204614.858 | 2674394.3232 | 1204616.1226
18 | 2674390.3749 | 1204614.858 | 2674378.5447 | 1204611.069
19 | 2674366.5086 | 1204606.6387 | 2674375.6864 | 1204610.1535 | 2674378.5447 | 1204611.069
20 | 2674366.5086 | 1204606.6387 | 2674350.2611 | 1204600.4163
21 | 2674333.9005 | 1204593.5364 | 2674347.2997 | 1204599.2823 | 2674350.2611 | 1204600.4163
22 | 2674289.3133 | 1204734.3113 | 2674290.6888 | 1204731.371 | 2674295.0268 | 1204719.6288
23 | 2674266.8215 | 1204730.2958 | 2674289.3133 | 1204734.3113
24 | 2674235.0062 | 1204724.7771 | 2674160.2073 | 1204818.4259
25 | 2674160.2073 | 1204818.4259 | 2674145.8966 | 1204808.3429
26 | 2674266.8215 | 1204730.2958 | 2674235.0062 | 1204724.7771

## bus_geodata
| x | y | coords
0 | 2674434.9522 | 1204629.4338
1 | 2674450.8139 | 1204634.2453
2 | 2674433.2644 | 1204628.8774
3 | 2674459.4725 | 1204636.6987
4 | 2674413.412 | 1204622.3323
5 | 2674467.6319 | 1204638.689
6 | 2674407.5044 | 1204620.3847
7 | 2674442.9365 | 1204577.2577
8 | 2674477.7182 | 1204588.8561
9 | 2674385.545 | 1204749.4638
10 | 2674340.3432 | 1204742.4734
11 | 2674478.6324 | 1204756.2157
12 | 2674299.6661 | 1205016.8044
13 | 2674280.3373 | 1204919.4702
14 | 2674278.8406 | 1205026.2056
15 | 2674470.3262 | 1204639.28
16 | 2674394.3232 | 1204616.1226
17 | 2674390.3749 | 1204614.858
18 | 2674378.5447 | 1204611.069
19 | 2674366.5086 | 1204606.6387
20 | 2674350.2611 | 1204600.4163
21 | 2674289.3133 | 1204734.3113
22 | 2674160.2073 | 1204818.4259
23 | 2674333.9005 | 1204593.5364
24 | 2674295.0268 | 1204719.6288
25 | 2674266.8215 | 1204730.2958
26 | 2674235.0062 | 1204724.7771
27 | 2674145.8966 | 1204808.3429
28 | 2674544.0914 | 1204650.033

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99743 | -0.017953 | 0.0034254 | 0.00085849
1 | 0.99619 | -0.026618 | 0.0052545 | 0.0013169
2 | 0.99757 | -0.016964 | 0.0037316 | 0.00093522
3 | 0.99559 | -0.030854 | 0.0048246 | 0.0012092
4 | 0.99934 | -0.0045777 | 0.014497 | 0.0036332
5 | 0.99509 | -0.034404 | 0.0071621 | 0.001795
6 | 1 | 0 | -0.10461 | -0.026061
7 | 0.99384 | -0.043174 | 0.0059912 | 0.0015015
8 | 0.99416 | -0.040927 | 0.0067194 | 0.0016841
9 | 0.99022 | -0.068751 | 0.004867 | 0.0012198
10 | 0.9895 | -0.073844 | 0 | 0
11 | 0.99234 | -0.053755 | 0 | 0
12 | 0.98802 | -0.084495 | 0 | 0
13 | 0.98804 | -0.084301 | 0.00018135 | 4.5451e-05
14 | 0.98801 | -0.08454 | 0.00018389 | 4.6087e-05
15 | 0.995 | -0.035018 | 0.0062503 | 0.0015665
16 | 0.99941 | -0.0041234 | 0.0027645 | 0.00069285
17 | 0.99925 | -0.0052438 | 0.0025372 | 0.00063589
18 | 0.99882 | -0.0082874 | 0.0074567 | 0.0018688
19 | 0.9985 | -0.010476 | 0.0043674 | 0.0010946
20 | 0.99819 | -0.012684 | 0.0067942 | 0.0017028
21 | 0.9887 | -0.079586 | 0 | 0
22 | 0.98813 | -0.083684 | 0.00032205 | 8.0713e-05
23 | 0.99804 | -0.01373 | 0.005879 | 0.0014734
24 | 0.98856 | -0.080537 | 0.0059027 | 0.0014794
25 | 0.98853 | -0.080754 | 0 | 0
26 | 0.9883 | -0.082407 | 0.0039643 | 0.00099354
27 | 0.98812 | -0.083741 | 0.00032066 | 8.0365e-05
28 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.052163 | 0.013091 | -0.0521 | -0.013067 | 6.266e-05 | 2.3884e-05 | 0.077825 | 0.077825 | 0.077825 | 0.99743 | -0.017953 | 0.99619 | -0.026618 | 28.8242
1 | -0.055588 | -0.013949 | 0.055596 | 0.013952 | 7.6281e-06 | 2.9107e-06 | 0.082936 | 0.082936 | 0.082936 | 0.99743 | -0.017953 | 0.99757 | -0.016964 | 30.7169
2 | 0.046846 | 0.01175 | -0.046818 | -0.01174 | 2.7499e-05 | 1.0459e-05 | 0.069977 | 0.069977 | 0.069977 | 0.99619 | -0.026618 | 0.99559 | -0.030854 | 25.9174
3 | -0.059328 | -0.014887 | 0.05943 | 0.014926 | 0.00010217 | 3.9021e-05 | 0.088502 | 0.088502 | 0.088502 | 0.99757 | -0.016964 | 0.99934 | -0.0045777 | 32.7784
4 | 0.041994 | 0.01053 | -0.041973 | -0.010523 | 2.0655e-05 | 7.8351e-06 | 0.062766 | 0.062766 | 0.062766 | 0.99559 | -0.030854 | 0.99509 | -0.034404 | 23.2467
5 | -0.073926 | -0.01856 | 0.073973 | 0.018578 | 4.704e-05 | 1.8011e-05 | 0.11009 | 0.11009 | 0.11009 | 0.99934 | -0.0045777 | 1 | 0 | 40.773
6 | 0.012724 | 0.0031896 | -0.012712 | -0.0031858 | 1.1486e-05 | 3.7578e-06 | 0.019027 | 0.019027 | 0.019027 | 0.99509 | -0.034404 | 0.99416 | -0.040927 | 7.0472
7 | 0.022087 | 0.005538 | -0.022085 | -0.0055373 | 1.8777e-06 | 6.8635e-07 | 0.033029 | 0.033029 | 0.033029 | 0.99509 | -0.034404 | 0.995 | -0.035018 | 12.233
8 | 0.029841 | 0.0074833 | -0.029824 | -0.0074769 | 1.7045e-05 | 6.3741e-06 | 0.044405 | 0.044405 | 0.044405 | 1 | 0 | 0.99941 | -0.0041234 | 16.4463
9 | -0.0059912 | -0.0015015 | 0.005993 | 0.0015018 | 1.8638e-06 | 2.3568e-07 | 0.0089702 | 0.00897 | 0.0089702 | 0.99384 | -0.043174 | 0.99416 | -0.040927 | 3.3223
10 | 0.010894 | 0.0027254 | -0.010886 | -0.002723 | 7.6495e-06 | 2.354e-06 | 0.016369 | 0.016369 | 0.016369 | 0.99022 | -0.068751 | 0.9895 | -0.073844 | 6.0626
11 | -0.015761 | -0.0039452 | 0.015794 | 0.0039565 | 3.2698e-05 | 1.1372e-05 | 0.023683 | 0.023682 | 0.023683 | 0.99022 | -0.068751 | 0.99234 | -0.053755 | 8.7714
12 | 0.010886 | 0.002723 | -0.010878 | -0.0027204 | 8.6161e-06 | 2.6525e-06 | 0.016369 | 0.016369 | 0.016369 | 0.9895 | -0.073844 | 0.9887 | -0.079586 | 6.0627
13 | -0.015794 | -0.0039565 | 0.015835 | 0.0039708 | 4.1026e-05 | 1.4261e-05 | 0.023682 | 0.023682 | 0.023682 | 0.99234 | -0.053755 | 0.995 | -0.035018 | 8.7712
14 | -0.00018389 | -4.5779e-05 | 0.0001839 | 4.451e-05 | 4.7382e-09 | -1.2691e-06 | 0.00027684 | 0.0002764 | 0.00027684 | 0.98802 | -0.084495 | 0.98804 | -0.084301 | 0.10253
15 | 0.00018389 | 4.5779e-05 | -0.00018389 | -4.6087e-05 | 1.1503e-09 | -3.0746e-07 | 0.00027684 | 0.00027695 | 0.00027695 | 0.98802 | -0.084495 | 0.98801 | -0.08454 | 0.10257
16 | -0.00036525 | -8.9961e-05 | 0.00036527 | 8.7961e-05 | 2.954e-08 | -1.9993e-06 | 0.00054951 | 0.00054882 | 0.00054951 | 0.98804 | -0.084301 | 0.98813 | -0.083684 | 0.20352
17 | 0.027059 | 0.0067841 | -0.027055 | -0.0067825 | 4.1993e-06 | 1.5608e-06 | 0.040289 | 0.040289 | 0.040289 | 0.99941 | -0.0041234 | 0.99925 | -0.0052438 | 14.9218
18 | 0.024518 | 0.0061466 | -0.024507 | -0.0061428 | 1.0333e-05 | 3.8115e-06 | 0.036511 | 0.036511 | 0.036511 | 0.99925 | -0.0052438 | 0.99882 | -0.0082874 | 13.5225
19 | 0.017051 | 0.004274 | -0.017045 | -0.0042721 | 5.1655e-06 | 1.8189e-06 | 0.025402 | 0.025402 | 0.025402 | 0.99882 | -0.0082874 | 0.9985 | -0.010476 | 9.4081
20 | 0.012678 | 0.0031776 | -0.012674 | -0.0031763 | 3.8753e-06 | 1.263e-06 | 0.018893 | 0.018893 | 0.018893 | 0.9985 | -0.010476 | 0.99819 | -0.012684 | 6.9975
21 | 0.0058799 | 0.0014735 | -0.005879 | -0.0014734 | 8.5097e-07 | 9.5302e-08 | 0.0087652 | 0.0087652 | 0.0087652 | 0.99819 | -0.012684 | 0.99804 | -0.01373 | 3.2464
22 | 0.0059034 | 0.0014794 | -0.0059027 | -0.0014793 | 7.7637e-07 | 9.6508e-08 | 0.0088848 | 0.0088849 | 0.0088849 | 0.9887 | -0.079586 | 0.98856 | -0.080537 | 3.2907
23 | 0.0049744 | 0.0012409 | -0.0049736 | -0.0012409 | 7.964e-07 | 1.4177e-08 | 0.0074845 | 0.0074846 | 0.0074846 | 0.9887 | -0.079586 | 0.98853 | -0.080754 | 2.7721
24 | -0.001008 | -0.00024882 | 0.0010082 | 0.00024735 | 1.7195e-07 | -1.4694e-06 | 0.0015166 | 0.001516 | 0.0015166 | 0.98813 | -0.083684 | 0.9883 | -0.082407 | 0.5617
25 | 0.00032066 | 8.0142e-05 | -0.00032066 | -8.0365e-05 | 2.5468e-09 | -2.2326e-07 | 0.00048281 | 0.00048289 | 0.00048289 | 0.98813 | -0.083684 | 0.98812 | -0.083741 | 0.17885
26 | 0.0049736 | 0.0012409 | -0.0049724 | -0.0012409 | 1.1288e-06 | 2.0274e-08 | 0.0074846 | 0.0074848 | 0.0074848 | 0.98853 | -0.080754 | 0.9883 | -0.082407 | 2.7721

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.11031 | 0.027487

## res_load
| p_mw | q_mvar
0 | 0.0034254 | 0.00085849
1 | 0.0052545 | 0.0013169
2 | 0.0037316 | 0.00093522
3 | 0.0048246 | 0.0012092
4 | 0.014497 | 0.0036332
5 | 0.0071621 | 0.001795
6 | 0.0056915 | 0.0014264
7 | 0.0059912 | 0.0015015
8 | 0.0067194 | 0.0016841
9 | 0.004867 | 0.0012198
10 | 0.00018135 | 4.5451e-05
11 | 0.00018389 | 4.6087e-05
12 | 0.0062503 | 0.0015665
13 | 0.0027645 | 0.00069285
14 | 0.0025372 | 0.00063589
15 | 0.0074567 | 0.0018688
16 | 0.0043674 | 0.0010946
17 | 0.0067942 | 0.0017028
18 | 0.00032205 | 8.0713e-05
19 | 0.005879 | 0.0014734
20 | 0.0059027 | 0.0014794
21 | 0.0039643 | 0.00099354
22 | 0.00032066 | 8.0365e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1