## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1505-34_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1505-34_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1505-34_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1505-34_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1505-34_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1505-34_0_3_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_1505-34_0_3_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_1505-34_0_3_node_13 | 0.4 | n |  | TRUE
8 | bus_LV_1505-34_0_3_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1505-34_0_3_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_1505-34_0_3_node_17 | 0.4 | n |  | TRUE
11 | bus_LV_1505-34_0_3_node_19 | 0.4 | n |  | TRUE
12 | bus_LV_1505-34_0_3_node_15 | 0.4 | n |  | TRUE
13 | bus_LV_1505-34_0_3_node_20 | 0.4 | n |  | TRUE
14 | bus_LV_1505-34_0_3_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_1505-34_0_3_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_1505-34_0_3_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_1505-34_0_3_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_1505-34_0_3_node_37 | 0.4 | n |  | TRUE
19 | bus_LV_1505-34_0_3_node_23 | 0.4 | n |  | TRUE
20 | bus_LV_1505-34_0_3_node_24 | 0.4 | n |  | TRUE
21 | bus_LV_1505-34_0_3_node_25 | 0.4 | n |  | TRUE
22 | bus_LV_1505-34_0_3_node_32 | 0.4 | n |  | TRUE
23 | bus_LV_1505-34_0_3_node_31 | 0.4 | n |  | TRUE
24 | bus_LV_1505-34_0_3_node_36 | 0.4 | n |  | TRUE
25 | bus_LV_1505-34_0_3_node_35 | 0.4 | n |  | TRUE
26 | bus_LV_1505-34_0_3_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_1505-34_0_3_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_1505-34_0_3_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_1505-34_0_3_node_22 | 0.4 | n |  | TRUE
30 | bus_LV_1505-34_0_3_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_1505-34_0_3_node_28 | 0.4 | n |  | TRUE
32 | bus_LV_1505-34_0_3_node_29 | 0.4 | n |  | TRUE
33 | bus_LV_1505-34_0_3_node_30 | 0.4 | n |  | TRUE
34 | bus_LV_1505-34_0_3_node_33 | 0.4 | n |  | TRUE
35 | bus_LV_1505-34_0_3_node_34 | 0.4 | n |  | TRUE
36 | bus_MV_142_1_node_182 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1505-34_0_3_load_0 | 0 | 0.0019703 | 0.00049379 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1505-34_0_3_load_1 | 1 | 0.005083 | 0.0012739 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1505-34_0_3_load_2 | 2 | 0.0046338 | 0.0011613 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1505-34_0_3_load_3 | 3 | 0.0031044 | 0.00077804 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1505-34_0_3_load_4 | 4 | 0.0033616 | 0.00084251 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1505-34_0_3_load_8 | 5 | 0.0064413 | 0.0016143 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1505-34_0_3_load_5 | 6 | 0.003767 | 0.0009441 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1505-34_0_3_load_13 | 7 | 0.0072633 | 0.0018204 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1505-34_0_3_load_6 | 8 | 0.0070905 | 0.0017771 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1505-34_0_3_load_19 | 11 | 0.0024079 | 0.00060348 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1505-34_0_3_load_15 | 12 | 0.0035164 | 0.00088128 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1505-34_0_3_load_9 | 14 | 0.0042111 | 0.0010554 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1505-34_0_3_load_12 | 17 | 0.0029528 | 0.00074005 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1505-34_0_3_load_23 | 19 | 0.0085035 | 0.0021312 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1505-34_0_3_load_24 | 20 | 0.0032427 | 0.00081269 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1505-34_0_3_load_25 | 21 | 0.0037736 | 0.00094576 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1505-34_0_3_load_32 | 22 | 0.0026732 | 0.00066996 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1505-34_0_3_load_31 | 23 | 0.0034237 | 0.00085807 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1505-34_0_3_load_35 | 25 | 0.012587 | 0.0031546 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1505-34_0_3_load_16 | 26 | 0.0067264 | 0.0016858 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1505-34_0_3_load_18 | 27 | 0.0063498 | 0.0015914 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1505-34_0_3_load_21 | 28 | 0.0032255 | 0.00080839 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1505-34_0_3_load_22 | 29 | 0.0061397 | 0.0015388 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1505-34_0_3_load_26 | 30 | 0.001493 | 0.00037417 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1505-34_0_3_load_28 | 31 | 0.0045159 | 0.0011318 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1505-34_0_3_load_29 | 32 | 0.0073874 | 0.0018515 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1505-34_0_3_load_30 | 33 | 0.0051786 | 0.0012979 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1505-34_0_3_load_33 | 34 | 0.0041855 | 0.001049 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1505-34_0_3_load_34 | 35 | 0.0073818 | 0.0018501 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 1 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1505-34_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.010815 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
1 | LV_1505-34_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0085957 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
2 | LV_1505-34_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.022092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1505-34_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.01374 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
4 | LV_1505-34_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.0059724 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1505-34_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.013782 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
6 | LV_1505-34_0_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.012765 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1505-34_0_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.014359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_1505-34_0_3_line_8 | NAYY 4x150 SE | 8 | 9 | 0.016356 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1505-34_0_3_line_9 | NAYY 4x150 SE | 9 | 10 | 0.040128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1505-34_0_3_line_10 | NAYY 4x150 SE | 9 | 11 | 0.039813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1505-34_0_3_line_11 | NAYY 4x150 SE | 10 | 12 | 0.023671 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1505-34_0_3_line_12 | NAYY 4x150 SE | 11 | 13 | 0.019652 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1505-34_0_3_line_13 | NAYY 4x150 SE | 12 | 26 | 0.028944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1505-34_0_3_line_14 | NAYY 4x150 SE | 13 | 28 | 0.012406 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1505-34_0_3_line_15 | NAYY 4x150 SE | 13 | 29 | 0.01455 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1505-34_0_3_line_16 | NAYY 4x150 SE | 14 | 15 | 0.021338 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1505-34_0_3_line_17 | NAYY 4x150 SE | 15 | 16 | 0.006461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1505-34_0_3_line_18 | NAYY 4x150 SE | 16 | 22 | 0.041618 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1505-34_0_3_line_19 | NAYY 4x150 SE | 16 | 23 | 0.018694 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1505-34_0_3_line_20 | NAYY 4x150 SE | 17 | 18 | 0.038277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1505-34_0_3_line_21 | NAYY 4x150 SE | 17 | 19 | 0.049679 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1505-34_0_3_line_22 | NAYY 4x150 SE | 18 | 24 | 0.008098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1505-34_0_3_line_23 | NAYY 4x150 SE | 19 | 20 | 0.018084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1505-34_0_3_line_24 | NAYY 4x150 SE | 20 | 21 | 0.01908 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1505-34_0_3_line_25 | NAYY 4x150 SE | 22 | 25 | 0.0049251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1505-34_0_3_line_26 | NAYY 4x150 SE | 24 | 27 | 0.017678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1505-34_0_3_line_27 | NAYY 4x150 SE | 25 | 35 | 0.013547 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1505-34_0_3_line_28 | NAYY 4x150 SE | 26 | 27 | 0.018822 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1505-34_0_3_line_29 | NAYY 4x150 SE | 28 | 30 | 0.01498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1505-34_0_3_line_30 | NAYY 4x150 SE | 29 | 31 | 0.023223 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1505-34_0_3_line_31 | NAYY 4x150 SE | 31 | 32 | 0.016808 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1505-34_0_3_line_32 | NAYY 4x150 SE | 32 | 33 | 0.0068531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1505-34_0_3_line_33 | NAYY 4x150 SE | 33 | 34 | 0.021067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1505-34_0_3_line_34 | NAYY 4x150 SE | 34 | 35 | 0.016383 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1505-34_0_3_trafo_1 | 0.25 MVA 20/0.4 kV | 36 | 1 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2674409.2911 | 1204359.1616 | 2674410.6507 | 1204369.8911
1 | 2674409.2911 | 1204359.1616 | 2674408.2105 | 1204350.634
2 | 2674410.6507 | 1204369.8911 | 2674413.428 | 1204391.8083
3 | 2674408.2105 | 1204350.634 | 2674406.4831 | 1204337.0026
4 | 2674414.1788 | 1204397.7333 | 2674413.428 | 1204391.8083
5 | 2674404.7506 | 1204323.3304 | 2674406.4831 | 1204337.0026
6 | 2674414.1788 | 1204397.7333 | 2674415.1935 | 1204405.7409 | 2674414.8397 | 1204410.4211
7 | 2674404.7506 | 1204323.3304 | 2674402.9455 | 1204309.0853
8 | 2674400.8894 | 1204292.8594 | 2674402.9455 | 1204309.0853
9 | 2674362.0108 | 1204282.4911 | 2674400.8894 | 1204292.8594
10 | 2674400.8894 | 1204292.8594 | 2674439.5345 | 1204302.4299
11 | 2674362.0108 | 1204282.4911 | 2674354.0632 | 1204304.7875
12 | 2674458.6103 | 1204307.154 | 2674439.5345 | 1204302.4299
13 | 2674344.8046 | 1204332.2106 | 2674353.4569 | 1204306.4884 | 2674354.0632 | 1204304.7875
14 | 2674458.6103 | 1204307.154 | 2674470.5594 | 1204310.4916
15 | 2674458.6103 | 1204307.154 | 2674460.4831 | 1204321.5825
16 | 2674469.7321 | 1204460.977 | 2674452.1011 | 1204448.9589
17 | 2674475.0808 | 1204464.6237 | 2674469.7321 | 1204460.977
18 | 2674475.0808 | 1204464.6237 | 2674477.0333 | 1204459.9674 | 2674472.5928 | 1204424.9903 | 2674472.4462 | 1204423.687
19 | 2674475.0808 | 1204464.6237 | 2674491.6813 | 1204473.2188
20 | 2674337.4309 | 1204370.2729 | 2674368.955 | 1204391.9829
21 | 2674368.955 | 1204391.9829 | 2674362.9514 | 1204441.2975
22 | 2674337.4309 | 1204370.2729 | 2674330.8789 | 1204365.4884
23 | 2674359.0833 | 1204458.8863 | 2674359.0833 | 1204458.8863 | 2674360.4321 | 1204448.9413 | 2674362.9514 | 1204441.2975
24 | 2674359.0833 | 1204458.8863 | 2674360.0241 | 1204465.2019 | 2674363.8326 | 1204470.9529 | 2674368.6799 | 1204474.1319
25 | 2674472.4462 | 1204423.687 | 2674471.8955 | 1204418.7928
26 | 2674330.8789 | 1204365.4884 | 2674335.3089 | 1204360.4404 | 2674338.8037 | 1204350.0506
27 | 2674470.3809 | 1204405.3311 | 2674471.8955 | 1204418.7928
28 | 2674338.8037 | 1204350.0506 | 2674344.8046 | 1204332.2106
29 | 2674470.5594 | 1204310.4916 | 2674484.9873 | 1204314.5214
30 | 2674463.4722 | 1204344.6126 | 2674460.4831 | 1204321.5825
31 | 2674463.4722 | 1204344.6126 | 2674464.0522 | 1204349.0812 | 2674465.4277 | 1204361.3063
32 | 2674465.4277 | 1204361.3063 | 2674466.1939 | 1204368.1164
33 | 2674468.5492 | 1204389.051 | 2674466.1939 | 1204368.1164
34 | 2674470.3809 | 1204405.3311 | 2674468.5492 | 1204389.051

## bus_geodata
| x | y | coords
0 | 2674409.2911 | 1204359.1616
1 | 2674410.6507 | 1204369.8911
2 | 2674408.2105 | 1204350.634
3 | 2674413.428 | 1204391.8083
4 | 2674406.4831 | 1204337.0026
5 | 2674414.1788 | 1204397.7333
6 | 2674404.7506 | 1204323.3304
7 | 2674414.8397 | 1204410.4211
8 | 2674402.9455 | 1204309.0853
9 | 2674400.8894 | 1204292.8594
10 | 2674362.0108 | 1204282.4911
11 | 2674439.5345 | 1204302.4299
12 | 2674354.0632 | 1204304.7875
13 | 2674458.6103 | 1204307.154
14 | 2674452.1011 | 1204448.9589
15 | 2674469.7321 | 1204460.977
16 | 2674475.0808 | 1204464.6237
17 | 2674368.955 | 1204391.9829
18 | 2674337.4309 | 1204370.2729
19 | 2674362.9514 | 1204441.2975
20 | 2674359.0833 | 1204458.8863
21 | 2674368.6799 | 1204474.1319
22 | 2674472.4462 | 1204423.687
23 | 2674491.6813 | 1204473.2188
24 | 2674330.8789 | 1204365.4884
25 | 2674471.8955 | 1204418.7928
26 | 2674344.8046 | 1204332.2106
27 | 2674338.8037 | 1204350.0506
28 | 2674470.5594 | 1204310.4916
29 | 2674460.4831 | 1204321.5825
30 | 2674484.9873 | 1204314.5214
31 | 2674463.4722 | 1204344.6126
32 | 2674465.4277 | 1204361.3063
33 | 2674466.1939 | 1204368.1164
34 | 2674468.5492 | 1204389.051
35 | 2674470.3809 | 1204405.3311
36 | 2674411.5981 | 1204421.3502

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99906 | -0.0065238 | 0.0019703 | 0.00049379
1 | 1 | 0 | -0.13998 | -0.035097
2 | 0.99832 | -0.011633 | 0.0046338 | 0.0011613
3 | 0.99947 | -0.0037088 | 0.0031044 | 0.00077804
4 | 0.99718 | -0.019495 | 0.0033616 | 0.00084251
5 | 0.99935 | -0.0045268 | 0.0064413 | 0.0016143
6 | 0.99608 | -0.027166 | 0.003767 | 0.0009441
7 | 0.99922 | -0.0054535 | 0.0072633 | 0.0018204
8 | 0.99497 | -0.034904 | 0.0070905 | 0.0017771
9 | 0.9926 | -0.05142 | 0 | 0
10 | 0.99057 | -0.065712 | 0 | 0
11 | 0.98886 | -0.077667 | 0.0024079 | 0.00060348
12 | 0.98937 | -0.07417 | 0.0035164 | 0.00088128
13 | 0.98708 | -0.090211 | 0 | 0
14 | 0.97964 | -0.14303 | 0.0042111 | 0.0010554
15 | 0.97977 | -0.1421 | 0 | 0
16 | 0.97981 | -0.14182 | 0 | 0
17 | 0.98566 | -0.10042 | 0.0029528 | 0.00074005
18 | 0.98668 | -0.093162 | 0 | 0
19 | 0.98454 | -0.10835 | 0.0085035 | 0.0021312
20 | 0.98436 | -0.10966 | 0.0032427 | 0.00081269
21 | 0.98425 | -0.1104 | 0.0037736 | 0.00094576
22 | 0.98028 | -0.13851 | 0.0026732 | 0.00066996
23 | 0.97972 | -0.14248 | 0.0034237 | 0.00085807
24 | 0.9869 | -0.091628 | 0 | 0
25 | 0.98035 | -0.13799 | 0.012587 | 0.0031546
26 | 0.98805 | -0.083498 | 0.0067264 | 0.0016858
27 | 0.98737 | -0.088281 | 0.0063498 | 0.0015914
28 | 0.98699 | -0.090811 | 0.0032255 | 0.00080839
29 | 0.98586 | -0.098821 | 0.0061397 | 0.0015388
30 | 0.98696 | -0.09104 | 0.001493 | 0.00037417
31 | 0.98412 | -0.11114 | 0.0045159 | 0.0011318
32 | 0.98297 | -0.1193 | 0.0073874 | 0.0018515
33 | 0.98258 | -0.1221 | 0.0051786 | 0.0012979
34 | 0.98152 | -0.12962 | 0.0041855 | 0.001049
35 | 0.9808 | -0.13476 | 0.0073818 | 0.0018501
36 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.12225 | -0.030838 | 0.12236 | 0.030881 | 0.00011196 | 4.2778e-05 | 0.18215 | 0.18215 | 0.18215 | 0.99906 | -0.0065238 | 1 | 0 | 33.7319
1 | 0.12028 | 0.030344 | -0.12019 | -0.030311 | 8.6139e-05 | 3.2906e-05 | 0.17922 | 0.17922 | 0.17922 | 0.99906 | -0.0065238 | 0.99832 | -0.011633 | 33.1885
2 | 0.01682 | 0.0042165 | -0.016811 | -0.0042134 | 8.6361e-06 | 3.0319e-06 | 0.025029 | 0.025029 | 0.025029 | 1 | 0 | 0.99947 | -0.0037088 | 9.27
3 | 0.11556 | 0.02915 | -0.11543 | -0.029101 | 0.00012729 | 4.8597e-05 | 0.17231 | 0.17231 | 0.17231 | 0.99832 | -0.011633 | 0.99718 | -0.019495 | 31.9095
4 | 0.013707 | 0.0034354 | -0.013706 | -0.0034349 | 1.552e-06 | 5.1868e-07 | 0.020407 | 0.020407 | 0.020407 | 0.99947 | -0.0037088 | 0.99935 | -0.0045268 | 7.5582
5 | 0.11207 | 0.028259 | -0.11195 | -0.028213 | 0.00012034 | 4.5927e-05 | 0.1673 | 0.1673 | 0.1673 | 0.99718 | -0.019495 | 0.99608 | -0.027166 | 30.9806
6 | 0.0072643 | 0.0018206 | -0.0072633 | -0.0018204 | 9.3191e-07 | 1.9119e-07 | 0.010816 | 0.010816 | 0.010816 | 0.99935 | -0.0045268 | 0.99922 | -0.0054535 | 4.0061
7 | 0.10818 | 0.027269 | -0.10807 | -0.027224 | 0.00011709 | 4.4662e-05 | 0.16167 | 0.16167 | 0.16167 | 0.99608 | -0.027166 | 0.99497 | -0.034904 | 29.9385
8 | 0.10098 | 0.025447 | -0.10074 | -0.025358 | 0.0002329 | 8.9366e-05 | 0.15106 | 0.15106 | 0.15106 | 0.99497 | -0.034904 | 0.9926 | -0.05142 | 55.9496
9 | 0.035284 | 0.0088689 | -0.035214 | -0.0088425 | 7.0082e-05 | 2.6437e-05 | 0.052904 | 0.052904 | 0.052904 | 0.9926 | -0.05142 | 0.99057 | -0.065712 | 19.594
10 | 0.065459 | 0.016489 | -0.06522 | -0.016397 | 0.00023937 | 9.1554e-05 | 0.09816 | 0.09816 | 0.09816 | 0.9926 | -0.05142 | 0.98886 | -0.077667 | 36.3557
11 | 0.035214 | 0.0088425 | -0.035172 | -0.0088269 | 4.134e-05 | 1.5596e-05 | 0.052904 | 0.052904 | 0.052904 | 0.99057 | -0.065712 | 0.98937 | -0.07417 | 19.594
12 | 0.062812 | 0.015794 | -0.062703 | -0.015752 | 0.0001096 | 4.1901e-05 | 0.094537 | 0.094537 | 0.094537 | 0.98886 | -0.077667 | 0.98708 | -0.090211 | 35.0137
13 | 0.031656 | 0.0079456 | -0.031615 | -0.0079302 | 4.0949e-05 | 1.5378e-05 | 0.047615 | 0.047615 | 0.047615 | 0.98937 | -0.07417 | 0.98805 | -0.083498 | 17.6353
14 | 0.0047189 | 0.0011824 | -0.0047185 | -0.0011824 | 3.9176e-07 | -7.8943e-09 | 0.0071136 | 0.0071137 | 0.0071137 | 0.98708 | -0.090211 | 0.98699 | -0.090811 | 2.6347
15 | 0.057984 | 0.01457 | -0.057914 | -0.014543 | 6.9389e-05 | 2.6502e-05 | 0.087423 | 0.087424 | 0.087424 | 0.98708 | -0.090211 | 0.98586 | -0.098821 | 32.3791
16 | -0.0042111 | -0.0010554 | 0.0042117 | 0.0010554 | 5.4475e-07 | -5.9167e-08 | 0.0063965 | 0.0063964 | 0.0063965 | 0.97964 | -0.14303 | 0.97977 | -0.1421 | 2.3691
17 | -0.0042117 | -0.0010554 | 0.0042118 | 0.0010553 | 1.6495e-07 | -1.7931e-08 | 0.0063964 | 0.0063963 | 0.0063964 | 0.97977 | -0.1421 | 0.97981 | -0.14182 | 2.369
18 | -0.0076359 | -0.0019133 | 0.0076394 | 0.0019141 | 3.4922e-06 | 8.1873e-07 | 0.011596 | 0.011596 | 0.011596 | 0.97981 | -0.14182 | 0.98028 | -0.13851 | 4.2949
19 | 0.0034241 | 0.00085796 | -0.0034237 | -0.00085807 | 3.1542e-07 | -1.1411e-07 | 0.0052 | 0.0052 | 0.0052 | 0.97981 | -0.14182 | 0.97972 | -0.14248 | 1.9259
20 | -0.018491 | -0.0046358 | 0.01851 | 0.0046424 | 1.8614e-05 | 6.6707e-06 | 0.027916 | 0.027916 | 0.027916 | 0.98566 | -0.10042 | 0.98668 | -0.093162 | 10.3394
21 | 0.015539 | 0.0038957 | -0.015521 | -0.0038898 | 1.7059e-05 | 5.9288e-06 | 0.023458 | 0.023459 | 0.023459 | 0.98566 | -0.10042 | 0.98454 | -0.10835 | 8.6884
22 | -0.01851 | -0.0046424 | 0.018514 | 0.0046439 | 3.938e-06 | 1.4111e-06 | 0.027916 | 0.027916 | 0.027916 | 0.98668 | -0.093162 | 0.9869 | -0.091628 | 10.3393
23 | 0.007018 | 0.0017586 | -0.0070167 | -0.0017584 | 1.2696e-06 | 2.5836e-07 | 0.010607 | 0.010607 | 0.010607 | 0.98454 | -0.10835 | 0.98436 | -0.10966 | 3.9285
24 | 0.003774 | 0.00094567 | -0.0037736 | -0.00094576 | 3.875e-07 | -9.348e-08 | 0.005705 | 0.0057051 | 0.0057051 | 0.98436 | -0.10966 | 0.98425 | -0.1104 | 2.113
25 | -0.010313 | -0.0025841 | 0.010313 | 0.0025843 | 7.5308e-07 | 2.2755e-07 | 0.015654 | 0.015654 | 0.015654 | 0.98028 | -0.13851 | 0.98035 | -0.13799 | 5.7977
26 | -0.018514 | -0.0046439 | 0.018522 | 0.0046469 | 8.5966e-06 | 3.0804e-06 | 0.027916 | 0.027916 | 0.027916 | 0.9869 | -0.091628 | 0.98737 | -0.088281 | 10.3393
27 | -0.0229 | -0.0057389 | 0.02291 | 0.0057426 | 1.0213e-05 | 3.7571e-06 | 0.034759 | 0.034759 | 0.034759 | 0.98035 | -0.13799 | 0.9808 | -0.13476 | 12.8736
28 | 0.024889 | 0.0062444 | -0.024872 | -0.0062383 | 1.6504e-05 | 6.1066e-06 | 0.037485 | 0.037485 | 0.037485 | 0.98805 | -0.083498 | 0.98737 | -0.088281 | 13.8835
29 | 0.001493 | 0.000374 | -0.001493 | -0.00037417 | 4.7359e-08 | -1.7323e-07 | 0.0022508 | 0.0022509 | 0.0022509 | 0.98699 | -0.090811 | 0.98696 | -0.09104 | 0.83367
30 | 0.051775 | 0.013004 | -0.051686 | -0.012971 | 8.8519e-05 | 3.375e-05 | 0.078157 | 0.078157 | 0.078157 | 0.98586 | -0.098821 | 0.98412 | -0.11114 | 28.9469
31 | 0.04717 | 0.011839 | -0.047117 | -0.011819 | 5.3362e-05 | 2.0311e-05 | 0.071328 | 0.071329 | 0.071329 | 0.98412 | -0.11114 | 0.98297 | -0.1193 | 26.418
32 | 0.039729 | 0.0099671 | -0.039714 | -0.0099612 | 1.547e-05 | 5.863e-06 | 0.060145 | 0.060146 | 0.060146 | 0.98297 | -0.1193 | 0.98258 | -0.1221 | 22.2761
33 | 0.034535 | 0.0086633 | -0.034499 | -0.0086498 | 3.5961e-05 | 1.3565e-05 | 0.052303 | 0.052303 | 0.052303 | 0.98258 | -0.1221 | 0.98152 | -0.12962 | 19.3715
34 | 0.030314 | 0.0076008 | -0.030292 | -0.0075927 | 2.1592e-05 | 8.0977e-06 | 0.045958 | 0.045958 | 0.045958 | 0.98152 | -0.12962 | 0.9808 | -0.13476 | 17.0215

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.14507 | 0.036371

## res_load
| p_mw | q_mvar
0 | 0.0019703 | 0.00049379
1 | 0.005083 | 0.0012739
2 | 0.0046338 | 0.0011613
3 | 0.0031044 | 0.00077804
4 | 0.0033616 | 0.00084251
5 | 0.0064413 | 0.0016143
6 | 0.003767 | 0.0009441
7 | 0.0072633 | 0.0018204
8 | 0.0070905 | 0.0017771
9 | 0.0024079 | 0.00060348
10 | 0.0035164 | 0.00088128
11 | 0.0042111 | 0.0010554
12 | 0.0029528 | 0.00074005
13 | 0.0085035 | 0.0021312
14 | 0.0032427 | 0.00081269
15 | 0.0037736 | 0.00094576
16 | 0.0026732 | 0.00066996
17 | 0.0034237 | 0.00085807
18 | 0.012587 | 0.0031546
19 | 0.0067264 | 0.0016858
20 | 0.0063498 | 0.0015914
21 | 0.0032255 | 0.00080839
22 | 0.0061397 | 0.0015388
23 | 0.001493 | 0.00037417
24 | 0.0045159 | 0.0011318
25 | 0.0073874 | 0.0018515
26 | 0.0051786 | 0.0012979
27 | 0.0041855 | 0.001049
28 | 0.0073818 | 0.0018501

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1