## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1505-36_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1505-36_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1505-36_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1505-36_0_3_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1505-36_0_3_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1505-36_0_3_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_1505-36_0_3_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_1505-36_0_3_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_1505-36_0_3_node_28 | 0.4 | n |  | TRUE
9 | bus_LV_1505-36_0_3_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_1505-36_0_3_node_16 | 0.4 | n |  | TRUE
11 | bus_LV_1505-36_0_3_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_1505-36_0_3_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_1505-36_0_3_node_25 | 0.4 | n |  | TRUE
14 | bus_LV_1505-36_0_3_node_26 | 0.4 | n |  | TRUE
15 | bus_LV_1505-36_0_3_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_1505-36_0_3_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_1505-36_0_3_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_1505-36_0_3_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_1505-36_0_3_node_27 | 0.4 | n |  | TRUE
20 | bus_LV_1505-36_0_3_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_1505-36_0_3_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_1505-36_0_3_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_1505-36_0_3_node_23 | 0.4 | n |  | TRUE
24 | bus_LV_1505-36_0_3_node_24 | 0.4 | n |  | TRUE
25 | bus_LV_1505-36_0_3_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_1505-36_0_3_node_21 | 0.4 | n |  | TRUE
27 | bus_MV_142_1_node_312 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1505-36_0_3_load_0 | 0 | 0.0069568 | 0.0017435 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1505-36_0_3_load_1 | 1 | 0.016906 | 0.004237 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1505-36_0_3_load_3 | 2 | 0.0075962 | 0.0019038 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1505-36_0_3_load_4 | 3 | 0.0029467 | 0.00073851 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1505-36_0_3_load_6 | 5 | 0.010028 | 0.0025132 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1505-36_0_3_load_7 | 6 | 0.012291 | 0.0030805 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1505-36_0_3_load_8 | 7 | 0.0098725 | 0.0024743 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1505-36_0_3_load_28 | 8 | 0.0089555 | 0.0022445 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1505-36_0_3_load_9 | 9 | 0.0044361 | 0.0011118 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1505-36_0_3_load_11 | 12 | 0.00063727 | 0.00015972 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1505-36_0_3_load_25 | 13 | 0.00024944 | 6.2515e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1505-36_0_3_load_26 | 14 | 0.0011989 | 0.00030046 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1505-36_0_3_load_12 | 15 | 0.012083 | 0.0030284 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1505-36_0_3_load_15 | 18 | 0.0046416 | 0.0011633 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1505-36_0_3_load_27 | 19 | 0.0099925 | 0.0025044 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1505-36_0_3_load_17 | 21 | 0.00067396 | 0.00016891 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1505-36_0_3_load_18 | 22 | 0.019826 | 0.004969 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1505-36_0_3_load_24 | 24 | 0.0065658 | 0.0016455 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1505-36_0_3_load_20 | 25 | 0.012792 | 0.0032059 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1505-36_0_3_load_21 | 26 | 0.017569 | 0.0044033 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 8 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1505-36_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.02551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1505-36_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.051143 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1505-36_0_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.017626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1505-36_0_3_line_3 | NAYY 4x150 SE | 3 | 4 | 0.050693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1505-36_0_3_line_4 | NAYY 4x150 SE | 4 | 5 | 0.013067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1505-36_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.055948 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1505-36_0_3_line_6 | NAYY 4x150 SE | 6 | 7 | 0.032526 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1505-36_0_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.12787 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1505-36_0_3_line_8 | NAYY 4x150 SE | 7 | 9 | 0.051879 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1505-36_0_3_line_9 | NAYY 4x150 SE | 8 | 10 | 0.23174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
10 | LV_1505-36_0_3_line_10 | NAYY 4x150 SE | 9 | 11 | 0.016717 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1505-36_0_3_line_11 | NAYY 4x150 SE | 10 | 21 | 0.12429 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1505-36_0_3_line_12 | NAYY 4x150 SE | 10 | 22 | 0.03202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1505-36_0_3_line_13 | NAYY 4x150 SE | 10 | 17 | 0.16105 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
14 | LV_1505-36_0_3_line_14 | NAYY 4x150 SE | 11 | 12 | 0.064775 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1505-36_0_3_line_15 | NAYY 4x150 SE | 12 | 13 | 0.30832 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1505-36_0_3_line_16 | NAYY 4x150 SE | 13 | 14 | 0.0037489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1505-36_0_3_line_17 | NAYY 4x150 SE | 15 | 16 | 0.035107 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1505-36_0_3_line_18 | NAYY 4x150 SE | 16 | 17 | 0.14507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
19 | LV_1505-36_0_3_line_19 | NAYY 4x150 SE | 16 | 18 | 0.030068 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
20 | LV_1505-36_0_3_line_20 | NAYY 4x150 SE | 17 | 19 | 0.10828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1505-36_0_3_line_21 | NAYY 4x150 SE | 18 | 20 | 0.0056842 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1505-36_0_3_line_22 | NAYY 4x150 SE | 20 | 25 | 0.02827 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1505-36_0_3_line_23 | NAYY 4x150 SE | 20 | 26 | 0.088632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1505-36_0_3_line_24 | NAYY 4x150 SE | 22 | 23 | 0.0075188 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1505-36_0_3_line_25 | NAYY 4x150 SE | 23 | 24 | 0.024952 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1505-36_0_3_trafo_28 | 0.25 MVA 20/0.4 kV | 27 | 8 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2672667.9166 | 1204748.1 | 2672687.4566 | 1204754.2835 | 2672691.7929 | 1204756.8021
1 | 2672691.7929 | 1204756.8021 | 2672698.093 | 1204760.4612 | 2672703.8284 | 1204778.6423 | 2672712.4434 | 1204796.4915 | 2672715.1972 | 1204800.633
2 | 2672715.1972 | 1204800.633 | 2672724.9569 | 1204815.311
3 | 2672765.8167 | 1204845.316 | 2672724.9569 | 1204815.311
4 | 2672765.8167 | 1204845.316 | 2672774.645 | 1204835.662
5 | 2672765.8167 | 1204845.316 | 2672800.0484 | 1204870.4486 | 2672809.8715 | 1204879.6817
6 | 2672809.8715 | 1204879.6817 | 2672825.9216 | 1204894.7679 | 2672834.7819 | 1204900.3991
7 | 2672809.8715 | 1204879.6817 | 2672894.0295 | 1204783.4076
8 | 2672834.7819 | 1204900.3991 | 2672846.3793 | 1204907.7699 | 2672855.4984 | 1204915.4303 | 2672876.4585 | 1204931.1974
9 | 2672894.0295 | 1204783.4076 | 2673121.5211 | 1204739.2607
10 | 2672888.1075 | 1204943.1786 | 2672876.8618 | 1204931.5008 | 2672876.4585 | 1204931.1974
11 | 2673121.5211 | 1204739.2607 | 2673127.3849 | 1204731.9502 | 2673135.8043 | 1204727.1726 | 2673149.4859 | 1204726.3173 | 2673168.4318 | 1204729.1956 | 2673185.0751 | 1204736.2149 | 2673199.3656 | 1204744.0171 | 2673210.1373 | 1204747.807 | 2673220.6144 | 1204750.1813 | 2673236.4923 | 1204753.2223
12 | 2673121.5211 | 1204739.2607 | 2673128.4669 | 1204751.6868 | 2673135.1631 | 1204763.3649 | 2673138.0675 | 1204766.566
13 | 2673179.288 | 1204588.9307 | 2673121.5211 | 1204739.2607
14 | 2672888.1075 | 1204943.1786 | 2672881.3522 | 1204945.6643 | 2672872.0501 | 1204946.7626 | 2672858.5808 | 1204947.1097 | 2672823.6734 | 1204948.1068
15 | 2672823.6734 | 1204948.1068 | 2672723.2795 | 1205239.6195
16 | 2672725.2796 | 1205242.7902 | 2672723.2795 | 1205239.6195
17 | 2673043.1574 | 1204540.0344 | 2673041.5259 | 1204544.6618 | 2673042.8687 | 1204551.1934 | 2673050.3364 | 1204558.3002 | 2673059.419 | 1204567.9108
18 | 2673043.1574 | 1204540.0344 | 2673070.4665 | 1204547.1506 | 2673100.6771 | 1204554.6471 | 2673121.8337 | 1204565.913 | 2673147.4183 | 1204579.0232 | 2673179.288 | 1204588.9307
19 | 2673043.1574 | 1204540.0344 | 2673019.0023 | 1204522.128
20 | 2673179.288 | 1204588.9307 | 2673179.2256 | 1204584.0937 | 2673177.6377 | 1204580.8166 | 2673152.5783 | 1204544.0981 | 2673137.4854 | 1204526.6136 | 2673117.4872 | 1204510.2031 | 2673112.3297 | 1204506.4496
21 | 2673013.9018 | 1204519.7531 | 2673017.4776 | 1204520.9976 | 2673019.0023 | 1204522.128
22 | 2673013.9018 | 1204519.7531 | 2673009.3901 | 1204514.1723 | 2672995.2947 | 1204498.4348
23 | 2673013.9018 | 1204519.7531 | 2673001.3791 | 1204515.3974 | 2672981.8474 | 1204506.2309 | 2672957.0705 | 1204479.8897 | 2672943.7493 | 1204468.334
24 | 2673143.1198 | 1204772.1344 | 2673138.0675 | 1204766.566
25 | 2673143.1198 | 1204772.1344 | 2673148.1492 | 1204777.6661 | 2673163.8648 | 1204785.3091

## bus_geodata
| x | y | coords
0 | 2672667.9166 | 1204748.1
1 | 2672691.7929 | 1204756.8021
2 | 2672715.1972 | 1204800.633
3 | 2672724.9569 | 1204815.311
4 | 2672765.8167 | 1204845.316
5 | 2672774.645 | 1204835.662
6 | 2672809.8715 | 1204879.6817
7 | 2672834.7819 | 1204900.3991
8 | 2672894.0295 | 1204783.4076
9 | 2672876.4585 | 1204931.1974
10 | 2673121.5211 | 1204739.2607
11 | 2672888.1075 | 1204943.1786
12 | 2672823.6734 | 1204948.1068
13 | 2672723.2795 | 1205239.6195
14 | 2672725.2796 | 1205242.7902
15 | 2673059.419 | 1204567.9108
16 | 2673043.1574 | 1204540.0344
17 | 2673179.288 | 1204588.9307
18 | 2673019.0023 | 1204522.128
19 | 2673112.3297 | 1204506.4496
20 | 2673013.9018 | 1204519.7531
21 | 2673236.4923 | 1204753.2223
22 | 2673138.0675 | 1204766.566
23 | 2673143.1198 | 1204772.1344
24 | 2673163.8648 | 1204785.3091
25 | 2672995.2947 | 1204498.4348
26 | 2672943.7493 | 1204468.334
27 | 2673143.1198 | 1204772.1344

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97742 | -0.15871 | 0.0069568 | 0.0017435
1 | 0.97768 | -0.15686 | 0.016906 | 0.004237
2 | 0.97946 | -0.14413 | 0.0075962 | 0.0019038
3 | 0.98026 | -0.13837 | 0.0029467 | 0.00073851
4 | 0.98281 | -0.12029 | 0 | 0
5 | 0.98262 | -0.12165 | 0.010028 | 0.0025132
6 | 0.98642 | -0.094691 | 0.012291 | 0.0030805
7 | 0.98565 | -0.10018 | 0.0098725 | 0.0024743
8 | 1 | 0 | -0.16132 | -0.040637
9 | 0.98516 | -0.10368 | 0.0044361 | 0.0011118
10 | 0.98577 | -0.098859 | 0 | 0
11 | 0.98511 | -0.10404 | 0 | 0
12 | 0.98492 | -0.10545 | 0.00063727 | 0.00015972
13 | 0.98427 | -0.1101 | 0.00024944 | 6.2515e-05
14 | 0.98427 | -0.11015 | 0.0011989 | 0.00030046
15 | 0.97341 | -0.18669 | 0.012083 | 0.0030284
16 | 0.97403 | -0.18222 | 0 | 0
17 | 0.97904 | -0.14645 | 0 | 0
18 | 0.97326 | -0.18776 | 0.0046416 | 0.0011633
19 | 0.97746 | -0.15774 | 0.0099925 | 0.0025044
20 | 0.973 | -0.18958 | 0 | 0
21 | 0.98565 | -0.099727 | 0.00067396 | 0.00016891
22 | 0.98455 | -0.10755 | 0.019826 | 0.004969
23 | 0.98447 | -0.10806 | 0 | 0
24 | 0.98424 | -0.10975 | 0.0065658 | 0.0016455
25 | 0.97247 | -0.1934 | 0.012792 | 0.0032059
26 | 0.97072 | -0.20604 | 0.017569 | 0.0044033
27 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0069568 | -0.0017435 | 0.0069586 | 0.0017439 | 1.7855e-06 | 3.6692e-07 | 0.010591 | 0.010591 | 0.010591 | 0.97742 | -0.15871 | 0.97768 | -0.15686 | 3.9226
1 | -0.023865 | -0.0059809 | 0.023907 | 0.0059965 | 4.2101e-05 | 1.555e-05 | 0.036322 | 0.036321 | 0.036322 | 0.97768 | -0.15686 | 0.97946 | -0.14413 | 13.4524
2 | -0.031503 | -0.0079003 | 0.031528 | 0.0079097 | 2.5196e-05 | 9.4686e-06 | 0.047862 | 0.047862 | 0.047862 | 0.97946 | -0.14413 | 0.98026 | -0.13837 | 17.7265
3 | -0.034475 | -0.0086482 | 0.034561 | 0.0086809 | 8.6638e-05 | 3.2682e-05 | 0.052334 | 0.052334 | 0.052334 | 0.98026 | -0.13837 | 0.98281 | -0.12029 | 19.3831
4 | 0.01003 | 0.0025137 | -0.010028 | -0.0025132 | 1.8802e-06 | 5.5761e-07 | 0.015185 | 0.015185 | 0.015185 | 0.98281 | -0.12029 | 0.98262 | -0.12165 | 5.6242
5 | -0.044591 | -0.011195 | 0.04475 | 0.011255 | 0.00015916 | 6.0503e-05 | 0.06752 | 0.067519 | 0.06752 | 0.98281 | -0.12029 | 0.98642 | -0.094691 | 25.0072
6 | 0.016411 | 0.0041092 | -0.016399 | -0.0041049 | 1.2437e-05 | 4.3688e-06 | 0.024755 | 0.024755 | 0.024755 | 0.98642 | -0.094691 | 0.98565 | -0.10018 | 9.1685
7 | -0.073452 | -0.018445 | 0.074432 | 0.01882 | 0.00097985 | 0.00037521 | 0.11082 | 0.11081 | 0.11082 | 0.98642 | -0.094691 | 1 | 0 | 41.0427
8 | 0.0065263 | 0.0016306 | -0.0065231 | -0.00163 | 3.1414e-06 | 5.4734e-07 | 0.0098507 | 0.009851 | 0.009851 | 0.98565 | -0.10018 | 0.98516 | -0.10368 | 3.6485
9 | 0.086089 | 0.021816 | -0.084901 | -0.021365 | 0.0011881 | 0.00045096 | 0.12819 | 0.12819 | 0.12819 | 1 | 0 | 0.98577 | -0.098859 | 23.7387
10 | 0.002087 | 0.00051824 | -0.0020869 | -0.00051841 | 1.0354e-07 | -1.7302e-07 | 0.0031506 | 0.0031506 | 0.0031506 | 0.98516 | -0.10368 | 0.98511 | -0.10404 | 1.1669
11 | 0.00067404 | 0.00016736 | -0.00067396 | -0.00016891 | 8.0243e-08 | -1.5534e-06 | 0.0010169 | 0.0010175 | 0.0010175 | 0.98577 | -0.098859 | 0.98565 | -0.099727 | 0.37684
12 | 0.026426 | 0.0066267 | -0.026394 | -0.0066149 | 3.1795e-05 | 1.1821e-05 | 0.039891 | 0.039891 | 0.039891 | 0.98577 | -0.098859 | 0.98455 | -0.10755 | 14.7746
13 | 0.057801 | 0.014571 | -0.057418 | -0.014428 | 0.00038278 | 0.00014315 | 0.087281 | 0.087282 | 0.087282 | 0.98577 | -0.098859 | 0.97904 | -0.14645 | 16.1634
14 | 0.0020869 | 0.00051841 | -0.0020865 | -0.00051908 | 4.0126e-07 | -6.702e-07 | 0.0031506 | 0.0031509 | 0.0031509 | 0.98511 | -0.10404 | 0.98492 | -0.10545 | 1.167
15 | 0.0014492 | 0.00035937 | -0.0014483 | -0.00036293 | 9.2172e-07 | -3.5667e-06 | 0.0021881 | 0.0021895 | 0.0021895 | 0.98492 | -0.10545 | 0.98427 | -0.1101 | 0.81093
16 | 0.0011989 | 0.00030042 | -0.0011989 | -0.00030046 | 7.6843e-09 | -4.4692e-08 | 0.0018124 | 0.0018124 | 0.0018124 | 0.98427 | -0.1101 | 0.98427 | -0.11015 | 0.67127
17 | -0.012083 | -0.0030284 | 0.012091 | 0.0030308 | 7.4744e-06 | 2.4381e-06 | 0.018471 | 0.018471 | 0.018471 | 0.97341 | -0.18669 | 0.97403 | -0.18222 | 6.8413
18 | -0.047175 | -0.011832 | 0.04741 | 0.011919 | 0.0002351 | 8.6793e-05 | 0.072072 | 0.072071 | 0.072072 | 0.97403 | -0.18222 | 0.97904 | -0.14645 | 13.3467
19 | 0.035084 | 0.0088016 | -0.035057 | -0.008792 | 2.6953e-05 | 9.6188e-06 | 0.053601 | 0.053601 | 0.053601 | 0.97403 | -0.18222 | 0.97326 | -0.18776 | 9.9262
20 | 0.010008 | 0.002509 | -0.0099925 | -0.0025044 | 1.5635e-05 | 4.6539e-06 | 0.015211 | 0.015212 | 0.015212 | 0.97904 | -0.14645 | 0.97746 | -0.15774 | 5.634
21 | 0.030416 | 0.0076287 | -0.030408 | -0.0076258 | 7.6709e-06 | 2.8797e-06 | 0.046505 | 0.046505 | 0.046505 | 0.97326 | -0.18776 | 0.973 | -0.18958 | 17.224
22 | 0.012798 | 0.0032082 | -0.012792 | -0.0032059 | 6.7581e-06 | 2.2483e-06 | 0.019573 | 0.019573 | 0.019573 | 0.973 | -0.18958 | 0.97247 | -0.1934 | 7.2493
23 | 0.01761 | 0.0044176 | -0.017569 | -0.0044033 | 4.0115e-05 | 1.4331e-05 | 0.026932 | 0.026932 | 0.026932 | 0.973 | -0.18958 | 0.97072 | -0.20604 | 9.9749
24 | 0.0065678 | 0.0016459 | -0.0065673 | -0.0016458 | 4.6229e-07 | 8.2193e-08 | 0.0099263 | 0.0099263 | 0.0099263 | 0.98455 | -0.10755 | 0.98447 | -0.10806 | 3.6764
25 | 0.0065673 | 0.0016458 | -0.0065658 | -0.0016455 | 1.5342e-06 | 2.7287e-07 | 0.0099263 | 0.0099264 | 0.0099264 | 0.98447 | -0.10806 | 0.98424 | -0.10975 | 3.6765

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.17028 | 0.042881

## res_load
| p_mw | q_mvar
0 | 0.0069568 | 0.0017435
1 | 0.016906 | 0.004237
2 | 0.0075962 | 0.0019038
3 | 0.0029467 | 0.00073851
4 | 0.010028 | 0.0025132
5 | 0.012291 | 0.0030805
6 | 0.0098725 | 0.0024743
7 | 0.0089555 | 0.0022445
8 | 0.0044361 | 0.0011118
9 | 0.00063727 | 0.00015972
10 | 0.00024944 | 6.2515e-05
11 | 0.0011989 | 0.00030046
12 | 0.012083 | 0.0030284
13 | 0.0046416 | 0.0011633
14 | 0.0099925 | 0.0025044
15 | 0.00067396 | 0.00016891
16 | 0.019826 | 0.004969
17 | 0.0065658 | 0.0016455
18 | 0.012792 | 0.0032059
19 | 0.017569 | 0.0044033

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1