## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1506-3_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1506-3_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1506-3_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1506-3_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1506-3_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1506-3_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1506-3_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1506-3_0_3_node_17 | 0.4 | n |  | TRUE
8 | bus_LV_1506-3_0_3_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_1506-3_0_3_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_1506-3_0_3_node_18 | 0.4 | n |  | TRUE
11 | bus_LV_1506-3_0_3_node_21 | 0.4 | n |  | TRUE
12 | bus_LV_1506-3_0_3_node_12 | 0.4 | n |  | TRUE
13 | bus_LV_1506-3_0_3_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_1506-3_0_3_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_1506-3_0_3_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_1506-3_0_3_node_16 | 0.4 | n |  | TRUE
17 | bus_LV_1506-3_0_3_node_20 | 0.4 | n |  | TRUE
18 | bus_LV_1506-3_0_3_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_1506-3_0_3_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_1506-3_0_3_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_1506-3_0_3_node_22 | 0.4 | n |  | TRUE
22 | bus_LV_1506-3_0_3_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_1506-3_0_3_node_24 | 0.4 | n |  | TRUE
24 | bus_LV_1506-3_0_3_node_23 | 0.4 | n |  | TRUE
25 | bus_MV_143_0_node_140 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1506-3_0_3_load_0 | 0 | 0.027208 | 0.006819 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1506-3_0_3_load_1 | 1 | 0.0091911 | 0.0023035 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1506-3_0_3_load_3 | 3 | 0.027228 | 0.006824 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1506-3_0_3_load_4 | 4 | 0.0076186 | 0.0019094 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1506-3_0_3_load_5 | 5 | 0.0030754 | 0.00077076 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1506-3_0_3_load_17 | 7 | 0.013015 | 0.0032618 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1506-3_0_3_load_7 | 8 | 0.012621 | 0.0031631 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1506-3_0_3_load_8 | 9 | 0.013865 | 0.003475 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1506-3_0_3_load_21 | 11 | 0.0039059 | 0.0009789 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1506-3_0_3_load_12 | 12 | 0.0036635 | 0.00091815 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1506-3_0_3_load_14 | 13 | 0.0036634 | 0.00091815 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1506-3_0_3_load_10 | 14 | 0.0032884 | 0.00082415 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1506-3_0_3_load_15 | 15 | 0.004895 | 0.0012268 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1506-3_0_3_load_16 | 16 | 0.0051644 | 0.0012943 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1506-3_0_3_load_20 | 17 | 0.0068909 | 0.001727 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1506-3_0_3_load_9 | 18 | 0.0036289 | 0.00090948 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1506-3_0_3_load_11 | 19 | 0.0036253 | 0.00090858 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1506-3_0_3_load_13 | 20 | 0.0030767 | 0.00077109 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1506-3_0_3_load_22 | 21 | 0.0080582 | 0.0020196 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1506-3_0_3_load_24 | 23 | 0.0034958 | 0.00087613 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1506-3_0_3_load_23 | 24 | 0.0094254 | 0.0023622 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 6 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1506-3_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.033363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1506-3_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.02269 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1506-3_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.001685 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1506-3_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.0040755 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1506-3_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.037775 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1506-3_0_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.02731 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1506-3_0_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.016104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1506-3_0_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.017846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1506-3_0_3_line_8 | NAYY 4x150 SE | 6 | 9 | 0.020576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1506-3_0_3_line_9 | NAYY 4x150 SE | 7 | 10 | 0.031414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1506-3_0_3_line_10 | NAYY 4x150 SE | 9 | 11 | 0.039817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1506-3_0_3_line_11 | NAYY 4x150 SE | 10 | 22 | 0.0099647 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1506-3_0_3_line_12 | NAYY 4x150 SE | 11 | 21 | 0.011176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1506-3_0_3_line_13 | NAYY 4x150 SE | 11 | 20 | 0.0096024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1506-3_0_3_line_14 | NAYY 4x150 SE | 12 | 13 | 0.011105 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1506-3_0_3_line_15 | NAYY 4x150 SE | 12 | 14 | 0.0059093 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1506-3_0_3_line_16 | NAYY 4x150 SE | 13 | 15 | 0.017122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1506-3_0_3_line_17 | NAYY 4x150 SE | 14 | 18 | 0.014404 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1506-3_0_3_line_18 | NAYY 4x150 SE | 15 | 16 | 0.0065494 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1506-3_0_3_line_19 | NAYY 4x150 SE | 16 | 17 | 0.01358 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1506-3_0_3_line_20 | NAYY 4x150 SE | 18 | 19 | 0.010575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1506-3_0_3_line_21 | NAYY 4x150 SE | 19 | 20 | 0.0047407 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1506-3_0_3_line_22 | NAYY 4x150 SE | 22 | 23 | 0.030942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1506-3_0_3_line_23 | NAYY 4x150 SE | 23 | 24 | 0.019449 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1506-3_0_3_trafo_6 | 0.25 MVA 20/0.4 kV | 25 | 6 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2668245.2611 | 1201082.1227 | 2668277.4249 | 1201090.9875
1 | 2668223.3868 | 1201076.0939 | 2668245.2611 | 1201082.1227
2 | 2668279.0493 | 1201091.4352 | 2668277.4249 | 1201090.9875
3 | 2668223.3868 | 1201076.0939 | 2668221.4755 | 1201079.6934
4 | 2668223.3868 | 1201076.0939 | 2668242.9759 | 1201043.7952
5 | 2668305.3785 | 1201098.6883 | 2668302.419 | 1201097.8762 | 2668279.0493 | 1201091.4352
6 | 2668242.9759 | 1201043.7952 | 2668251.3271 | 1201030.0257
7 | 2668305.3785 | 1201098.6883 | 2668303.4733 | 1201104.8703 | 2668301.1804 | 1201111.0033 | 2668303.1701 | 1201115.4065
8 | 2668305.3785 | 1201098.6883 | 2668316.1842 | 1201101.6691 | 2668321.3263 | 1201101.3277 | 2668325.2888 | 1201099.8972
9 | 2668267.6175 | 1201003.166 | 2668251.3271 | 1201030.0257
10 | 2668325.2888 | 1201099.8972 | 2668362.8223 | 1201113.1862
11 | 2668273.7766 | 1200997.7664 | 2668271.4967 | 1200996.7731 | 2668267.6175 | 1201003.166
12 | 2668366.6433 | 1201102.6835 | 2668364.3855 | 1201108.9024 | 2668362.8223 | 1201113.1862
13 | 2668359.5305 | 1201122.2068 | 2668362.8223 | 1201113.1862
14 | 2668347.3771 | 1201155.6981 | 2668343.6911 | 1201166.1738
15 | 2668349.3427 | 1201150.1253 | 2668349.2106 | 1201150.4872 | 2668347.3771 | 1201155.6981
16 | 2668338.008 | 1201182.3254 | 2668343.6911 | 1201166.1738
17 | 2668349.3427 | 1201150.1253 | 2668354.2803 | 1201136.5943
18 | 2668338.008 | 1201182.3254 | 2668335.8341 | 1201188.5036
19 | 2668331.3269 | 1201201.3134 | 2668335.8341 | 1201188.5036
20 | 2668357.9054 | 1201126.6602 | 2668354.2803 | 1201136.5943
21 | 2668359.5305 | 1201122.2068 | 2668357.9054 | 1201126.6602
22 | 2668273.7766 | 1200997.7664 | 2668277.0487 | 1200999.2047 | 2668288.6923 | 1201003.4847 | 2668303.068 | 1201007.6347
23 | 2668321.8208 | 1201012.7823 | 2668314.838 | 1201011.0325 | 2668303.068 | 1201007.6347

## bus_geodata
| x | y | coords
0 | 2668245.2611 | 1201082.1227
1 | 2668277.4249 | 1201090.9875
2 | 2668223.3868 | 1201076.0939
3 | 2668279.0493 | 1201091.4352
4 | 2668221.4755 | 1201079.6934
5 | 2668242.9759 | 1201043.7952
6 | 2668305.3785 | 1201098.6883
7 | 2668251.3271 | 1201030.0257
8 | 2668303.1701 | 1201115.4065
9 | 2668325.2888 | 1201099.8972
10 | 2668267.6175 | 1201003.166
11 | 2668362.8223 | 1201113.1862
12 | 2668347.3771 | 1201155.6981
13 | 2668343.6911 | 1201166.1738
14 | 2668349.3427 | 1201150.1253
15 | 2668338.008 | 1201182.3254
16 | 2668335.8341 | 1201188.5036
17 | 2668331.3269 | 1201201.3134
18 | 2668354.2803 | 1201136.5943
19 | 2668357.9054 | 1201126.6602
20 | 2668359.5306 | 1201122.2068
21 | 2668366.6433 | 1201102.6835
22 | 2668273.7766 | 1200997.7664
23 | 2668303.068 | 1201007.6347
24 | 2668321.8208 | 1201012.7823
25 | 2668303.1701 | 1201115.4065

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99283 | -0.050182 | 0.027208 | 0.006819
1 | 0.99589 | -0.028678 | 0.0091911 | 0.0023035
2 | 0.99163 | -0.058611 | 0 | 0
3 | 0.99607 | -0.02744 | 0.027228 | 0.006824
4 | 0.99159 | -0.058926 | 0.0076186 | 0.0019094
5 | 0.99005 | -0.069756 | 0.0030754 | 0.00077076
6 | 1 | 0 | -0.17845 | -0.044659
7 | 0.98945 | -0.074013 | 0.013015 | 0.0032618
8 | 0.99968 | -0.0022488 | 0.012621 | 0.0031631
9 | 0.99812 | -0.013114 | 0.013865 | 0.003475
10 | 0.98886 | -0.078156 | 0 | 0
11 | 0.99527 | -0.033064 | 0.0039059 | 0.0009789
12 | 0.99326 | -0.047194 | 0.0036635 | 0.00091815
13 | 0.99294 | -0.049511 | 0.0036634 | 0.00091815
14 | 0.99347 | -0.045743 | 0.0032884 | 0.00082415
15 | 0.99252 | -0.052451 | 0.004895 | 0.0012268
16 | 0.99241 | -0.053251 | 0.0051644 | 0.0012943
17 | 0.99227 | -0.0542 | 0.0068909 | 0.001727
18 | 0.99404 | -0.04173 | 0.0036289 | 0.00090948
19 | 0.99451 | -0.038399 | 0.0036253 | 0.00090858
20 | 0.99475 | -0.036733 | 0.0030767 | 0.00077109
21 | 0.99514 | -0.033971 | 0.0080582 | 0.0020196
22 | 0.98868 | -0.079471 | 0 | 0
23 | 0.9881 | -0.083556 | 0.0034958 | 0.00087613
24 | 0.98784 | -0.085431 | 0.0094254 | 0.0023622
25 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.063961 | -0.016044 | 0.064152 | 0.016118 | 0.00019133 | 7.3157e-05 | 0.095867 | 0.095867 | 0.095867 | 0.99283 | -0.050182 | 0.99589 | -0.028678 | 35.5064
1 | 0.036753 | 0.0092254 | -0.03671 | -0.0092092 | 4.2968e-05 | 1.6233e-05 | 0.055089 | 0.055089 | 0.055089 | 0.99283 | -0.050182 | 0.99163 | -0.058611 | 20.4033
2 | -0.073343 | -0.018421 | 0.073356 | 0.018426 | 1.263e-05 | 4.8358e-06 | 0.1096 | 0.1096 | 0.1096 | 0.99589 | -0.028678 | 0.99607 | -0.02744 | 40.5926
3 | 0.0076189 | 0.0019095 | -0.0076186 | -0.0019094 | 3.3241e-07 | 7.5275e-08 | 0.011433 | 0.011433 | 0.011433 | 0.99163 | -0.058611 | 0.99159 | -0.058926 | 4.2344
4 | 0.029091 | 0.0072997 | -0.029046 | -0.0072829 | 4.4924e-05 | 1.6792e-05 | 0.043656 | 0.043656 | 0.043656 | 0.99163 | -0.058611 | 0.99005 | -0.069756 | 16.169
5 | -0.10058 | -0.02525 | 0.10097 | 0.025397 | 0.00038484 | 0.00014766 | 0.15028 | 0.15028 | 0.15028 | 0.99607 | -0.02744 | 1 | 0 | 55.6576
6 | 0.025971 | 0.0065121 | -0.025955 | -0.0065064 | 1.5311e-05 | 5.682e-06 | 0.039034 | 0.039034 | 0.039034 | 0.99005 | -0.069756 | 0.98945 | -0.074013 | 14.4571
7 | 0.012625 | 0.0031644 | -0.012621 | -0.0031631 | 3.9301e-06 | 1.2775e-06 | 0.018786 | 0.018786 | 0.018786 | 1 | 0 | 0.99968 | -0.0022488 | 6.9579
8 | 0.06406 | 0.016097 | -0.063943 | -0.016053 | 0.0001167 | 4.4614e-05 | 0.095337 | 0.095337 | 0.095337 | 1 | 0 | 0.99812 | -0.013114 | 35.31
9 | 0.012941 | 0.0032447 | -0.012933 | -0.0032422 | 7.4246e-06 | 2.4524e-06 | 0.019462 | 0.019462 | 0.019462 | 0.98945 | -0.074013 | 0.98886 | -0.078156 | 7.2081
10 | 0.050078 | 0.012578 | -0.049939 | -0.012525 | 0.00013852 | 5.2757e-05 | 0.074666 | 0.074667 | 0.074667 | 0.99812 | -0.013114 | 0.99527 | -0.033064 | 27.6543
11 | 0.012933 | 0.0032422 | -0.012931 | -0.0032415 | 2.3552e-06 | 7.7803e-07 | 0.019462 | 0.019462 | 0.019462 | 0.98886 | -0.078156 | 0.98868 | -0.079471 | 7.2082
12 | 0.0080592 | 0.0020198 | -0.0080582 | -0.0020196 | 1.0125e-06 | 2.442e-07 | 0.012049 | 0.012049 | 0.012049 | 0.99527 | -0.033064 | 0.99514 | -0.033971 | 4.4627
13 | 0.037974 | 0.0095265 | -0.037955 | -0.0095191 | 1.9316e-05 | 7.3046e-06 | 0.056778 | 0.056778 | 0.056778 | 0.99527 | -0.033064 | 0.99475 | -0.036733 | 21.0289
14 | 0.02063 | 0.0051717 | -0.020623 | -0.0051693 | 6.6191e-06 | 2.4021e-06 | 0.030906 | 0.030906 | 0.030906 | 0.99326 | -0.047194 | 0.99294 | -0.049511 | 11.4466
15 | -0.024293 | -0.0060899 | 0.024298 | 0.0060917 | 4.884e-06 | 1.802e-06 | 0.036394 | 0.036394 | 0.036394 | 0.99326 | -0.047194 | 0.99347 | -0.045743 | 13.4793
16 | 0.016959 | 0.0042512 | -0.016953 | -0.0042488 | 6.9017e-06 | 2.4331e-06 | 0.025416 | 0.025416 | 0.025416 | 0.99294 | -0.049511 | 0.99252 | -0.052451 | 9.4133
17 | -0.027586 | -0.0069158 | 0.027602 | 0.0069216 | 1.5345e-05 | 5.7153e-06 | 0.041319 | 0.041319 | 0.041319 | 0.99347 | -0.045743 | 0.99404 | -0.04173 | 15.3035
18 | 0.012058 | 0.003022 | -0.012056 | -0.0030215 | 1.3355e-06 | 4.2902e-07 | 0.018077 | 0.018077 | 0.018077 | 0.99252 | -0.052451 | 0.99241 | -0.053251 | 6.6952
19 | 0.0068918 | 0.0017272 | -0.0068909 | -0.001727 | 9.0486e-07 | 1.7259e-07 | 0.010334 | 0.010334 | 0.010334 | 0.99241 | -0.053251 | 0.99227 | -0.0542 | 3.8273
20 | -0.03123 | -0.007831 | 0.031245 | 0.0078364 | 1.4423e-05 | 5.4101e-06 | 0.046751 | 0.046751 | 0.046751 | 0.99404 | -0.04173 | 0.99451 | -0.038399 | 17.3154
21 | -0.03487 | -0.008745 | 0.034878 | 0.0087481 | 8.0531e-06 | 3.0358e-06 | 0.052176 | 0.052176 | 0.052176 | 0.99451 | -0.038399 | 0.99475 | -0.036733 | 19.3243
22 | 0.012931 | 0.0032415 | -0.012924 | -0.003239 | 7.3133e-06 | 2.4163e-06 | 0.019462 | 0.019462 | 0.019462 | 0.98868 | -0.079471 | 0.9881 | -0.083556 | 7.2082
23 | 0.0094278 | 0.0023629 | -0.0094254 | -0.0023622 | 2.4464e-06 | 6.9187e-07 | 0.014198 | 0.014198 | 0.014198 | 0.9881 | -0.083556 | 0.98784 | -0.085431 | 5.2585

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.17845 | 0.044659

## res_load
| p_mw | q_mvar
0 | 0.027208 | 0.006819
1 | 0.0091911 | 0.0023035
2 | 0.027228 | 0.006824
3 | 0.0076186 | 0.0019094
4 | 0.0030754 | 0.00077076
5 | 0.013015 | 0.0032618
6 | 0.012621 | 0.0031631
7 | 0.013865 | 0.003475
8 | 0.0039059 | 0.0009789
9 | 0.0036635 | 0.00091815
10 | 0.0036634 | 0.00091815
11 | 0.0032884 | 0.00082415
12 | 0.004895 | 0.0012268
13 | 0.0051644 | 0.0012943
14 | 0.0068909 | 0.001727
15 | 0.0036289 | 0.00090948
16 | 0.0036253 | 0.00090858
17 | 0.0030767 | 0.00077109
18 | 0.0080582 | 0.0020196
19 | 0.0034958 | 0.00087613
20 | 0.0094254 | 0.0023622

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1