## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1506-5_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1506-5_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1506-5_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1506-5_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1506-5_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1506-5_0_3_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_1506-5_0_3_node_17 | 0.4 | n |  | TRUE
7 | bus_LV_1506-5_0_3_node_20 | 0.4 | n |  | TRUE
8 | bus_LV_1506-5_0_3_node_21 | 0.4 | n |  | TRUE
9 | bus_LV_1506-5_0_3_node_18 | 0.4 | n |  | TRUE
10 | bus_LV_1506-5_0_3_node_19 | 0.4 | n |  | TRUE
11 | bus_LV_1506-5_0_3_node_32 | 0.4 | n |  | TRUE
12 | bus_LV_1506-5_0_3_node_31 | 0.4 | n |  | TRUE
13 | bus_LV_1506-5_0_3_node_27 | 0.4 | n |  | TRUE
14 | bus_LV_1506-5_0_3_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_1506-5_0_3_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_1506-5_0_3_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_1506-5_0_3_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_1506-5_0_3_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_1506-5_0_3_node_24 | 0.4 | n |  | TRUE
20 | bus_LV_1506-5_0_3_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_1506-5_0_3_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_1506-5_0_3_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_1506-5_0_3_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_1506-5_0_3_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_1506-5_0_3_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_1506-5_0_3_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_1506-5_0_3_node_28 | 0.4 | n |  | TRUE
28 | bus_LV_1506-5_0_3_node_29 | 0.4 | n |  | TRUE
29 | bus_LV_1506-5_0_3_node_30 | 0.4 | n |  | TRUE
30 | bus_MV_143_0_node_10 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1506-5_0_3_load_0 | 0 | 0.012523 | 0.0031386 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1506-5_0_3_load_1 | 1 | 0.022129 | 0.0055461 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1506-5_0_3_load_3 | 3 | 0.0071922 | 0.0018025 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1506-5_0_3_load_4 | 4 | 0.0013204 | 0.00033092 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1506-5_0_3_load_21 | 8 | 0.0065231 | 0.0016348 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1506-5_0_3_load_19 | 10 | 0.055782 | 0.01398 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1506-5_0_3_load_32 | 11 | 0.0052617 | 0.0013187 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1506-5_0_3_load_31 | 12 | 0.014332 | 0.0035919 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1506-5_0_3_load_27 | 13 | 0.0086316 | 0.0021633 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1506-5_0_3_load_7 | 14 | 0.0031215 | 0.00078231 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1506-5_0_3_load_8 | 15 | 0.0031234 | 0.0007828 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1506-5_0_3_load_12 | 17 | 0.018139 | 0.004546 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1506-5_0_3_load_10 | 18 | 0.017252 | 0.0043237 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1506-5_0_3_load_24 | 19 | 0.007961 | 0.0019952 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1506-5_0_3_load_13 | 21 | 0.003168 | 0.00079399 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1506-5_0_3_load_16 | 23 | 0.0030246 | 0.00075804 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1506-5_0_3_load_15 | 24 | 0.0030264 | 0.00075848 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1506-5_0_3_load_22 | 25 | 0.0020174 | 0.00050562 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1506-5_0_3_load_23 | 26 | 0.0021811 | 0.00054665 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1506-5_0_3_load_28 | 27 | 0.0075168 | 0.0018839 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1506-5_0_3_load_30 | 29 | 0.0010476 | 0.00026255 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 0 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1506-5_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.038992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
1 | LV_1506-5_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.012208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1506-5_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.036864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
3 | LV_1506-5_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.038295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1506-5_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.015917 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1506-5_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.0088962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1506-5_0_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.060011 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1506-5_0_3_line_7 | NAYY 4x150 SE | 5 | 8 | 0.016808 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1506-5_0_3_line_8 | NAYY 4x150 SE | 6 | 9 | 0.012686 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1506-5_0_3_line_9 | NAYY 4x150 SE | 6 | 10 | 0.071249 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1506-5_0_3_line_10 | NAYY 4x150 SE | 7 | 11 | 0.017202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1506-5_0_3_line_11 | NAYY 4x150 SE | 7 | 12 | 0.020266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1506-5_0_3_line_12 | NAYY 4x150 SE | 8 | 13 | 0.010517 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1506-5_0_3_line_13 | NAYY 4x150 SE | 9 | 25 | 0.024592 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1506-5_0_3_line_14 | NAYY 4x150 SE | 11 | 22 | 0.038207 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1506-5_0_3_line_15 | NAYY 4x150 SE | 13 | 27 | 0.015705 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1506-5_0_3_line_16 | NAYY 4x150 SE | 14 | 15 | 0.0068368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1506-5_0_3_line_17 | NAYY 4x150 SE | 15 | 16 | 0.019661 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1506-5_0_3_line_18 | NAYY 4x150 SE | 16 | 17 | 0.017926 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1506-5_0_3_line_19 | NAYY 4x150 SE | 16 | 18 | 0.013129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1506-5_0_3_line_20 | NAYY 4x150 SE | 17 | 19 | 0.022826 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1506-5_0_3_line_21 | NAYY 4x150 SE | 18 | 20 | 0.01506 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1506-5_0_3_line_22 | NAYY 4x150 SE | 20 | 21 | 0.023857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1506-5_0_3_line_23 | NAYY 4x150 SE | 20 | 22 | 0.067302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1506-5_0_3_line_24 | NAYY 4x150 SE | 21 | 23 | 0.006757 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1506-5_0_3_line_25 | NAYY 4x150 SE | 23 | 24 | 0.0068205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1506-5_0_3_line_26 | NAYY 4x150 SE | 25 | 26 | 0.0055351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1506-5_0_3_line_27 | NAYY 4x150 SE | 27 | 28 | 0.074466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1506-5_0_3_line_28 | NAYY 4x150 SE | 28 | 29 | 0.014761 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1506-5_0_3_trafo_0 | 0.25 MVA 20/0.4 kV | 30 | 0 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2668698.0625 | 1201086.5672 | 2668713.9721 | 1201094.6022 | 2668731.6606 | 1201106.2312
1 | 2668687.1653 | 1201081.0637 | 2668698.0625 | 1201086.5672
2 | 2668731.6606 | 1201106.2312 | 2668762.4641 | 1201126.4822
3 | 2668687.1653 | 1201081.0637 | 2668693.95 | 1201078.2289 | 2668711.8906 | 1201080.3364 | 2668723.9619 | 1201075.8502
4 | 2668775.7646 | 1201135.2263 | 2668762.4641 | 1201126.4822
5 | 2668723.1503 | 1201066.9911 | 2668723.9619 | 1201075.8502
6 | 2668775.7646 | 1201135.2263 | 2668768.3815 | 1201143.7687 | 2668727.5988 | 1201170.6159
7 | 2668775.7646 | 1201135.2263 | 2668789.9427 | 1201144.2527
8 | 2668723.1503 | 1201066.9911 | 2668735.5165 | 1201064.0092
9 | 2668723.1503 | 1201066.9911 | 2668711.3794 | 1201068.5233 | 2668704.3035 | 1201068.8867 | 2668698.9873 | 1201068.4698 | 2668692.5955 | 1201066.9287 | 2668654.1267 | 1201054.634
10 | 2668727.5988 | 1201170.6159 | 2668713.1391 | 1201179.9336
11 | 2668727.5988 | 1201170.6159 | 2668736.8903 | 1201188.6267
12 | 2668798.8147 | 1201149.901 | 2668789.9427 | 1201144.2527
13 | 2668735.5165 | 1201064.0092 | 2668754.4764 | 1201079.6708
14 | 2668686.4438 | 1201206.7091 | 2668691.6725 | 1201202.1442 | 2668704.8681 | 1201185.2634 | 2668713.1391 | 1201179.9336
15 | 2668798.8147 | 1201149.901 | 2668805.7498 | 1201154.3162 | 2668811.4927 | 1201159.1152
16 | 2668665.5917 | 1201130.6407 | 2668659.6292 | 1201133.9858
17 | 2668641.8401 | 1201141.524 | 2668646.9988 | 1201141.0719 | 2668659.6292 | 1201133.9858
18 | 2668641.8401 | 1201141.524 | 2668640.9352 | 1201130.1845 | 2668639.8489 | 1201123.7244
19 | 2668641.8401 | 1201141.524 | 2668642.771 | 1201154.6201
20 | 2668639.8489 | 1201123.7244 | 2668639.1182 | 1201119.3794 | 2668636.6832 | 1201112.6807 | 2668632.5455 | 1201104.4393 | 2668631.3274 | 1201102.7646
21 | 2668643.8387 | 1201169.6417 | 2668642.771 | 1201154.6201
22 | 2668643.8387 | 1201169.6417 | 2668649.18 | 1201169.1917 | 2668660.7937 | 1201166.7458 | 2668666.9883 | 1201164.3878
23 | 2668643.8387 | 1201169.6417 | 2668645.1887 | 1201183.9881 | 2668649.0519 | 1201194.2498 | 2668652.6558 | 1201199.2497 | 2668662.0368 | 1201204.9609 | 2668672.1591 | 1201207.1007 | 2668679.8227 | 1201207.9115 | 2668686.4438 | 1201206.7091
24 | 2668672.6296 | 1201160.6885 | 2668667.3995 | 1201164.2313 | 2668666.9883 | 1201164.3878
25 | 2668672.6296 | 1201160.6885 | 2668678.2765 | 1201156.8633
26 | 2668758.7438 | 1201083.1959 | 2668754.4764 | 1201079.6708
27 | 2668864.3366 | 1201211.4365 | 2668840.4844 | 1201185.3238 | 2668822.3971 | 1201168.2274 | 2668811.4927 | 1201159.1152
28 | 2668864.3366 | 1201211.4365 | 2668874.9133 | 1201201.1405

## bus_geodata
| x | y | coords
0 | 2668698.0625 | 1201086.5672
1 | 2668731.6606 | 1201106.2312
2 | 2668687.1653 | 1201081.0637
3 | 2668762.4641 | 1201126.4822
4 | 2668723.9619 | 1201075.8502
5 | 2668775.7646 | 1201135.2263
6 | 2668723.1503 | 1201066.9911
7 | 2668727.5988 | 1201170.6159
8 | 2668789.9427 | 1201144.2527
9 | 2668735.5165 | 1201064.0092
10 | 2668654.1267 | 1201054.634
11 | 2668713.1391 | 1201179.9336
12 | 2668736.8903 | 1201188.6267
13 | 2668798.8147 | 1201149.901
14 | 2668665.5917 | 1201130.6407
15 | 2668659.6292 | 1201133.9858
16 | 2668641.8401 | 1201141.524
17 | 2668639.8489 | 1201123.7244
18 | 2668642.771 | 1201154.6201
19 | 2668631.3274 | 1201102.7646
20 | 2668643.8387 | 1201169.6417
21 | 2668666.9883 | 1201164.3878
22 | 2668686.4438 | 1201206.7091
23 | 2668672.6296 | 1201160.6885
24 | 2668678.2765 | 1201156.8633
25 | 2668754.4764 | 1201079.6708
26 | 2668758.7438 | 1201083.1959
27 | 2668811.4927 | 1201159.1152
28 | 2668864.3366 | 1201211.4365
29 | 2668874.9133 | 1201201.1405
30 | 2668687.1653 | 1201081.0637

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 1 | 0 | -0.19652 | -0.049438
1 | 0.99628 | -0.025684 | 0.022129 | 0.0055461
2 | 0.99892 | -0.0074789 | 0 | 0
3 | 0.99335 | -0.046013 | 0.0071922 | 0.0018025
4 | 0.99554 | -0.031044 | 0.0013204 | 0.00033092
5 | 0.99098 | -0.062502 | 0 | 0
6 | 0.99477 | -0.036422 | 0 | 0
7 | 0.98409 | -0.11067 | 0 | 0
8 | 0.9904 | -0.066558 | 0.0065231 | 0.0016348
9 | 0.9947 | -0.03696 | 0 | 0
10 | 0.98904 | -0.07674 | 0.055782 | 0.01398
11 | 0.98248 | -0.12206 | 0.0052617 | 0.0013187
12 | 0.98367 | -0.11367 | 0.014332 | 0.0035919
13 | 0.99014 | -0.0684 | 0.0086316 | 0.0021633
14 | 0.97144 | -0.20073 | 0.0031215 | 0.00078231
15 | 0.97148 | -0.2005 | 0.0031234 | 0.0007828
16 | 0.97166 | -0.1992 | 0 | 0
17 | 0.97097 | -0.20415 | 0.018139 | 0.004546
18 | 0.97228 | -0.19472 | 0.017252 | 0.0043237
19 | 0.9707 | -0.20608 | 0.007961 | 0.0019952
20 | 0.97337 | -0.18684 | 0 | 0
21 | 0.97305 | -0.18916 | 0.003168 | 0.00079399
22 | 0.97918 | -0.14538 | 0 | 0
23 | 0.97299 | -0.18959 | 0.0030246 | 0.00075804
24 | 0.97296 | -0.18981 | 0.0030264 | 0.00075848
25 | 0.99455 | -0.038002 | 0.0020174 | 0.00050562
26 | 0.99453 | -0.038124 | 0.0021811 | 0.00054665
27 | 0.98995 | -0.069771 | 0.0075168 | 0.0018839
28 | 0.98984 | -0.070569 | 0 | 0
29 | 0.98981 | -0.070727 | 0.0010476 | 0.00026255
30 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.13379 | 0.033836 | -0.13331 | -0.033651 | 0.00048267 | 0.00018462 | 0.19919 | 0.19919 | 0.19919 | 1 | 0 | 0.99628 | -0.025684 | 36.8864
1 | 0.061928 | 0.015602 | -0.061863 | -0.015578 | 6.4728e-05 | 2.4735e-05 | 0.092179 | 0.092179 | 0.092179 | 1 | 0 | 0.99892 | -0.0074789 | 34.1403
2 | 0.11118 | 0.028105 | -0.11086 | -0.027984 | 0.00031745 | 0.00012114 | 0.16613 | 0.16613 | 0.16613 | 0.99628 | -0.025684 | 0.99335 | -0.046013 | 30.7657
3 | 0.061863 | 0.015578 | -0.06166 | -0.0155 | 0.00020304 | 7.7594e-05 | 0.092179 | 0.092179 | 0.092179 | 0.99892 | -0.0074789 | 0.99554 | -0.031044 | 34.1403
4 | 0.10367 | 0.026181 | -0.10343 | -0.026089 | 0.00023974 | 9.2002e-05 | 0.15536 | 0.15536 | 0.15536 | 0.99335 | -0.046013 | 0.99098 | -0.062502 | 57.5412
5 | 0.06034 | 0.015169 | -0.060295 | -0.015152 | 4.517e-05 | 1.7258e-05 | 0.090205 | 0.090205 | 0.090205 | 0.99554 | -0.031044 | 0.99477 | -0.036422 | 33.4094
6 | 0.079688 | 0.020139 | -0.079151 | -0.019933 | 0.00053669 | 0.00020565 | 0.11972 | 0.11972 | 0.11972 | 0.99098 | -0.062502 | 0.98409 | -0.11067 | 44.3394
7 | 0.023739 | 0.0059503 | -0.023725 | -0.0059454 | 1.3326e-05 | 4.9089e-06 | 0.035645 | 0.035645 | 0.035645 | 0.99098 | -0.062502 | 0.9904 | -0.066558 | 13.202
8 | 0.0041995 | 0.0010521 | -0.0041992 | -0.0010521 | 3.1237e-07 | -4.4542e-08 | 0.0062817 | 0.0062817 | 0.0062817 | 0.99477 | -0.036422 | 0.9947 | -0.03696 | 2.3266
9 | 0.056095 | 0.0141 | -0.055782 | -0.01398 | 0.00031314 | 0.00011952 | 0.083924 | 0.083924 | 0.083924 | 0.99477 | -0.036422 | 0.98904 | -0.07674 | 31.083
10 | 0.064813 | 0.016339 | -0.06471 | -0.0163 | 0.00010317 | 3.9461e-05 | 0.098037 | 0.098037 | 0.098037 | 0.98409 | -0.11067 | 0.98248 | -0.12206 | 36.3099
11 | 0.014338 | 0.0035939 | -0.014332 | -0.0035919 | 5.9439e-06 | 2.0287e-06 | 0.02168 | 0.02168 | 0.02168 | 0.98409 | -0.11067 | 0.98367 | -0.11367 | 8.0296
12 | 0.017202 | 0.0043106 | -0.017198 | -0.004309 | 4.3837e-06 | 1.5507e-06 | 0.025845 | 0.025845 | 0.025845 | 0.9904 | -0.066558 | 0.99014 | -0.0684 | 9.5722
13 | 0.0041992 | 0.0010521 | -0.0041986 | -0.0010522 | 6.0554e-07 | -8.6267e-08 | 0.0062817 | 0.0062818 | 0.0062818 | 0.9947 | -0.03696 | 0.99455 | -0.038002 | 2.3266
14 | 0.059449 | 0.014981 | -0.059255 | -0.014907 | 0.0001934 | 7.3903e-05 | 0.090067 | 0.090068 | 0.090068 | 0.98248 | -0.12206 | 0.97918 | -0.14538 | 33.3584
15 | 0.0085661 | 0.0021458 | -0.0085645 | -0.0021453 | 1.624e-06 | 4.2267e-07 | 0.012873 | 0.012873 | 0.012873 | 0.99014 | -0.0684 | 0.98995 | -0.069771 | 4.7678
16 | -0.0031215 | -0.00078231 | 0.0031216 | 0.00078226 | 9.7528e-08 | -4.7136e-08 | 0.0047813 | 0.0047813 | 0.0047813 | 0.97144 | -0.20073 | 0.97148 | -0.2005 | 1.7709
17 | -0.006245 | -0.0015651 | 0.0062461 | 0.0015652 | 1.1225e-06 | 1.8826e-07 | 0.0095654 | 0.0095653 | 0.0095654 | 0.97148 | -0.2005 | 0.97166 | -0.1992 | 3.5427
18 | 0.02612 | 0.0065484 | -0.026102 | -0.0065418 | 1.7899e-05 | 6.6623e-06 | 0.040001 | 0.040001 | 0.040001 | 0.97166 | -0.1992 | 0.97097 | -0.20415 | 14.8153
19 | -0.032366 | -0.0081137 | 0.032386 | 0.0081213 | 2.0128e-05 | 7.5788e-06 | 0.049567 | 0.049567 | 0.049567 | 0.97166 | -0.1992 | 0.97228 | -0.19472 | 18.358
20 | 0.0079631 | 0.0019957 | -0.007961 | -0.0019952 | 2.1212e-06 | 5.3361e-07 | 0.012203 | 0.012204 | 0.012204 | 0.97097 | -0.20415 | 0.9707 | -0.20608 | 4.5199
21 | -0.049638 | -0.012445 | 0.049692 | 0.012466 | 5.4234e-05 | 2.0672e-05 | 0.075969 | 0.075969 | 0.075969 | 0.97228 | -0.19472 | 0.97337 | -0.18684 | 28.1368
22 | 0.0092225 | 0.0023114 | -0.0092195 | -0.0023105 | 2.959e-06 | 8.4165e-07 | 0.014099 | 0.014099 | 0.014099 | 0.97337 | -0.18684 | 0.97305 | -0.18916 | 5.2217
23 | -0.058915 | -0.014777 | 0.059255 | 0.014907 | 0.00034069 | 0.00013019 | 0.090068 | 0.090068 | 0.090068 | 0.97337 | -0.18684 | 0.97918 | -0.14538 | 33.3585
24 | 0.0060515 | 0.0015165 | -0.0060511 | -0.0015165 | 3.6108e-07 | 5.4947e-08 | 0.009254 | 0.009254 | 0.009254 | 0.97305 | -0.18916 | 0.97299 | -0.18959 | 3.4274
25 | 0.0030265 | 0.00075844 | -0.0030264 | -0.00075848 | 9.1173e-08 | -4.9642e-08 | 0.0046284 | 0.0046285 | 0.0046285 | 0.97299 | -0.18959 | 0.97296 | -0.18981 | 1.7142
26 | 0.0021812 | 0.00054659 | -0.0021811 | -0.00054665 | 3.6784e-08 | -5.7678e-08 | 0.0032634 | 0.0032634 | 0.0032634 | 0.99455 | -0.038002 | 0.99453 | -0.038124 | 1.2087
27 | 0.0010477 | 0.00026145 | -0.0010476 | -0.00026237 | 1.1521e-07 | -9.1298e-07 | 0.0015744 | 0.0015748 | 0.0015748 | 0.98995 | -0.069771 | 0.98984 | -0.070569 | 0.58325
28 | 0.0010476 | 0.00026237 | -0.0010476 | -0.00026255 | 2.2843e-08 | -1.8094e-07 | 0.0015748 | 0.0015749 | 0.0015749 | 0.98984 | -0.070569 | 0.98981 | -0.070727 | 0.58328

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.20904 | 0.052577

## res_load
| p_mw | q_mvar
0 | 0.012523 | 0.0031386
1 | 0.022129 | 0.0055461
2 | 0.0071922 | 0.0018025
3 | 0.0013204 | 0.00033092
4 | 0.0065231 | 0.0016348
5 | 0.055782 | 0.01398
6 | 0.0052617 | 0.0013187
7 | 0.014332 | 0.0035919
8 | 0.0086316 | 0.0021633
9 | 0.0031215 | 0.00078231
10 | 0.0031234 | 0.0007828
11 | 0.018139 | 0.004546
12 | 0.017252 | 0.0043237
13 | 0.007961 | 0.0019952
14 | 0.003168 | 0.00079399
15 | 0.0030246 | 0.00075804
16 | 0.0030264 | 0.00075848
17 | 0.0020174 | 0.00050562
18 | 0.0021811 | 0.00054665
19 | 0.0075168 | 0.0018839
20 | 0.0010476 | 0.00026255

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1