## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1506-6_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1506-6_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1506-6_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1506-6_0_3_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1506-6_0_3_node_103 | 0.4 | n |  | TRUE
5 | bus_LV_1506-6_0_3_node_148 | 0.4 | n |  | TRUE
6 | bus_LV_1506-6_0_3_node_96 | 0.4 | n |  | TRUE
7 | bus_LV_1506-6_0_3_node_150 | 0.4 | n |  | TRUE
8 | bus_LV_1506-6_0_3_node_149 | 0.4 | n |  | TRUE
9 | bus_LV_1506-6_0_3_node_151 | 0.4 | n |  | TRUE
10 | bus_LV_1506-6_0_3_node_152 | 0.4 | n |  | TRUE
11 | bus_LV_1506-6_0_3_node_153 | 0.4 | n |  | TRUE
12 | bus_LV_1506-6_0_3_node_154 | 0.4 | n |  | TRUE
13 | bus_LV_1506-6_0_3_node_83 | 0.4 | n |  | TRUE
14 | bus_LV_1506-6_0_3_node_84 | 0.4 | n |  | TRUE
15 | bus_LV_1506-6_0_3_node_85 | 0.4 | n |  | TRUE
16 | bus_LV_1506-6_0_3_node_86 | 0.4 | n |  | TRUE
17 | bus_LV_1506-6_0_3_node_87 | 0.4 | n |  | TRUE
18 | bus_LV_1506-6_0_3_node_88 | 0.4 | n |  | TRUE
19 | bus_LV_1506-6_0_3_node_95 | 0.4 | n |  | TRUE
20 | bus_LV_1506-6_0_3_node_90 | 0.4 | n |  | TRUE
21 | bus_LV_1506-6_0_3_node_91 | 0.4 | n |  | TRUE
22 | bus_LV_1506-6_0_3_node_92 | 0.4 | n |  | TRUE
23 | bus_LV_1506-6_0_3_node_93 | 0.4 | n |  | TRUE
24 | bus_LV_1506-6_0_3_node_94 | 0.4 | n |  | TRUE
25 | bus_LV_1506-6_0_3_node_108 | 0.4 | n |  | TRUE
26 | bus_LV_1506-6_0_3_node_104 | 0.4 | n |  | TRUE
27 | bus_MV_0_node_95 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1506-6_0_3_load_0 | 0 | 0.0010839 | 0.00027165 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1506-6_0_3_load_3 | 2 | 0.00024158 | 6.0546e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1506-6_0_3_load_103 | 4 | 0.00017369 | 4.3532e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1506-6_0_3_load_148 | 5 | 0.00025233 | 6.324e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1506-6_0_3_load_150 | 7 | 0.00034917 | 8.7509e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1506-6_0_3_load_149 | 8 | 0.00035336 | 8.856e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1506-6_0_3_load_151 | 9 | 9.471e-05 | 2.3737e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1506-6_0_3_load_153 | 11 | 0.0001213 | 3.0401e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1506-6_0_3_load_154 | 12 | 0.00020104 | 5.0385e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1506-6_0_3_load_83 | 13 | 0.0039827 | 0.00099816 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1506-6_0_3_load_84 | 14 | 0.00091516 | 0.00022936 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1506-6_0_3_load_86 | 16 | 0.00084464 | 0.00021169 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1506-6_0_3_load_87 | 17 | 0.0011645 | 0.00029184 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1506-6_0_3_load_88 | 18 | 0.0014828 | 0.00037163 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1506-6_0_3_load_90 | 20 | 0.0011092 | 0.000278 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1506-6_0_3_load_91 | 21 | 0.00071687 | 0.00017966 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1506-6_0_3_load_92 | 22 | 0.00044351 | 0.00011115 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1506-6_0_3_load_93 | 23 | 0.0021357 | 0.00053525 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1506-6_0_3_load_94 | 24 | 0.00034424 | 8.6274e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1506-6_0_3_load_108 | 25 | 0.0044202 | 0.0011078 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1506-6_0_3_load_104 | 26 | 0.00080952 | 0.00020288 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 19 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1506-6_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.026776 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1506-6_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.024201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1506-6_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.058495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1506-6_0_3_line_3 | NAYY 4x150 SE | 3 | 4 | 0.28823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1506-6_0_3_line_4 | NAYY 4x150 SE | 4 | 26 | 0.065133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1506-6_0_3_line_5 | NAYY 4x150 SE | 5 | 6 | 0.077766 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1506-6_0_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.025644 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1506-6_0_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.088411 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1506-6_0_3_line_8 | NAYY 4x150 SE | 6 | 24 | 0.011095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1506-6_0_3_line_9 | NAYY 4x150 SE | 7 | 10 | 0.13194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1506-6_0_3_line_10 | NAYY 4x150 SE | 8 | 9 | 0.26973 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1506-6_0_3_line_11 | NAYY 4x150 SE | 10 | 11 | 0.068646 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1506-6_0_3_line_12 | NAYY 4x150 SE | 11 | 12 | 0.012864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1506-6_0_3_line_13 | NAYY 4x150 SE | 13 | 14 | 0.089688 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1506-6_0_3_line_14 | NAYY 4x150 SE | 13 | 15 | 0.09258 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1506-6_0_3_line_15 | NAYY 4x150 SE | 14 | 16 | 0.009607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1506-6_0_3_line_16 | NAYY 4x150 SE | 15 | 17 | 0.093786 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1506-6_0_3_line_17 | NAYY 4x150 SE | 15 | 18 | 0.074972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1506-6_0_3_line_18 | NAYY 4x150 SE | 18 | 19 | 0.073022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1506-6_0_3_line_19 | NAYY 4x150 SE | 19 | 25 | 0.062326 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1506-6_0_3_line_20 | NAYY 4x150 SE | 19 | 23 | 0.1224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1506-6_0_3_line_21 | NAYY 4x150 SE | 20 | 21 | 0.019281 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1506-6_0_3_line_22 | NAYY 4x150 SE | 20 | 22 | 0.09276 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1506-6_0_3_line_23 | NAYY 4x150 SE | 21 | 23 | 0.022047 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1506-6_0_3_line_24 | NAYY 4x150 SE | 22 | 24 | 0.020219 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1506-6_0_3_line_25 | NAYY 4x150 SE | 25 | 26 | 0.18996 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1506-6_0_3_trafo_95 | 0.25 MVA 20/0.4 kV | 27 | 19 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2667858.0921 | 1200403.1867 | 2667844.0794 | 1200380.37
1 | 2667858.0921 | 1200403.1867 | 2667836.6492 | 1200414.4073
2 | 2667858.0921 | 1200403.1867 | 2667859.5243 | 1200402.4358 | 2667888.8595 | 1200451.1648
3 | 2668165.1354 | 1200533.3158 | 2667888.8595 | 1200451.1648
4 | 2668224.7642 | 1200559.5207 | 2668165.1354 | 1200533.3158
5 | 2668340.2709 | 1200230.3754 | 2668329.007 | 1200207.4106 | 2668326.6523 | 1200194.9539 | 2668327.594 | 1200180.5116 | 2668332.8607 | 1200156.0348
6 | 2668328.2713 | 1200130.883 | 2668331.4588 | 1200142.8109 | 2668332.8607 | 1200156.0348 | 2668332.8607 | 1200156.0348
7 | 2668340.2709 | 1200230.3754 | 2668316.7599 | 1200205.1693 | 2668281.5432 | 1200164.309
8 | 2668340.2709 | 1200230.3754 | 2668346.0214 | 1200239.8641
9 | 2668303.383 | 1200001.405 | 2668311.1705 | 1200054.1146 | 2668326.1364 | 1200122.8936 | 2668328.2713 | 1200130.883
10 | 2668281.5432 | 1200164.309 | 2668281.5432 | 1200164.309 | 2668232.8598 | 1200137.9485 | 2668191.8722 | 1200111.665 | 2668135.5315 | 1200081.7269 | 2668093.9377 | 1200047.777 | 2668082.9861 | 1200026.017 | 2668076.2285 | 1200005.0163 | 2668075.1873 | 1200003.5865
11 | 2668303.383 | 1200001.405 | 2668296.966 | 1199991.3034 | 2668279.0832 | 1199971.1759 | 2668255.7528 | 1199952.7096 | 2668255.7528 | 1199952.7096
12 | 2668255.7528 | 1199952.7096 | 2668258.1472 | 1199945.0545 | 2668259.0399 | 1199940.2939
13 | 2668558.926 | 1200569.2941 | 2668558.926 | 1200569.2941 | 2668561.6684 | 1200574.4509 | 2668566.4644 | 1200577.7745 | 2668573.3027 | 1200578.9315 | 2668578.9357 | 1200576.9838 | 2668588.5125 | 1200571.0345 | 2668603.5786 | 1200561.7351 | 2668625.9852 | 1200550.9636 | 2668633.9405 | 1200549.6541 | 2668637.1407 | 1200549.9531
14 | 2668598.259 | 1200494.6114 | 2668600.5078 | 1200502.9756 | 2668601.3655 | 1200509.8229 | 2668599.8508 | 1200519.7448 | 2668595.6586 | 1200532.1264 | 2668588.6844 | 1200542.1413 | 2668582.0846 | 1200546.7239 | 2668565.914 | 1200557.4115 | 2668561.0346 | 1200562.0139 | 2668558.926 | 1200569.2941
15 | 2668646.4908 | 1200551.747 | 2668643.4388 | 1200550.5415 | 2668637.1407 | 1200549.9531
16 | 2668598.259 | 1200494.6114 | 2668607.4622 | 1200481.4313 | 2668618.9214 | 1200474.6588 | 2668645.7282 | 1200466.5839 | 2668662.6641 | 1200456.9059 | 2668676.1002 | 1200446.6603
17 | 2668598.259 | 1200494.6114 | 2668580.1757 | 1200495.4934 | 2668567.3881 | 1200495.9692 | 2668557.1257 | 1200493.9836 | 2668528.2675 | 1200484.4692 | 2668525.187 | 1200483.4923
18 | 2668455.1074 | 1200463.1515 | 2668477.0205 | 1200468.2167 | 2668525.187 | 1200483.4923
19 | 2668455.1074 | 1200463.1515 | 2668444.7577 | 1200472.1051 | 2668423.7073 | 1200486.7729 | 2668414.1737 | 1200489.6211 | 2668407.6238 | 1200489.8574 | 2668401.0882 | 1200488.8487
20 | 2668455.1074 | 1200463.1515 | 2668432.7136 | 1200458.8481 | 2668419.9975 | 1200453.7328 | 2668412.1466 | 1200445.2601 | 2668406.5314 | 1200431.6765 | 2668403.1494 | 1200414.5497 | 2668403.9158 | 1200402.1288 | 2668409.1997 | 1200389.4594 | 2668414.97 | 1200375.5393 | 2668414.9614 | 1200374.5985
21 | 2668392.5512 | 1200341.5906 | 2668405.6098 | 1200355.7755
22 | 2668392.5512 | 1200341.5906 | 2668391.3767 | 1200340.3148 | 2668382.6764 | 1200324.2167 | 2668378.1784 | 1200308.7893 | 2668374.7993 | 1200290.7287 | 2668367.1933 | 1200274.7988 | 2668356.5008 | 1200257.1556
23 | 2668405.6098 | 1200355.7755 | 2668410.4615 | 1200361.0457 | 2668414.899 | 1200367.7783 | 2668414.9614 | 1200374.5985
24 | 2668356.5008 | 1200257.1556 | 2668346.0214 | 1200239.8641
25 | 2668401.0882 | 1200488.8487 | 2668224.7642 | 1200559.5207

## bus_geodata
| x | y | coords
0 | 2667844.0794 | 1200380.37
1 | 2667858.0921 | 1200403.1867
2 | 2667836.6492 | 1200414.4073
3 | 2667888.8595 | 1200451.1648
4 | 2668165.1354 | 1200533.3158
5 | 2668332.8607 | 1200156.0348
6 | 2668340.2709 | 1200230.3754
7 | 2668328.2713 | 1200130.883
8 | 2668281.5432 | 1200164.309
9 | 2668075.1873 | 1200003.5865
10 | 2668303.383 | 1200001.405
11 | 2668255.7528 | 1199952.7096
12 | 2668259.0399 | 1199940.2939
13 | 2668558.926 | 1200569.2941
14 | 2668637.1407 | 1200549.9531
15 | 2668598.259 | 1200494.6114
16 | 2668646.4908 | 1200551.747
17 | 2668676.1002 | 1200446.6603
18 | 2668525.187 | 1200483.4923
19 | 2668455.1074 | 1200463.1515
20 | 2668392.5512 | 1200341.5906
21 | 2668405.6098 | 1200355.7755
22 | 2668356.5008 | 1200257.1556
23 | 2668414.9614 | 1200374.5985
24 | 2668346.0214 | 1200239.8641
25 | 2668401.0882 | 1200488.8487
26 | 2668224.7642 | 1200559.5207
27 | 2668455.1074 | 1200463.1515

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99794 | -0.014692 | 0.0010839 | 0.00027165
1 | 0.99798 | -0.014401 | 0 | 0
2 | 0.99797 | -0.01446 | 0.00024158 | 6.0546e-05
3 | 0.99809 | -0.013619 | 0 | 0
4 | 0.99864 | -0.0097225 | 0.00017369 | 4.3532e-05
5 | 0.99826 | -0.012471 | 0.00025233 | 6.324e-05
6 | 0.99836 | -0.01173 | 0 | 0
7 | 0.99823 | -0.012649 | 0.00034917 | 8.7509e-05
8 | 0.9983 | -0.012154 | 0.00035336 | 8.856e-05
9 | 0.99827 | -0.012445 | 9.471e-05 | 2.3737e-05
10 | 0.99817 | -0.013094 | 0 | 0
11 | 0.99814 | -0.013319 | 0.0001213 | 3.0401e-05
12 | 0.99814 | -0.013345 | 0.00020104 | 5.0385e-05
13 | 0.99763 | -0.016693 | 0.0039827 | 0.00099816
14 | 0.9974 | -0.018281 | 0.00091516 | 0.00022936
15 | 0.99839 | -0.011353 | 0 | 0
16 | 0.99739 | -0.018362 | 0.00084464 | 0.00021169
17 | 0.99823 | -0.01245 | 0.0011645 | 0.00029184
18 | 0.99913 | -0.0061479 | 0.0014828 | 0.00037163
19 | 1 | 0 | -0.022071 | -0.0053078
20 | 0.99872 | -0.009136 | 0.0011092 | 0.000278
21 | 0.99881 | -0.0084902 | 0.00071687 | 0.00017966
22 | 0.99843 | -0.011209 | 0.00044351 | 0.00011115
23 | 0.99893 | -0.0075933 | 0.0021357 | 0.00053525
24 | 0.99838 | -0.01157 | 0.00034424 | 8.6274e-05
25 | 0.9994 | -0.0042297 | 0.0044202 | 0.0011078
26 | 0.99878 | -0.008718 | 0.00080952 | 0.00020288
27 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0010839 | -0.00027165 | 0.001084 | 0.00027132 | 4.3641e-08 | -3.3307e-07 | 0.0016162 | 0.0016161 | 0.0016162 | 0.99794 | -0.014692 | 0.99798 | -0.014401 | 0.5986
1 | 0.00024158 | 6.023e-05 | -0.00024158 | -6.0546e-05 | 1.9588e-09 | -3.1547e-07 | 0.00036009 | 0.0003602 | 0.0003602 | 0.99798 | -0.014401 | 0.99797 | -0.01446 | 0.13341
2 | -0.0013255 | -0.00033155 | 0.0013257 | 0.00033084 | 1.4253e-07 | -7.0958e-07 | 0.0019762 | 0.0019759 | 0.0019762 | 0.99798 | -0.014401 | 0.99809 | -0.013619 | 0.73192
3 | -0.0013257 | -0.00033084 | 0.0013264 | 0.00032734 | 7.0173e-07 | -3.4991e-06 | 0.0019759 | 0.0019746 | 0.0019759 | 0.99809 | -0.013619 | 0.99864 | -0.0097225 | 0.73182
4 | -0.0015001 | -0.00037087 | 0.0015003 | 0.0003701 | 2.0271e-07 | -7.7432e-07 | 0.0022334 | 0.0022331 | 0.0022334 | 0.99864 | -0.0097225 | 0.99878 | -0.008718 | 0.82719
5 | -0.00092389 | -0.00022843 | 0.00092398 | 0.00022745 | 9.1863e-08 | -9.8145e-07 | 0.0013761 | 0.0013757 | 0.0013761 | 0.99826 | -0.012471 | 0.99836 | -0.01173 | 0.50965
6 | 0.00067155 | 0.00016519 | -0.00067154 | -0.00016552 | 1.6002e-08 | -3.291e-07 | 0.00099994 | 0.0010001 | 0.0010001 | 0.99826 | -0.012471 | 0.99823 | -0.012649 | 0.37039
7 | 0.00044809 | 0.00010762 | -0.00044807 | -0.00010877 | 2.4504e-08 | -1.1466e-06 | 0.00066626 | 0.00066665 | 0.00066665 | 0.99836 | -0.01173 | 0.9983 | -0.012154 | 0.24691
8 | -0.0013721 | -0.00033507 | 0.0013721 | 0.00033494 | 2.8867e-08 | -1.3398e-07 | 0.002042 | 0.0020419 | 0.002042 | 0.99836 | -0.01173 | 0.99838 | -0.01157 | 0.75628
9 | 0.00032237 | 7.8008e-05 | -0.00032235 | -7.9725e-05 | 1.8959e-08 | -1.7174e-06 | 0.00047958 | 0.00048017 | 0.00048017 | 0.99823 | -0.012649 | 0.99817 | -0.013094 | 0.17784
10 | 9.4713e-05 | 2.0211e-05 | -9.471e-05 | -2.3737e-05 | 3.3262e-09 | -3.5253e-06 | 0.00014002 | 0.00014117 | 0.00014117 | 0.9983 | -0.012154 | 0.99827 | -0.012445 | 0.052287
11 | 0.00032235 | 7.9725e-05 | -0.00032234 | -8.0619e-05 | 9.8827e-09 | -8.9347e-07 | 0.00048017 | 0.00048048 | 0.00048048 | 0.99817 | -0.013094 | 0.99814 | -0.013319 | 0.17796
12 | 0.00020104 | 5.0217e-05 | -0.00020104 | -5.0385e-05 | 7.2091e-10 | -1.6787e-07 | 0.00029965 | 0.00029971 | 0.00029971 | 0.99814 | -0.013319 | 0.99814 | -0.013345 | 0.111
13 | 0.0017602 | 0.0004399 | -0.0017598 | -0.00044093 | 3.857e-07 | -1.0225e-06 | 0.002625 | 0.0026254 | 0.0026254 | 0.99763 | -0.016693 | 0.9974 | -0.018281 | 0.97237
14 | -0.0057429 | -0.0014381 | 0.0057471 | 0.0014385 | 4.2381e-06 | 4.2031e-07 | 0.0085654 | 0.008565 | 0.0085654 | 0.99763 | -0.016693 | 0.99839 | -0.011353 | 3.1724
15 | 0.00084465 | 0.00021157 | -0.00084464 | -0.00021169 | 9.519e-09 | -1.2172e-07 | 0.0012601 | 0.0012601 | 0.0012601 | 0.9974 | -0.018281 | 0.99739 | -0.018362 | 0.46672
16 | 0.0011646 | 0.00029068 | -0.0011645 | -0.00029184 | 1.7629e-07 | -1.1584e-06 | 0.0017354 | 0.0017358 | 0.0017358 | 0.99839 | -0.011353 | 0.99823 | -0.01245 | 0.64289
17 | -0.0069118 | -0.0017292 | 0.0069167 | 0.0017301 | 4.9633e-06 | 9.2784e-07 | 0.0103 | 0.0103 | 0.0103 | 0.99839 | -0.011353 | 0.99913 | -0.0061479 | 3.8149
18 | -0.0083996 | -0.0021017 | 0.0084067 | 0.0021035 | 7.129e-06 | 1.7848e-06 | 0.012508 | 0.012508 | 0.012508 | 0.99913 | -0.0061479 | 1 | 0 | 4.6327
19 | 0.0067353 | 0.0016795 | -0.0067314 | -0.0016788 | 3.9043e-06 | 6.8446e-07 | 0.010019 | 0.01002 | 0.01002 | 1 | 0 | 0.9994 | -0.0042297 | 3.711
20 | 0.0061294 | 0.0015247 | -0.0061231 | -0.0015238 | 6.3482e-06 | 8.3757e-07 | 0.0091166 | 0.0091172 | 0.0091172 | 1 | 0 | 0.99893 | -0.0075933 | 3.3767
21 | -0.0032697 | -0.00080915 | 0.00327 | 0.000809 | 2.8511e-07 | -1.4266e-07 | 0.0048681 | 0.004868 | 0.0048681 | 0.99872 | -0.009136 | 0.99881 | -0.0084902 | 1.803
22 | 0.0021605 | 0.00053115 | -0.0021599 | -0.00053213 | 5.9852e-07 | -9.8327e-07 | 0.0032154 | 0.0032159 | 0.0032159 | 0.99872 | -0.009136 | 0.99843 | -0.011209 | 1.1911
23 | -0.0039869 | -0.00098867 | 0.0039874 | 0.00098856 | 4.8475e-07 | -1.0215e-07 | 0.005936 | 0.0059359 | 0.005936 | 0.99881 | -0.0084902 | 0.99893 | -0.0075933 | 2.1985
24 | 0.0017164 | 0.00042098 | -0.0017163 | -0.00042121 | 8.2358e-08 | -2.3274e-07 | 0.0025549 | 0.002555 | 0.002555 | 0.99843 | -0.011209 | 0.99838 | -0.01157 | 0.94628
25 | 0.0023112 | 0.00057104 | -0.0023098 | -0.00057298 | 1.4017e-06 | -1.9485e-06 | 0.0034383 | 0.0034392 | 0.0034392 | 0.9994 | -0.0042297 | 0.99878 | -0.008718 | 1.2738

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.022071 | 0.0053078

## res_load
| p_mw | q_mvar
0 | 0.0010839 | 0.00027165
1 | 0.00024158 | 6.0546e-05
2 | 0.00017369 | 4.3532e-05
3 | 0.00025233 | 6.324e-05
4 | 0.00034917 | 8.7509e-05
5 | 0.00035336 | 8.856e-05
6 | 9.471e-05 | 2.3737e-05
7 | 0.0001213 | 3.0401e-05
8 | 0.00020104 | 5.0385e-05
9 | 0.0039827 | 0.00099816
10 | 0.00091516 | 0.00022936
11 | 0.00084464 | 0.00021169
12 | 0.0011645 | 0.00029184
13 | 0.0014828 | 0.00037163
14 | 0.0011092 | 0.000278
15 | 0.00071687 | 0.00017966
16 | 0.00044351 | 0.00011115
17 | 0.0021357 | 0.00053525
18 | 0.00034424 | 8.6274e-05
19 | 0.0044202 | 0.0011078
20 | 0.00080952 | 0.00020288

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1