## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1506-9_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1506-9_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1506-9_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1506-9_0_2_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1506-9_0_2_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_1506-9_0_2_node_20 | 0.4 | n |  | TRUE
6 | bus_LV_1506-9_0_2_node_21 | 0.4 | n |  | TRUE
7 | bus_LV_1506-9_0_2_node_3 | 0.4 | n |  | TRUE
8 | bus_LV_1506-9_0_2_node_38 | 0.4 | n |  | TRUE
9 | bus_LV_1506-9_0_2_node_39 | 0.4 | n |  | TRUE
10 | bus_LV_1506-9_0_2_node_37 | 0.4 | n |  | TRUE
11 | bus_LV_1506-9_0_2_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_1506-9_0_2_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1506-9_0_2_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1506-9_0_2_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_1506-9_0_2_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_1506-9_0_2_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_1506-9_0_2_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_1506-9_0_2_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_1506-9_0_2_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_1506-9_0_2_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_1506-9_0_2_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_1506-9_0_2_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_1506-9_0_2_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_1506-9_0_2_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_1506-9_0_2_node_26 | 0.4 | n |  | TRUE
26 | bus_LV_1506-9_0_2_node_28 | 0.4 | n |  | TRUE
27 | bus_LV_1506-9_0_2_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_1506-9_0_2_node_36 | 0.4 | n |  | TRUE
29 | bus_LV_1506-9_0_2_node_171 | 0.4 | n |  | TRUE
30 | bus_LV_1506-9_0_2_node_169 | 0.4 | n |  | TRUE
31 | bus_LV_1506-9_0_2_node_48 | 0.4 | n |  | TRUE
32 | bus_LV_1506-9_0_2_node_60 | 0.4 | n |  | TRUE
33 | bus_LV_1506-9_0_2_node_22 | 0.4 | n |  | TRUE
34 | bus_LV_1506-9_0_2_node_152 | 0.4 | n |  | TRUE
35 | bus_LV_1506-9_0_2_node_34 | 0.4 | n |  | TRUE
36 | bus_LV_1506-9_0_2_node_153 | 0.4 | n |  | TRUE
37 | bus_LV_1506-9_0_2_node_35 | 0.4 | n |  | TRUE
38 | bus_LV_1506-9_0_2_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_1506-9_0_2_node_23 | 0.4 | n |  | TRUE
40 | bus_LV_1506-9_0_2_node_25 | 0.4 | n |  | TRUE
41 | bus_LV_1506-9_0_2_node_27 | 0.4 | n |  | TRUE
42 | bus_LV_1506-9_0_2_node_30 | 0.4 | n |  | TRUE
43 | bus_LV_1506-9_0_2_node_31 | 0.4 | n |  | TRUE
44 | bus_LV_1506-9_0_2_node_29 | 0.4 | n |  | TRUE
45 | bus_LV_1506-9_0_2_node_33 | 0.4 | n |  | TRUE
46 | bus_LV_1506-9_0_2_node_139 | 0.4 | n |  | TRUE
47 | bus_LV_1506-9_0_2_node_117 | 0.4 | n |  | TRUE
48 | bus_LV_1506-9_0_2_node_88 | 0.4 | n |  | TRUE
49 | bus_LV_1506-9_0_2_node_89 | 0.4 | n |  | TRUE
50 | bus_LV_1506-9_0_2_node_46 | 0.4 | n |  | TRUE
51 | bus_LV_1506-9_0_2_node_44 | 0.4 | n |  | TRUE
52 | bus_LV_1506-9_0_2_node_113 | 0.4 | n |  | TRUE
53 | bus_LV_1506-9_0_2_node_55 | 0.4 | n |  | TRUE
54 | bus_LV_1506-9_0_2_node_64 | 0.4 | n |  | TRUE
55 | bus_LV_1506-9_0_2_node_112 | 0.4 | n |  | TRUE
56 | bus_LV_1506-9_0_2_node_40 | 0.4 | n |  | TRUE
57 | bus_LV_1506-9_0_2_node_41 | 0.4 | n |  | TRUE
58 | bus_LV_1506-9_0_2_node_42 | 0.4 | n |  | TRUE
59 | bus_LV_1506-9_0_2_node_43 | 0.4 | n |  | TRUE
60 | bus_LV_1506-9_0_2_node_45 | 0.4 | n |  | TRUE
61 | bus_LV_1506-9_0_2_node_57 | 0.4 | n |  | TRUE
62 | bus_LV_1506-9_0_2_node_58 | 0.4 | n |  | TRUE
63 | bus_LV_1506-9_0_2_node_56 | 0.4 | n |  | TRUE
64 | bus_LV_1506-9_0_2_node_53 | 0.4 | n |  | TRUE
65 | bus_LV_1506-9_0_2_node_52 | 0.4 | n |  | TRUE
66 | bus_LV_1506-9_0_2_node_54 | 0.4 | n |  | TRUE
67 | bus_LV_1506-9_0_2_node_47 | 0.4 | n |  | TRUE
68 | bus_LV_1506-9_0_2_node_49 | 0.4 | n |  | TRUE
69 | bus_LV_1506-9_0_2_node_50 | 0.4 | n |  | TRUE
70 | bus_LV_1506-9_0_2_node_51 | 0.4 | n |  | TRUE
71 | bus_LV_1506-9_0_2_node_110 | 0.4 | n |  | TRUE
72 | bus_LV_1506-9_0_2_node_108 | 0.4 | n |  | TRUE
73 | bus_LV_1506-9_0_2_node_61 | 0.4 | n |  | TRUE
74 | bus_LV_1506-9_0_2_node_62 | 0.4 | n |  | TRUE
75 | bus_LV_1506-9_0_2_node_63 | 0.4 | n |  | TRUE
76 | bus_LV_1506-9_0_2_node_150 | 0.4 | n |  | TRUE
77 | bus_LV_1506-9_0_2_node_151 | 0.4 | n |  | TRUE
78 | bus_LV_1506-9_0_2_node_65 | 0.4 | n |  | TRUE
79 | bus_LV_1506-9_0_2_node_66 | 0.4 | n |  | TRUE
80 | bus_LV_1506-9_0_2_node_67 | 0.4 | n |  | TRUE
81 | bus_LV_1506-9_0_2_node_68 | 0.4 | n |  | TRUE
82 | bus_LV_1506-9_0_2_node_69 | 0.4 | n |  | TRUE
83 | bus_LV_1506-9_0_2_node_106 | 0.4 | n |  | TRUE
84 | bus_LV_1506-9_0_2_node_101 | 0.4 | n |  | TRUE
85 | bus_LV_1506-9_0_2_node_104 | 0.4 | n |  | TRUE
86 | bus_LV_1506-9_0_2_node_100 | 0.4 | n |  | TRUE
87 | bus_LV_1506-9_0_2_node_70 | 0.4 | n |  | TRUE
88 | bus_LV_1506-9_0_2_node_71 | 0.4 | n |  | TRUE
89 | bus_LV_1506-9_0_2_node_72 | 0.4 | n |  | TRUE
90 | bus_LV_1506-9_0_2_node_73 | 0.4 | n |  | TRUE
91 | bus_LV_1506-9_0_2_node_74 | 0.4 | n |  | TRUE
92 | bus_LV_1506-9_0_2_node_95 | 0.4 | n |  | TRUE
93 | bus_LV_1506-9_0_2_node_76 | 0.4 | n |  | TRUE
94 | bus_LV_1506-9_0_2_node_96 | 0.4 | n |  | TRUE
95 | bus_LV_1506-9_0_2_node_97 | 0.4 | n |  | TRUE
96 | bus_LV_1506-9_0_2_node_75 | 0.4 | n |  | TRUE
97 | bus_LV_1506-9_0_2_node_77 | 0.4 | n |  | TRUE
98 | bus_LV_1506-9_0_2_node_78 | 0.4 | n |  | TRUE
99 | bus_LV_1506-9_0_2_node_80 | 0.4 | n |  | TRUE
100 | bus_LV_1506-9_0_2_node_79 | 0.4 | n |  | TRUE
101 | bus_LV_1506-9_0_2_node_81 | 0.4 | n |  | TRUE
102 | bus_LV_1506-9_0_2_node_82 | 0.4 | n |  | TRUE
103 | bus_LV_1506-9_0_2_node_93 | 0.4 | n |  | TRUE
104 | bus_LV_1506-9_0_2_node_103 | 0.4 | n |  | TRUE
105 | bus_LV_1506-9_0_2_node_91 | 0.4 | n |  | TRUE
106 | bus_LV_1506-9_0_2_node_90 | 0.4 | n |  | TRUE
107 | bus_LV_1506-9_0_2_node_92 | 0.4 | n |  | TRUE
108 | bus_LV_1506-9_0_2_node_94 | 0.4 | n |  | TRUE
109 | bus_LV_1506-9_0_2_node_158 | 0.4 | n |  | TRUE
110 | bus_LV_1506-9_0_2_node_159 | 0.4 | n |  | TRUE
111 | bus_LV_1506-9_0_2_node_165 | 0.4 | n |  | TRUE
112 | bus_LV_1506-9_0_2_node_166 | 0.4 | n |  | TRUE
113 | bus_LV_1506-9_0_2_node_167 | 0.4 | n |  | TRUE
114 | bus_LV_1506-9_0_2_node_109 | 0.4 | n |  | TRUE
115 | bus_LV_1506-9_0_2_node_102 | 0.4 | n |  | TRUE
116 | bus_LV_1506-9_0_2_node_164 | 0.4 | n |  | TRUE
117 | bus_LV_1506-9_0_2_node_160 | 0.4 | n |  | TRUE
118 | bus_LV_1506-9_0_2_node_161 | 0.4 | n |  | TRUE
119 | bus_LV_1506-9_0_2_node_170 | 0.4 | n |  | TRUE
120 | bus_LV_1506-9_0_2_node_168 | 0.4 | n |  | TRUE
121 | bus_LV_1506-9_0_2_node_162 | 0.4 | n |  | TRUE
122 | bus_LV_1506-9_0_2_node_163 | 0.4 | n |  | TRUE
123 | bus_LV_1506-9_0_2_node_105 | 0.4 | n |  | TRUE
124 | bus_LV_1506-9_0_2_node_107 | 0.4 | n |  | TRUE
125 | bus_LV_1506-9_0_2_node_111 | 0.4 | n |  | TRUE
126 | bus_MV_143_0_node_159 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1506-9_0_2_load_0 | 0 | 0.0006932 | 0.00017373 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1506-9_0_2_load_20 | 5 | 0.0029786 | 0.00074651 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1506-9_0_2_load_21 | 6 | 0.0017237 | 0.000432 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1506-9_0_2_load_3 | 7 | 0.0022326 | 0.00055953 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1506-9_0_2_load_39 | 9 | 0.0035915 | 0.00090012 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1506-9_0_2_load_37 | 10 | 0.00085482 | 0.00021424 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1506-9_0_2_load_5 | 11 | 0.00040151 | 0.00010063 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1506-9_0_2_load_9 | 13 | 0.00060521 | 0.00015168 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1506-9_0_2_load_10 | 15 | 0.00085988 | 0.00021551 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1506-9_0_2_load_11 | 16 | 0.0011378 | 0.00028516 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1506-9_0_2_load_13 | 18 | 0.0016293 | 0.00040835 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1506-9_0_2_load_14 | 19 | 0.00053285 | 0.00013354 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1506-9_0_2_load_15 | 20 | 0.0015674 | 0.00039282 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1506-9_0_2_load_19 | 21 | 0.00056844 | 0.00014246 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1506-9_0_2_load_16 | 22 | 0.0016852 | 0.00042236 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1506-9_0_2_load_18 | 23 | 0.0039227 | 0.00098313 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1506-9_0_2_load_26 | 25 | 0.0029234 | 0.00073268 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1506-9_0_2_load_28 | 26 | 0.0038515 | 0.00096527 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1506-9_0_2_load_24 | 27 | 0.0020998 | 0.00052626 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1506-9_0_2_load_171 | 29 | 0.0017921 | 0.00044915 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1506-9_0_2_load_169 | 30 | 0.0014953 | 0.00037476 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1506-9_0_2_load_48 | 31 | 0.00060873 | 0.00015256 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1506-9_0_2_load_22 | 33 | 0.001953 | 0.00048946 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1506-9_0_2_load_152 | 34 | 0.0021408 | 0.00053654 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1506-9_0_2_load_153 | 36 | 0.00075764 | 0.00018988 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1506-9_0_2_load_35 | 37 | 0.0011226 | 0.00028136 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1506-9_0_2_load_23 | 39 | 0.0024155 | 0.00060537 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1506-9_0_2_load_25 | 40 | 0.0041351 | 0.0010364 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1506-9_0_2_load_30 | 42 | 0.002286 | 0.00057293 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1506-9_0_2_load_31 | 43 | 0.0027821 | 0.00069726 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1506-9_0_2_load_29 | 44 | 0.0048619 | 0.0012185 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1506-9_0_2_load_33 | 45 | 0.0025921 | 0.00064965 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1506-9_0_2_load_139 | 46 | 0.0014233 | 0.00035671 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1506-9_0_2_load_117 | 47 | 0.0025308 | 0.00063429 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1506-9_0_2_load_88 | 48 | 0.0014162 | 0.00035494 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1506-9_0_2_load_46 | 50 | 0.0015428 | 0.00038665 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1506-9_0_2_load_44 | 51 | 0.0036299 | 0.00090974 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1506-9_0_2_load_55 | 53 | 0.0011481 | 0.00028775 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1506-9_0_2_load_64 | 54 | 0.0015141 | 0.00037947 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1506-9_0_2_load_112 | 55 | 0.0016853 | 0.00042238 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1506-9_0_2_load_40 | 56 | 0.0018086 | 0.00045329 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1506-9_0_2_load_41 | 57 | 0.0018824 | 0.00047177 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1506-9_0_2_load_42 | 58 | 0.001552 | 0.00038896 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1506-9_0_2_load_43 | 59 | 0.001238 | 0.00031027 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1506-9_0_2_load_45 | 60 | 0.001553 | 0.00038923 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1506-9_0_2_load_57 | 61 | 0.0014009 | 0.00035111 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1506-9_0_2_load_58 | 62 | 0.0011145 | 0.00027932 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1506-9_0_2_load_56 | 63 | 0.0017528 | 0.0004393 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1506-9_0_2_load_53 | 64 | 0.0021619 | 0.00054182 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1506-9_0_2_load_52 | 65 | 0.0027659 | 0.00069321 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1506-9_0_2_load_54 | 66 | 0.0021847 | 0.00054753 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1506-9_0_2_load_47 | 67 | 0.0011632 | 0.00029151 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1506-9_0_2_load_49 | 68 | 0.0016955 | 0.00042494 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1506-9_0_2_load_50 | 69 | 0.0009185 | 0.0002302 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1506-9_0_2_load_51 | 70 | 0.0020917 | 0.00052424 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1506-9_0_2_load_110 | 71 | 0.00053581 | 0.00013429 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1506-9_0_2_load_108 | 72 | 0.00055002 | 0.00013785 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1506-9_0_2_load_61 | 73 | 0.0024001 | 0.00060152 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1506-9_0_2_load_63 | 75 | 0.0020556 | 0.00051519 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1506-9_0_2_load_150 | 76 | 0.0014402 | 0.00036095 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1506-9_0_2_load_151 | 77 | 0.0015511 | 0.00038873 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1506-9_0_2_load_65 | 78 | 0.00047981 | 0.00012025 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1506-9_0_2_load_66 | 79 | 0.00067519 | 0.00016922 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1506-9_0_2_load_67 | 80 | 0.00093284 | 0.00023379 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1506-9_0_2_load_106 | 83 | 0.00038703 | 9.6999e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1506-9_0_2_load_101 | 84 | 0.00062142 | 0.00015574 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1506-9_0_2_load_104 | 85 | 0.00026298 | 6.5909e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1506-9_0_2_load_100 | 86 | 0.00054352 | 0.00013622 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1506-9_0_2_load_70 | 87 | 0.001397 | 0.00035012 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1506-9_0_2_load_71 | 88 | 0.0013055 | 0.00032719 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1506-9_0_2_load_72 | 89 | 0.0022284 | 0.0005585 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1506-9_0_2_load_73 | 90 | 0.0029441 | 0.00073787 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1506-9_0_2_load_76 | 93 | 0.0013598 | 0.0003408 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1506-9_0_2_load_96 | 94 | 0.0030392 | 0.0007617 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1506-9_0_2_load_97 | 95 | 0.0011413 | 0.00028603 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1506-9_0_2_load_75 | 96 | 0.0015021 | 0.00037646 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1506-9_0_2_load_77 | 97 | 0.00034647 | 8.6833e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1506-9_0_2_load_78 | 98 | 0.0011151 | 0.00027947 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1506-9_0_2_load_80 | 99 | 0.00086259 | 0.00021618 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1506-9_0_2_load_79 | 100 | 0.0008714 | 0.00021839 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1506-9_0_2_load_81 | 101 | 0.0014773 | 0.00037024 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1506-9_0_2_load_82 | 102 | 0.00095926 | 0.00024041 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1506-9_0_2_load_93 | 103 | 0.0017808 | 0.00044632 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1506-9_0_2_load_91 | 105 | 0.001034 | 0.00025915 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1506-9_0_2_load_90 | 106 | 0.00073095 | 0.00018319 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1506-9_0_2_load_92 | 107 | 0.0019711 | 0.00049399 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1506-9_0_2_load_94 | 108 | 0.00069873 | 0.00017512 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1506-9_0_2_load_158 | 109 | 0.0010975 | 0.00027505 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1506-9_0_2_load_159 | 110 | 0.00066851 | 0.00016754 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1506-9_0_2_load_165 | 111 | 0.0012897 | 0.00032322 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1506-9_0_2_load_166 | 112 | 0.0021596 | 0.00054125 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1506-9_0_2_load_167 | 113 | 0.0033111 | 0.00082984 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1506-9_0_2_load_109 | 114 | 0.0026026 | 0.00065227 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1506-9_0_2_load_102 | 115 | 0.0043827 | 0.0010984 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1506-9_0_2_load_164 | 116 | 0.0010728 | 0.00026886 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1506-9_0_2_load_160 | 117 | 0.00058845 | 0.00014748 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1506-9_0_2_load_161 | 118 | 0.00067085 | 0.00016813 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1506-9_0_2_load_170 | 119 | 0.001701 | 0.0004263 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1506-9_0_2_load_168 | 120 | 0.001898 | 0.00047568 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1506-9_0_2_load_162 | 121 | 0.00067391 | 0.0001689 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1506-9_0_2_load_163 | 122 | 0.00035239 | 8.8317e-05 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1506-9_0_2_load_105 | 123 | 0.00095871 | 0.00024028 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1506-9_0_2_load_107 | 124 | 0.00066842 | 0.00016752 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1506-9_0_2_load_111 | 125 | 0.00039556 | 9.9136e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 29 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1506-9_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.016372 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1506-9_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.010382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1506-9_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.022327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1506-9_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.014482 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1506-9_0_2_line_4 | NAYY 4x150 SE | 3 | 7 | 0.030114 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1506-9_0_2_line_5 | NAYY 4x150 SE | 4 | 13 | 0.015091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1506-9_0_2_line_6 | NAYY 4x150 SE | 5 | 6 | 0.048314 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1506-9_0_2_line_7 | NAYY 4x150 SE | 6 | 33 | 0.032211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1506-9_0_2_line_8 | NAYY 4x150 SE | 6 | 34 | 0.35089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1506-9_0_2_line_9 | NAYY 4x150 SE | 8 | 9 | 0.051807 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1506-9_0_2_line_10 | NAYY 4x150 SE | 8 | 10 | 0.011901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1506-9_0_2_line_11 | NAYY 4x150 SE | 9 | 12 | 0.10781 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1506-9_0_2_line_12 | NAYY 4x150 SE | 11 | 12 | 0.011237 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1506-9_0_2_line_13 | NAYY 4x150 SE | 12 | 14 | 0.023336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1506-9_0_2_line_14 | NAYY 4x150 SE | 13 | 14 | 0.018348 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1506-9_0_2_line_15 | NAYY 4x150 SE | 14 | 15 | 0.011931 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1506-9_0_2_line_16 | NAYY 4x150 SE | 15 | 16 | 0.029484 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1506-9_0_2_line_17 | NAYY 4x150 SE | 16 | 17 | 0.026564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1506-9_0_2_line_18 | NAYY 4x150 SE | 17 | 18 | 0.03286 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1506-9_0_2_line_19 | NAYY 4x150 SE | 17 | 19 | 0.023248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1506-9_0_2_line_20 | NAYY 4x150 SE | 18 | 20 | 0.024127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1506-9_0_2_line_21 | NAYY 4x150 SE | 19 | 21 | 0.046134 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1506-9_0_2_line_22 | NAYY 4x150 SE | 20 | 22 | 0.056406 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1506-9_0_2_line_23 | NAYY 4x150 SE | 21 | 23 | 0.022204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1506-9_0_2_line_24 | NAYY 4x150 SE | 22 | 24 | 0.016332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1506-9_0_2_line_25 | NAYY 4x150 SE | 24 | 28 | 0.070636 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1506-9_0_2_line_26 | NAYY 4x150 SE | 25 | 26 | 0.02974 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1506-9_0_2_line_27 | NAYY 4x150 SE | 25 | 27 | 0.015674 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1506-9_0_2_line_28 | NAYY 4x150 SE | 26 | 44 | 0.024639 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1506-9_0_2_line_29 | NAYY 4x150 SE | 27 | 39 | 0.011316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1506-9_0_2_line_30 | NAYY 4x150 SE | 28 | 31 | 0.0071989 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1506-9_0_2_line_31 | NAYY 4x150 SE | 28 | 32 | 0.087239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1506-9_0_2_line_32 | NAYY 4x150 SE | 29 | 30 | 0.0033016 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
33 | LV_1506-9_0_2_line_33 | NAYY 4x150 SE | 30 | 120 | 0.0073198 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
34 | LV_1506-9_0_2_line_34 | NAYY 4x150 SE | 31 | 50 | 0.016626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1506-9_0_2_line_35 | NAYY 4x150 SE | 32 | 51 | 0.016318 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
36 | LV_1506-9_0_2_line_36 | NAYY 4x150 SE | 33 | 35 | 0.041425 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1506-9_0_2_line_37 | NAYY 4x150 SE | 34 | 36 | 0.027277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1506-9_0_2_line_38 | NAYY 4x150 SE | 35 | 37 | 0.036548 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1506-9_0_2_line_39 | NAYY 4x150 SE | 35 | 38 | 0.041594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1506-9_0_2_line_40 | NAYY 4x150 SE | 37 | 48 | 0.026375 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1506-9_0_2_line_41 | NAYY 4x150 SE | 38 | 46 | 0.012454 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1506-9_0_2_line_42 | NAYY 4x150 SE | 38 | 41 | 0.023558 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1506-9_0_2_line_43 | NAYY 4x150 SE | 39 | 40 | 0.014795 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1506-9_0_2_line_44 | NAYY 4x150 SE | 41 | 42 | 0.0051602 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1506-9_0_2_line_45 | NAYY 4x150 SE | 41 | 43 | 0.012738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1506-9_0_2_line_46 | NAYY 4x150 SE | 41 | 44 | 0.03427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1506-9_0_2_line_47 | NAYY 4x150 SE | 43 | 45 | 0.05942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1506-9_0_2_line_48 | NAYY 4x150 SE | 46 | 47 | 0.0030732 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1506-9_0_2_line_49 | NAYY 4x150 SE | 47 | 91 | 0.020451 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1506-9_0_2_line_50 | NAYY 4x150 SE | 48 | 49 | 0.001139 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1506-9_0_2_line_51 | NAYY 4x150 SE | 49 | 81 | 0.014874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1506-9_0_2_line_52 | NAYY 4x150 SE | 50 | 67 | 0.015142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1506-9_0_2_line_53 | NAYY 4x150 SE | 51 | 58 | 0.042124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
54 | LV_1506-9_0_2_line_54 | NAYY 4x150 SE | 52 | 53 | 0.16017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
55 | LV_1506-9_0_2_line_55 | NAYY 4x150 SE | 52 | 54 | 0.0087844 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1506-9_0_2_line_56 | NAYY 4x150 SE | 52 | 55 | 0.011116 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
57 | LV_1506-9_0_2_line_57 | NAYY 4x150 SE | 53 | 63 | 0.013906 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1506-9_0_2_line_58 | NAYY 4x150 SE | 53 | 66 | 0.042446 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
59 | LV_1506-9_0_2_line_59 | NAYY 4x150 SE | 54 | 74 | 0.0087245 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1506-9_0_2_line_60 | NAYY 4x150 SE | 55 | 94 | 0.041002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
61 | LV_1506-9_0_2_line_61 | NAYY 4x150 SE | 56 | 57 | 0.012219 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
62 | LV_1506-9_0_2_line_62 | NAYY 4x150 SE | 56 | 58 | 0.0054547 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
63 | LV_1506-9_0_2_line_63 | NAYY 4x150 SE | 57 | 59 | 0.0050584 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
64 | LV_1506-9_0_2_line_64 | NAYY 4x150 SE | 59 | 60 | 0.011017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
65 | LV_1506-9_0_2_line_65 | NAYY 4x150 SE | 60 | 64 | 0.054149 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
66 | LV_1506-9_0_2_line_66 | NAYY 4x150 SE | 61 | 62 | 0.020615 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1506-9_0_2_line_67 | NAYY 4x150 SE | 61 | 63 | 0.025853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1506-9_0_2_line_68 | NAYY 4x150 SE | 64 | 66 | 0.0067666 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
69 | LV_1506-9_0_2_line_69 | NAYY 4x150 SE | 64 | 65 | 0.0073217 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1506-9_0_2_line_70 | NAYY 4x150 SE | 67 | 68 | 0.023375 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1506-9_0_2_line_71 | NAYY 4x150 SE | 68 | 69 | 0.030348 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1506-9_0_2_line_72 | NAYY 4x150 SE | 69 | 70 | 0.021444 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1506-9_0_2_line_73 | NAYY 4x150 SE | 71 | 72 | 0.021059 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1506-9_0_2_line_74 | NAYY 4x150 SE | 72 | 114 | 0.015436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1506-9_0_2_line_75 | NAYY 4x150 SE | 73 | 74 | 0.019696 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1506-9_0_2_line_76 | NAYY 4x150 SE | 74 | 75 | 0.002402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1506-9_0_2_line_77 | NAYY 4x150 SE | 75 | 76 | 0.005208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1506-9_0_2_line_78 | NAYY 4x150 SE | 76 | 77 | 0.0067366 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1506-9_0_2_line_79 | NAYY 4x150 SE | 78 | 79 | 0.0026274 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1506-9_0_2_line_80 | NAYY 4x150 SE | 78 | 80 | 0.037808 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1506-9_0_2_line_81 | NAYY 4x150 SE | 79 | 81 | 0.043923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1506-9_0_2_line_82 | NAYY 4x150 SE | 80 | 82 | 0.043729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1506-9_0_2_line_83 | NAYY 4x150 SE | 81 | 83 | 0.021132 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1506-9_0_2_line_84 | NAYY 4x150 SE | 82 | 84 | 0.034972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1506-9_0_2_line_85 | NAYY 4x150 SE | 83 | 85 | 0.0090872 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1506-9_0_2_line_86 | NAYY 4x150 SE | 84 | 86 | 0.0085095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1506-9_0_2_line_87 | NAYY 4x150 SE | 85 | 123 | 0.012353 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1506-9_0_2_line_88 | NAYY 4x150 SE | 87 | 88 | 0.018037 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1506-9_0_2_line_89 | NAYY 4x150 SE | 87 | 89 | 0.0044321 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1506-9_0_2_line_90 | NAYY 4x150 SE | 88 | 90 | 0.014083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1506-9_0_2_line_91 | NAYY 4x150 SE | 89 | 91 | 0.031972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1506-9_0_2_line_92 | NAYY 4x150 SE | 90 | 92 | 0.017645 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1506-9_0_2_line_93 | NAYY 4x150 SE | 91 | 93 | 0.0088317 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1506-9_0_2_line_94 | NAYY 4x150 SE | 92 | 94 | 0.0088383 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
95 | LV_1506-9_0_2_line_95 | NAYY 4x150 SE | 92 | 95 | 0.011935 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
96 | LV_1506-9_0_2_line_96 | NAYY 4x150 SE | 93 | 96 | 0.0077137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1506-9_0_2_line_97 | NAYY 4x150 SE | 95 | 119 | 0.0067289 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
98 | LV_1506-9_0_2_line_98 | NAYY 4x150 SE | 96 | 97 | 0.014573 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1506-9_0_2_line_99 | NAYY 4x150 SE | 97 | 98 | 0.01264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1506-9_0_2_line_100 | NAYY 4x150 SE | 98 | 99 | 0.0057011 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1506-9_0_2_line_101 | NAYY 4x150 SE | 99 | 100 | 0.016994 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1506-9_0_2_line_102 | NAYY 4x150 SE | 100 | 101 | 0.0094929 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1506-9_0_2_line_103 | NAYY 4x150 SE | 101 | 102 | 0.015161 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1506-9_0_2_line_104 | NAYY 4x150 SE | 102 | 103 | 0.0038733 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1506-9_0_2_line_105 | NAYY 4x150 SE | 103 | 104 | 0.091402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1506-9_0_2_line_106 | NAYY 4x150 SE | 103 | 105 | 0.033204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1506-9_0_2_line_107 | NAYY 4x150 SE | 104 | 116 | 0.058246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1506-9_0_2_line_108 | NAYY 4x150 SE | 104 | 111 | 0.034387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1506-9_0_2_line_109 | NAYY 4x150 SE | 104 | 115 | 0.012812 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1506-9_0_2_line_110 | NAYY 4x150 SE | 105 | 106 | 0.020163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_1506-9_0_2_line_111 | NAYY 4x150 SE | 106 | 107 | 0.0011431 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_1506-9_0_2_line_112 | NAYY 4x150 SE | 107 | 108 | 0.022709 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_1506-9_0_2_line_113 | NAYY 4x150 SE | 108 | 114 | 0.039599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_1506-9_0_2_line_114 | NAYY 4x150 SE | 109 | 110 | 0.017484 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_1506-9_0_2_line_115 | NAYY 4x150 SE | 110 | 117 | 0.012615 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_1506-9_0_2_line_116 | NAYY 4x150 SE | 111 | 112 | 0.022047 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_1506-9_0_2_line_117 | NAYY 4x150 SE | 112 | 113 | 0.015764 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_1506-9_0_2_line_118 | NAYY 4x150 SE | 116 | 122 | 0.040653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_1506-9_0_2_line_119 | NAYY 4x150 SE | 117 | 118 | 0.013998 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_1506-9_0_2_line_120 | NAYY 4x150 SE | 118 | 121 | 0.0077372 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_1506-9_0_2_line_121 | NAYY 4x150 SE | 119 | 120 | 0.0074105 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
122 | LV_1506-9_0_2_line_122 | NAYY 4x150 SE | 121 | 122 | 0.023162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_1506-9_0_2_line_123 | NAYY 4x150 SE | 123 | 124 | 0.0010159 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_1506-9_0_2_line_124 | NAYY 4x150 SE | 124 | 125 | 9.3223e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1506-9_0_2_trafo_171 | 0.25 MVA 20/0.4 kV | 126 | 29 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2665531.7762 | 1199134.2669 | 2665541.2842 | 1199137.284 | 2665546.6809 | 1199140.719
1 | 2665555.9698 | 1199145.1942 | 2665551.0239 | 1199143.4834 | 2665546.6809 | 1199140.719
2 | 2665525.5916 | 1199155.2449 | 2665528.7908 | 1199150.9775 | 2665530.1193 | 1199145.7889 | 2665531.7762 | 1199134.2669
3 | 2665555.9698 | 1199145.1942 | 2665556.1765 | 1199159.6717
4 | 2665525.5916 | 1199155.2449 | 2665511.5231 | 1199146.6079 | 2665501.553 | 1199138.505 | 2665501.0062 | 1199137.98
5 | 2665556.1765 | 1199159.6717 | 2665571.1504 | 1199157.7917
6 | 2665813.282 | 1199410.5649 | 2665820.2739 | 1199414.7136 | 2665832.3637 | 1199430.067 | 2665836.146 | 1199450.3594
7 | 2665836.146 | 1199450.3594 | 2665842.0482 | 1199482.0254
8 | 2665836.146 | 1199450.3594 | 2666143.1801 | 1199280.4893
9 | 2665553.2454 | 1198997.1874 | 2665553.3816 | 1199009.0626 | 2665558.7216 | 1199016.5145 | 2665587.0148 | 1199025.8303 | 2665587.683 | 1199026.541
10 | 2665553.2454 | 1198997.1874 | 2665564.9024 | 1198999.5863
11 | 2665590.3016 | 1199134.3197 | 2665587.683 | 1199026.541
12 | 2665590.3016 | 1199134.3197 | 2665585.4687 | 1199136.8794 | 2665579.9383 | 1199138.5185
13 | 2665589.4449 | 1199157.5686 | 2665588.8913 | 1199151.1143 | 2665590.3016 | 1199134.3197
14 | 2665589.4449 | 1199157.5686 | 2665576.7795 | 1199157.085 | 2665571.1504 | 1199157.7917
15 | 2665589.4449 | 1199157.5686 | 2665590.4535 | 1199169.4571
16 | 2665590.4535 | 1199169.4571 | 2665591.7845 | 1199185.144 | 2665594.6397 | 1199198.5852
17 | 2665600.3449 | 1199224.528 | 2665598.1995 | 1199215.3434 | 2665594.6397 | 1199198.5852
18 | 2665600.3449 | 1199224.528 | 2665575.4632 | 1199245.9908
19 | 2665600.3449 | 1199224.528 | 2665611.5467 | 1199243.8735 | 2665612.1817 | 1199244.5023
20 | 2665575.4632 | 1199245.9908 | 2665557.1941 | 1199261.7495
21 | 2665612.1817 | 1199244.5023 | 2665634.5963 | 1199266.6956 | 2665645.8825 | 1199275.9436
22 | 2665513.7365 | 1199297.5541 | 2665520.6122 | 1199293.3948 | 2665552.8993 | 1199265.4542 | 2665557.1941 | 1199261.7495
23 | 2665663.1916 | 1199289.8314 | 2665661.5373 | 1199288.7712 | 2665645.8825 | 1199275.9436
24 | 2665499.7628 | 1199306.0072 | 2665513.7365 | 1199297.5541
25 | 2665484.9329 | 1199371.0501 | 2665485.6952 | 1199360.5522 | 2665485.7609 | 1199340.6633 | 2665485.8822 | 1199337.9297 | 2665486.7113 | 1199318.5495 | 2665499.7628 | 1199306.0072
26 | 2665758.6067 | 1199472.2318 | 2665752.4778 | 1199476.8714 | 2665749.7228 | 1199480.2098 | 2665748.1994 | 1199484.4177 | 2665748.2528 | 1199487.8648 | 2665748.606 | 1199491.0595 | 2665750.2435 | 1199495.1688 | 2665751.3708 | 1199497.0163
27 | 2665772.241 | 1199465.4042 | 2665769.2166 | 1199465.5488 | 2665765.6075 | 1199466.9321 | 2665758.6067 | 1199472.2318
28 | 2665751.3708 | 1199497.0163 | 2665754.9629 | 1199502.9031 | 2665762.2136 | 1199515.8684 | 2665763.6643 | 1199518.3655
29 | 2665781.8535 | 1199471.0047 | 2665780.759 | 1199469.7671 | 2665776.4211 | 1199466.7954 | 2665772.241 | 1199465.4042 | 2665772.241 | 1199465.4042
30 | 2665484.9329 | 1199371.0501 | 2665490.3156 | 1199375.8304
31 | 2665484.9329 | 1199371.0501 | 2665482.5562 | 1199375.3155 | 2665470.7678 | 1199390.74 | 2665453.7258 | 1199399.8922 | 2665439.4326 | 1199406.2618 | 2665416.4808 | 1199422.4758
32 | 2665693.668 | 1199523.7751 | 2665696.8579 | 1199524.6266
33 | 2665703.9301 | 1199526.5143 | 2665696.8579 | 1199524.6266
34 | 2665504.9908 | 1199382.3543 | 2665500.8377 | 1199382.3088 | 2665493.8689 | 1199378.986 | 2665490.3156 | 1199375.8304
35 | 2665416.4808 | 1199422.4758 | 2665417.9873 | 1199428.8406 | 2665420.0121 | 1199430.2858 | 2665427.1765 | 1199428.9412
36 | 2665849.2427 | 1199522.8192 | 2665845.3043 | 1199499.4953 | 2665842.0482 | 1199482.0254
37 | 2666143.1801 | 1199280.4893 | 2666138.296 | 1199264.3333 | 2666132.7428 | 1199255.5411
38 | 2665849.2427 | 1199522.8192 | 2665857.5534 | 1199558.4097 | 2665857.5534 | 1199558.4097
39 | 2665849.2427 | 1199522.8192 | 2665845.379 | 1199523.8106 | 2665836.6811 | 1199528.1952 | 2665829.1978 | 1199532.2152 | 2665819.387 | 1199539.4782 | 2665814.4404 | 1199544.7713
40 | 2665857.5534 | 1199558.4097 | 2665867.3926 | 1199582.8812
41 | 2665814.4404 | 1199544.7713 | 2665812.6324 | 1199547.8533 | 2665809.9599 | 1199555.4506 | 2665809.662 | 1199556.2222
42 | 2665792.8845 | 1199535.1284 | 2665814.4404 | 1199544.7713
43 | 2665781.8535 | 1199471.0047 | 2665785.8429 | 1199475.5154 | 2665788.2078 | 1199480.6333 | 2665788.907 | 1199483.6894
44 | 2665792.8845 | 1199535.1284 | 2665793.6914 | 1199532.38 | 2665792.9166 | 1199530.2188
45 | 2665792.8845 | 1199535.1284 | 2665782.3791 | 1199530.788 | 2665781.1276 | 1199530.227
46 | 2665792.8845 | 1199535.1284 | 2665782.3791 | 1199530.788 | 2665773.8098 | 1199526.947 | 2665767.7139 | 1199523.211 | 2665764.7617 | 1199520.2546 | 2665763.6643 | 1199518.3655
47 | 2665748.1994 | 1199484.4177 | 2665748.2528 | 1199487.8648 | 2665748.606 | 1199491.0595 | 2665750.2435 | 1199495.1688 | 2665754.9629 | 1199502.9031 | 2665762.2136 | 1199515.8684 | 2665764.7617 | 1199520.2546 | 2665767.7139 | 1199523.211 | 2665773.8098 | 1199526.947 | 2665781.1276 | 1199530.227
48 | 2665809.662 | 1199556.2222 | 2665808.5552 | 1199559.0892
49 | 2665801.1896 | 1199578.1676 | 2665808.5552 | 1199559.0892
50 | 2665867.8175 | 1199583.938 | 2665867.3926 | 1199582.8812
51 | 2665872.4127 | 1199598.0859 | 2665867.8175 | 1199583.938
52 | 2665504.9908 | 1199382.3543 | 2665510.2859 | 1199382.4123 | 2665519.6997 | 1199379.5258
53 | 2665427.1765 | 1199428.9412 | 2665427.1765 | 1199428.9412 | 2665447.6623 | 1199423.0619 | 2665465.2909 | 1199417.3514 | 2665467.5468 | 1199417.0155
54 | 2665669.9134 | 1199549.9631 | 2665527.0215 | 1199477.6062
55 | 2665669.9134 | 1199549.9631 | 2665669.565 | 1199552.5719 | 2665670.2208 | 1199555.9478 | 2665671.7132 | 1199558.214
56 | 2665669.9134 | 1199549.9631 | 2665675.088 | 1199546.0843 | 2665679.0348 | 1199543.6282
57 | 2665527.0215 | 1199477.6062 | 2665519.0758 | 1199484.9141 | 2665516.941 | 1199487.1763
58 | 2665527.0215 | 1199477.6062 | 2665530.2212 | 1199474.6635 | 2665544.492 | 1199458.5325 | 2665545.8263 | 1199447.9519 | 2665545.4813 | 1199442.0647
59 | 2665676.5116 | 1199565.5004 | 2665671.7132 | 1199558.214
60 | 2665679.0348 | 1199543.6282 | 2665687.6228 | 1199538.284 | 2665693.6233 | 1199535.4594 | 2665699.9097 | 1199534.3278 | 2665711.9819 | 1199533.9824 | 2665717.7123 | 1199534.8147
61 | 2665472.942 | 1199416.2122 | 2665485.0274 | 1199414.4127
62 | 2665472.942 | 1199416.2122 | 2665467.5468 | 1199417.0155
63 | 2665490.0307 | 1199413.6677 | 2665485.0274 | 1199414.4127
64 | 2665500.4917 | 1199410.3995 | 2665493.3191 | 1199413.1781 | 2665490.0307 | 1199413.6677
65 | 2665500.4917 | 1199410.3995 | 2665548.0015 | 1199436.38
66 | 2665499.1959 | 1199505.9775 | 2665485.0436 | 1199520.9669
67 | 2665516.941 | 1199487.1763 | 2665504.1847 | 1199500.6937 | 2665499.1959 | 1199505.9775
68 | 2665548.0015 | 1199436.38 | 2665545.3132 | 1199439.1967 | 2665545.4813 | 1199442.0647
69 | 2665554.8494 | 1199438.3717 | 2665553.5046 | 1199437.252 | 2665548.0015 | 1199436.38 | 2665548.0015 | 1199436.38
70 | 2665542.0479 | 1199372.6732 | 2665519.6997 | 1199379.5258
71 | 2665542.0479 | 1199372.6732 | 2665558.3491 | 1199367.6748 | 2665568.9375 | 1199367.9577 | 2665571.5522 | 1199368.6532
72 | 2665589.9986 | 1199379.0731 | 2665577.2206 | 1199370.161 | 2665571.5522 | 1199368.6532
73 | 2665623.7111 | 1199624.1556 | 2665642.2262 | 1199614.1227
74 | 2665642.2262 | 1199614.1227 | 2665655.3835 | 1199606.9931 | 2665655.8209 | 1199606.8191
75 | 2665676.5116 | 1199565.5004 | 2665680.7351 | 1199567.0922 | 2665687.743 | 1199566.8246 | 2665695.2873 | 1199563.6898
76 | 2665676.5116 | 1199565.5004 | 2665677.0951 | 1199567.8304 | 2665677.0951 | 1199567.8304
77 | 2665677.0951 | 1199567.8304 | 2665679.1102 | 1199572.6327
78 | 2665681.7168 | 1199578.8447 | 2665679.1102 | 1199572.6327
79 | 2665893.0115 | 1199639.3695 | 2665891.0962 | 1199637.5709
80 | 2665893.0115 | 1199639.3695 | 2665895.5047 | 1199641.7108 | 2665906.1873 | 1199649.2887 | 2665913.6881 | 1199655.4083 | 2665916.2437 | 1199659.1054 | 2665917.7049 | 1199663.3017 | 2665918.0816 | 1199665.9467
81 | 2665872.4127 | 1199598.0859 | 2665884.6221 | 1199628.105 | 2665887.3396 | 1199633.0046 | 2665891.0962 | 1199637.5709 | 2665891.0962 | 1199637.5709
82 | 2665923.1281 | 1199709.3557 | 2665921.6142 | 1199698.8883 | 2665920.581 | 1199693.1624 | 2665918.5105 | 1199668.9584 | 2665918.0816 | 1199665.9467
83 | 2665872.4127 | 1199598.0859 | 2665863.7309 | 1199601.0143 | 2665852.3808 | 1199602.8681 | 2665851.9132 | 1199602.9056
84 | 2665923.1281 | 1199709.3557 | 2665895.8157 | 1199706.7197 | 2665888.283 | 1199706.7529
85 | 2665842.8549 | 1199603.6303 | 2665851.9132 | 1199602.9056
86 | 2665879.7735 | 1199706.7904 | 2665888.283 | 1199706.7529
87 | 2665842.8549 | 1199603.6303 | 2665842.8549 | 1199603.6303 | 2665830.565 | 1199602.3829
88 | 2665770.2517 | 1199559.0761 | 2665766.4778 | 1199556.6618 | 2665755.2805 | 1199549.0198
89 | 2665773.9852 | 1199561.4646 | 2665770.2517 | 1199559.0761
90 | 2665743.067 | 1199542.0846 | 2665750.169 | 1199545.5313 | 2665755.2805 | 1199549.0198
91 | 2665801.1896 | 1199578.1676 | 2665798.2181 | 1199576.9675 | 2665773.9852 | 1199561.4646
92 | 2665726.3912 | 1199536.4423 | 2665730.3631 | 1199537.3754 | 2665740.5353 | 1199540.856 | 2665743.067 | 1199542.0846
93 | 2665801.1896 | 1199578.1676 | 2665797.901 | 1199586.3641
94 | 2665726.3912 | 1199536.4423 | 2665722.2522 | 1199535.474 | 2665717.7123 | 1199534.8147
95 | 2665726.3912 | 1199536.4423 | 2665726.5041 | 1199534.4868 | 2665723.4968 | 1199532.3858 | 2665717.5732 | 1199530.2176
96 | 2665795.0286 | 1199593.5231 | 2665797.901 | 1199586.3641
97 | 2665711.0899 | 1199528.4255 | 2665716.9521 | 1199529.9902 | 2665717.5732 | 1199530.2176
98 | 2665795.0286 | 1199593.5231 | 2665794.7856 | 1199594.1289 | 2665789.9363 | 1199607.1769
99 | 2665782.1466 | 1199616.7956 | 2665785.9169 | 1199614.032 | 2665789.5677 | 1199608.1687 | 2665789.9363 | 1199607.1769
100 | 2665782.1466 | 1199616.7956 | 2665778.8934 | 1199619.18 | 2665777.5033 | 1199620.1012
101 | 2665764.1684 | 1199630.5774 | 2665771.9291 | 1199623.7951 | 2665777.5033 | 1199620.1012
102 | 2665757.0941 | 1199636.9049 | 2665758.9134 | 1199635.1698 | 2665764.1684 | 1199630.5774
103 | 2665757.0941 | 1199636.9049 | 2665746.4095 | 1199647.0949 | 2665746.1173 | 1199647.3622
104 | 2665743.2594 | 1199649.9766 | 2665746.1173 | 1199647.3622
105 | 2665743.2594 | 1199649.9766 | 2665751.8179 | 1199740.977
106 | 2665743.2594 | 1199649.9766 | 2665733.788 | 1199658.6408 | 2665731.3998 | 1199659.7819 | 2665729.322 | 1199659.7146 | 2665726.6545 | 1199658.5624 | 2665722.2169 | 1199652.9102 | 2665718.6016 | 1199648.6997
107 | 2665751.8179 | 1199740.977 | 2665766.0087 | 1199790.9073 | 2665769.3014 | 1199796.3232
108 | 2665751.8179 | 1199740.977 | 2665729.389 | 1199740.8414 | 2665717.5284 | 1199742.3667
109 | 2665751.8179 | 1199740.977 | 2665764.6223 | 1199740.5391
110 | 2665705.0712 | 1199633.7535 | 2665715.3457 | 1199644.9077 | 2665718.6016 | 1199648.6997
111 | 2665705.0712 | 1199633.7535 | 2665704.9172 | 1199633.5863 | 2665704.3463 | 1199632.8702
112 | 2665690.1902 | 1199615.1132 | 2665704.3463 | 1199632.8702
113 | 2665690.1902 | 1199615.1132 | 2665687.5081 | 1199611.7487 | 2665682.4565 | 1199607.2127 | 2665676.1833 | 1199603.6862 | 2665670.7465 | 1199602.3368 | 2665665.7228 | 1199602.8819 | 2665655.8209 | 1199606.8191
114 | 2665711.2629 | 1199870.5533 | 2665721.8412 | 1199856.6321
115 | 2665721.8412 | 1199856.6321 | 2665724.4837 | 1199853.1545 | 2665732.2289 | 1199850.3213
116 | 2665696.3782 | 1199739.3001 | 2665707.5673 | 1199743.6477 | 2665717.5284 | 1199742.3667
117 | 2665681.6841 | 1199733.5907 | 2665696.3782 | 1199739.3001
118 | 2665772.6206 | 1199831.8013 | 2665777.8567 | 1199827.4817 | 2665778.8491 | 1199812.0278 | 2665769.3014 | 1199796.3232
119 | 2665745.3754 | 1199845.5124 | 2665732.2289 | 1199850.3213
120 | 2665745.3754 | 1199845.5124 | 2665752.6417 | 1199842.8544
121 | 2665703.9301 | 1199526.5143 | 2665711.0899 | 1199528.4255
122 | 2665772.6206 | 1199831.8013 | 2665764.4643 | 1199838.5298 | 2665752.6417 | 1199842.8544
123 | 2665830.565 | 1199602.3829 | 2665829.5543 | 1199602.2804
124 | 2665829.5543 | 1199602.2804 | 2665829.4616 | 1199602.2709

## bus_geodata
| x | y | coords
0 | 2665546.6809 | 1199140.719
1 | 2665531.7762 | 1199134.2669
2 | 2665555.9698 | 1199145.1942
3 | 2665525.5916 | 1199155.2449
4 | 2665556.1765 | 1199159.6717
5 | 2665813.282 | 1199410.5649
6 | 2665836.146 | 1199450.3594
7 | 2665501.0062 | 1199137.98
8 | 2665553.2454 | 1198997.1874
9 | 2665587.683 | 1199026.541
10 | 2665564.9024 | 1198999.5863
11 | 2665579.9383 | 1199138.5185
12 | 2665590.3016 | 1199134.3197
13 | 2665571.1504 | 1199157.7917
14 | 2665589.4449 | 1199157.5686
15 | 2665590.4535 | 1199169.4571
16 | 2665594.6397 | 1199198.5852
17 | 2665600.3449 | 1199224.528
18 | 2665575.4632 | 1199245.9908
19 | 2665612.1817 | 1199244.5023
20 | 2665557.1941 | 1199261.7495
21 | 2665645.8825 | 1199275.9436
22 | 2665513.7365 | 1199297.5541
23 | 2665663.1916 | 1199289.8314
24 | 2665499.7628 | 1199306.0072
25 | 2665758.6067 | 1199472.2318
26 | 2665751.3708 | 1199497.0163
27 | 2665772.241 | 1199465.4042
28 | 2665484.9329 | 1199371.0501
29 | 2665693.668 | 1199523.7751
30 | 2665696.8579 | 1199524.6266
31 | 2665490.3156 | 1199375.8304
32 | 2665416.4808 | 1199422.4758
33 | 2665842.0482 | 1199482.0254
34 | 2666143.1801 | 1199280.4893
35 | 2665849.2427 | 1199522.8192
36 | 2666132.7428 | 1199255.5411
37 | 2665857.5534 | 1199558.4097
38 | 2665814.4404 | 1199544.7713
39 | 2665781.8535 | 1199471.0047
40 | 2665788.907 | 1199483.6894
41 | 2665792.8845 | 1199535.1284
42 | 2665792.9166 | 1199530.2188
43 | 2665781.1276 | 1199530.227
44 | 2665763.6643 | 1199518.3655
45 | 2665748.1994 | 1199484.4177
46 | 2665809.662 | 1199556.2222
47 | 2665808.5552 | 1199559.0892
48 | 2665867.3926 | 1199582.8812
49 | 2665867.8175 | 1199583.938
50 | 2665504.9908 | 1199382.3543
51 | 2665427.1765 | 1199428.9412
52 | 2665669.9134 | 1199549.9631
53 | 2665527.0215 | 1199477.6062
54 | 2665671.7132 | 1199558.214
55 | 2665679.0348 | 1199543.6282
56 | 2665472.942 | 1199416.2122
57 | 2665485.0274 | 1199414.4127
58 | 2665467.5468 | 1199417.0155
59 | 2665490.0307 | 1199413.6677
60 | 2665500.4917 | 1199410.3995
61 | 2665499.1959 | 1199505.9775
62 | 2665485.0436 | 1199520.9669
63 | 2665516.941 | 1199487.1763
64 | 2665548.0015 | 1199436.38
65 | 2665554.8494 | 1199438.3717
66 | 2665545.4813 | 1199442.0647
67 | 2665519.6997 | 1199379.5258
68 | 2665542.0479 | 1199372.6732
69 | 2665571.5522 | 1199368.6532
70 | 2665589.9986 | 1199379.0731
71 | 2665623.7111 | 1199624.1556
72 | 2665642.2262 | 1199614.1227
73 | 2665695.2873 | 1199563.6898
74 | 2665676.5116 | 1199565.5004
75 | 2665677.0951 | 1199567.8304
76 | 2665679.1102 | 1199572.6327
77 | 2665681.7168 | 1199578.8447
78 | 2665893.0115 | 1199639.3695
79 | 2665891.0962 | 1199637.5709
80 | 2665918.0816 | 1199665.9467
81 | 2665872.4127 | 1199598.0859
82 | 2665923.1281 | 1199709.3557
83 | 2665851.9132 | 1199602.9056
84 | 2665888.283 | 1199706.7529
85 | 2665842.8549 | 1199603.6303
86 | 2665879.7735 | 1199706.7904
87 | 2665770.2517 | 1199559.0761
88 | 2665755.2805 | 1199549.0198
89 | 2665773.9852 | 1199561.4646
90 | 2665743.067 | 1199542.0846
91 | 2665801.1896 | 1199578.1676
92 | 2665726.3912 | 1199536.4423
93 | 2665797.901 | 1199586.3641
94 | 2665717.7123 | 1199534.8147
95 | 2665717.5732 | 1199530.2176
96 | 2665795.0286 | 1199593.5231
97 | 2665789.9363 | 1199607.1769
98 | 2665782.1466 | 1199616.7956
99 | 2665777.5033 | 1199620.1012
100 | 2665764.1684 | 1199630.5774
101 | 2665757.0941 | 1199636.9049
102 | 2665746.1173 | 1199647.3622
103 | 2665743.2594 | 1199649.9766
104 | 2665751.8179 | 1199740.977
105 | 2665718.6016 | 1199648.6997
106 | 2665705.0712 | 1199633.7535
107 | 2665704.3463 | 1199632.8702
108 | 2665690.1902 | 1199615.1132
109 | 2665711.2629 | 1199870.5533
110 | 2665721.8412 | 1199856.6321
111 | 2665717.5284 | 1199742.3667
112 | 2665696.3782 | 1199739.3001
113 | 2665681.6841 | 1199733.5907
114 | 2665655.8209 | 1199606.8191
115 | 2665764.6223 | 1199740.5391
116 | 2665769.3014 | 1199796.3232
117 | 2665732.2289 | 1199850.3213
118 | 2665745.3754 | 1199845.5124
119 | 2665711.0899 | 1199528.4255
120 | 2665703.9301 | 1199526.5143
121 | 2665752.6417 | 1199842.8544
122 | 2665772.6206 | 1199831.8013
123 | 2665830.565 | 1199602.3829
124 | 2665829.5543 | 1199602.2804
125 | 2665829.4616 | 1199602.2709
126 | 2665726.3912 | 1199536.4423

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.971 | -0.2047 | 0.0006932 | 0.00017373
1 | 0.97095 | -0.20509 | 0 | 0
2 | 0.97105 | -0.20438 | 0 | 0
3 | 0.97087 | -0.20562 | 0 | 0
4 | 0.97111 | -0.20393 | 0 | 0
5 | 0.97994 | -0.14084 | 0.0029786 | 0.00074651
6 | 0.98015 | -0.13934 | 0.0017237 | 0.000432
7 | 0.97078 | -0.20633 | 0.0022326 | 0.00055953
8 | 0.97033 | -0.20953 | 0 | 0
9 | 0.9704 | -0.20906 | 0.0035915 | 0.00090012
10 | 0.97032 | -0.20964 | 0.00085482 | 0.00021424
11 | 0.9711 | -0.20402 | 0.00040151 | 0.00010063
12 | 0.9711 | -0.20397 | 0 | 0
13 | 0.97117 | -0.20346 | 0.00060521 | 0.00015168
14 | 0.97127 | -0.20277 | 0 | 0
15 | 0.97141 | -0.20171 | 0.00085988 | 0.00021551
16 | 0.97181 | -0.19882 | 0.0011378 | 0.00028516
17 | 0.97222 | -0.1959 | 0 | 0
18 | 0.97296 | -0.19054 | 0.0016293 | 0.00040835
19 | 0.97205 | -0.19713 | 0.00053285 | 0.00013354
20 | 0.97356 | -0.1862 | 0.0015674 | 0.00039282
21 | 0.97174 | -0.19932 | 0.00056844 | 0.00014246
22 | 0.9751 | -0.17514 | 0.0016852 | 0.00042236
23 | 0.97162 | -0.20024 | 0.0039227 | 0.00098313
24 | 0.97559 | -0.17166 | 0 | 0
25 | 0.97915 | -0.14644 | 0.0029234 | 0.00073268
26 | 0.97965 | -0.14286 | 0.0038515 | 0.00096527
27 | 0.97895 | -0.14785 | 0.0020998 | 0.00052626
28 | 0.97769 | -0.15662 | 0 | 0
29 | 1 | 0 | -0.16865 | -0.042421
30 | 0.9996 | -0.0027233 | 0.0014953 | 0.00037476
31 | 0.97761 | -0.15722 | 0.00060873 | 0.00015256
32 | 0.98131 | -0.13086 | 0 | 0
33 | 0.98051 | -0.13679 | 0.001953 | 0.00048946
34 | 0.97867 | -0.14999 | 0.0021408 | 0.00053654
35 | 0.98108 | -0.13266 | 0 | 0
36 | 0.97864 | -0.15021 | 0.00075764 | 0.00018988
37 | 0.98063 | -0.13588 | 0.0011226 | 0.00028136
38 | 0.98217 | -0.12487 | 0 | 0
39 | 0.97884 | -0.14863 | 0.0024155 | 0.00060537
40 | 0.97875 | -0.14926 | 0.0041351 | 0.0010364
41 | 0.98121 | -0.13169 | 0 | 0
42 | 0.9812 | -0.13181 | 0.002286 | 0.00057293
43 | 0.98111 | -0.1324 | 0.0027821 | 0.00069726
44 | 0.9802 | -0.13891 | 0.0048619 | 0.0012185
45 | 0.98089 | -0.134 | 0.0025921 | 0.00064965
46 | 0.983 | -0.11894 | 0.0014233 | 0.00035671
47 | 0.98322 | -0.11743 | 0.0025308 | 0.00063429
48 | 0.98035 | -0.1379 | 0.0014162 | 0.00035494
49 | 0.98034 | -0.13797 | 0 | 0
50 | 0.97743 | -0.15851 | 0.0015428 | 0.00038665
51 | 0.98164 | -0.12846 | 0.0036299 | 0.00090974
52 | 0.99291 | -0.04918 | 0 | 0
53 | 0.98678 | -0.092119 | 0.0011481 | 0.00028775
54 | 0.99279 | -0.049977 | 0.0015141 | 0.00037947
55 | 0.9934 | -0.045715 | 0.0016853 | 0.00042238
56 | 0.98276 | -0.12054 | 0.0018086 | 0.00045329
57 | 0.98308 | -0.11831 | 0.0018824 | 0.00047177
58 | 0.98263 | -0.12149 | 0.001552 | 0.00038896
59 | 0.98321 | -0.11733 | 0.001238 | 0.00031027
60 | 0.98352 | -0.11514 | 0.001553 | 0.00038923
61 | 0.9866 | -0.093396 | 0.0014009 | 0.00035111
62 | 0.98657 | -0.093632 | 0.0011145 | 0.00027932
63 | 0.9867 | -0.092728 | 0.0017528 | 0.0004393
64 | 0.9851 | -0.10397 | 0.0021619 | 0.00054182
65 | 0.98507 | -0.10417 | 0.0027659 | 0.00069321
66 | 0.98533 | -0.1024 | 0.0021847 | 0.00054753
67 | 0.9773 | -0.15944 | 0.0011632 | 0.00029151
68 | 0.97714 | -0.16059 | 0.0016955 | 0.00042494
69 | 0.977 | -0.16155 | 0.0009185 | 0.0002302
70 | 0.97694 | -0.16202 | 0.0020917 | 0.00052424
71 | 0.97949 | -0.14395 | 0.00053581 | 0.00013429
72 | 0.97951 | -0.14383 | 0.00055002 | 0.00013785
73 | 0.99263 | -0.051115 | 0.0024001 | 0.00060152
74 | 0.9927 | -0.050636 | 0 | 0
75 | 0.99268 | -0.050758 | 0.0020556 | 0.00051519
76 | 0.99266 | -0.050916 | 0.0014402 | 0.00036095
77 | 0.99265 | -0.051022 | 0.0015511 | 0.00038873
78 | 0.97999 | -0.14045 | 0.00047981 | 0.00012025
79 | 0.98 | -0.14038 | 0.00067519 | 0.00016922
80 | 0.97988 | -0.14128 | 0.00093284 | 0.00023379
81 | 0.98021 | -0.13889 | 0 | 0
82 | 0.9798 | -0.14181 | 0 | 0
83 | 0.98013 | -0.13947 | 0.00038703 | 9.6999e-05
84 | 0.97975 | -0.14223 | 0.00062142 | 0.00015574
85 | 0.9801 | -0.13969 | 0.00026298 | 6.5909e-05
86 | 0.97974 | -0.14228 | 0.00054352 | 0.00013622
87 | 0.98919 | -0.07517 | 0.001397 | 0.00035012
88 | 0.99151 | -0.05895 | 0.0013055 | 0.00032719
89 | 0.98863 | -0.079104 | 0.0022284 | 0.0005585
90 | 0.99334 | -0.046152 | 0.0029441 | 0.00073787
91 | 0.9847 | -0.10688 | 0 | 0
92 | 0.99571 | -0.02966 | 0 | 0
93 | 0.98425 | -0.11004 | 0.0013598 | 0.0003408
94 | 0.99529 | -0.032613 | 0.0030392 | 0.0007617
95 | 0.99709 | -0.020123 | 0.0011413 | 0.00028603
96 | 0.98388 | -0.11269 | 0.0015021 | 0.00037646
97 | 0.98321 | -0.11748 | 0.00034647 | 8.6833e-05
98 | 0.98263 | -0.1216 | 0.0011151 | 0.00027947
99 | 0.98238 | -0.12339 | 0.00086259 | 0.00021618
100 | 0.98165 | -0.12858 | 0.0008714 | 0.00021839
101 | 0.98125 | -0.1314 | 0.0014773 | 0.00037024
102 | 0.98065 | -0.13567 | 0.00095926 | 0.00024041
103 | 0.9805 | -0.13673 | 0.0017808 | 0.00044632
104 | 0.97834 | -0.15222 | 0 | 0
105 | 0.98011 | -0.13953 | 0.001034 | 0.00025915
106 | 0.9799 | -0.14102 | 0.00073095 | 0.00018319
107 | 0.97989 | -0.1411 | 0.0019711 | 0.00049399
108 | 0.97975 | -0.14213 | 0.00069873 | 0.00017512
109 | 0.97739 | -0.15899 | 0.0010975 | 0.00027505
110 | 0.97742 | -0.15879 | 0.00066851 | 0.00016754
111 | 0.978 | -0.15465 | 0.0012897 | 0.00032322
112 | 0.97782 | -0.15591 | 0.0021596 | 0.00054125
113 | 0.97775 | -0.15646 | 0.0033111 | 0.00082984
114 | 0.97954 | -0.14366 | 0.0026026 | 0.00065227
115 | 0.97825 | -0.15281 | 0.0043827 | 0.0010984
116 | 0.9779 | -0.15535 | 0.0010728 | 0.00026886
117 | 0.97745 | -0.15856 | 0.00058845 | 0.00014748
118 | 0.9775 | -0.15821 | 0.00067085 | 0.00016813
119 | 0.99787 | -0.014719 | 0.001701 | 0.0004263
120 | 0.99874 | -0.0087137 | 0.001898 | 0.00047568
121 | 0.97754 | -0.15797 | 0.00067391 | 0.0001689
122 | 0.97766 | -0.15707 | 0.00035239 | 8.8317e-05
123 | 0.98006 | -0.13995 | 0.00095871 | 0.00024028
124 | 0.98006 | -0.13996 | 0.00066842 | 0.00016752
125 | 0.98006 | -0.13996 | 0.00039556 | 9.9136e-05
126 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0022331 | 0.00055887 | -0.0022329 | -0.00055903 | 1.1962e-07 | -1.565e-07 | 0.0034218 | 0.0034218 | 0.0034218 | 0.971 | -0.2047 | 0.97095 | -0.20509 | 1.2674
1 | -0.0029263 | -0.00073261 | 0.0029264 | 0.00073253 | 1.3025e-07 | -7.8323e-08 | 0.0044841 | 0.004484 | 0.0044841 | 0.971 | -0.2047 | 0.97105 | -0.20438 | 1.6608
2 | 0.0022329 | 0.00055903 | -0.0022328 | -0.00055924 | 1.6314e-07 | -2.1338e-07 | 0.0034218 | 0.0034219 | 0.0034219 | 0.97095 | -0.20509 | 0.97087 | -0.20562 | 1.2674
3 | -0.0029264 | -0.00073253 | 0.0029266 | 0.00073242 | 1.817e-07 | -1.0928e-07 | 0.004484 | 0.004484 | 0.004484 | 0.97105 | -0.20438 | 0.97111 | -0.20393 | 1.6608
4 | 0.0022328 | 0.00055924 | -0.0022326 | -0.00055953 | 2.2005e-07 | -2.8772e-07 | 0.0034219 | 0.0034221 | 0.0034221 | 0.97087 | -0.20562 | 0.97078 | -0.20633 | 1.2674
5 | -0.0029266 | -0.00073242 | 0.0029268 | 0.0007323 | 1.8934e-07 | -1.139e-07 | 0.004484 | 0.0044839 | 0.004484 | 0.97111 | -0.20393 | 0.97117 | -0.20346 | 1.6607
6 | -0.0029786 | -0.00074651 | 0.0029792 | 0.00074614 | 6.167e-07 | -3.7161e-07 | 0.0045229 | 0.0045227 | 0.0045229 | 0.97994 | -0.14084 | 0.98015 | -0.13934 | 1.6752
7 | -0.0076057 | -0.0019014 | 0.0076083 | 0.0019021 | 2.679e-06 | 6.2424e-07 | 0.011545 | 0.011545 | 0.011545 | 0.98015 | -0.13934 | 0.98051 | -0.13679 | 4.2759
8 | 0.0029027 | 0.00072331 | -0.0028985 | -0.00072609 | 4.2507e-06 | -2.7809e-06 | 0.0044053 | 0.0044069 | 0.0044069 | 0.98015 | -0.13934 | 0.97867 | -0.14999 | 1.6322
9 | -0.00085483 | -0.0002141 | 0.00085488 | 0.00021348 | 5.5538e-08 | -6.1862e-07 | 0.0013108 | 0.0013106 | 0.0013108 | 0.97033 | -0.20953 | 0.9704 | -0.20906 | 0.4855
10 | 0.00085483 | 0.0002141 | -0.00085482 | -0.00021424 | 1.2761e-08 | -1.421e-07 | 0.0013108 | 0.0013109 | 0.0013109 | 0.97033 | -0.20953 | 0.97032 | -0.20964 | 0.48552
11 | -0.0044464 | -0.0011136 | 0.0044495 | 0.0011135 | 3.1269e-06 | -1.302e-07 | 0.0068179 | 0.0068174 | 0.0068179 | 0.9704 | -0.20906 | 0.9711 | -0.20397 | 2.5251
12 | -0.00040151 | -0.00010063 | 0.00040151 | 0.00010049 | 2.6539e-09 | -1.38e-07 | 0.00061523 | 0.00061518 | 0.00061523 | 0.9711 | -0.20402 | 0.9711 | -0.20397 | 0.22786
13 | -0.0048511 | -0.001214 | 0.0048519 | 0.001214 | 8.0443e-07 | 2.0633e-08 | 0.0074326 | 0.0074325 | 0.0074326 | 0.9711 | -0.20397 | 0.97127 | -0.20277 | 2.7528
14 | -0.003532 | -0.00088398 | 0.0035323 | 0.00088389 | 3.3524e-07 | -9.8119e-08 | 0.0054112 | 0.0054111 | 0.0054112 | 0.97117 | -0.20346 | 0.97127 | -0.20277 | 2.0041
15 | -0.0083842 | -0.0020979 | 0.0083854 | 0.0020982 | 1.2281e-06 | 3.2467e-07 | 0.012844 | 0.012844 | 0.012844 | 0.97127 | -0.20277 | 0.97141 | -0.20171 | 4.7569
16 | -0.0092453 | -0.0023137 | 0.009249 | 0.0023147 | 3.6893e-06 | 1.0538e-06 | 0.014161 | 0.014161 | 0.014161 | 0.97141 | -0.20171 | 0.97181 | -0.19882 | 5.2447
17 | -0.010387 | -0.0025999 | 0.010391 | 0.0026012 | 4.192e-06 | 1.283e-06 | 0.015903 | 0.015903 | 0.015903 | 0.97181 | -0.19882 | 0.97222 | -0.1959 | 5.8899
18 | -0.015418 | -0.0038602 | 0.015429 | 0.0038642 | 1.1416e-05 | 3.983e-06 | 0.023596 | 0.023596 | 0.023596 | 0.97222 | -0.1959 | 0.97296 | -0.19054 | 8.7392
19 | 0.0050267 | 0.001259 | -0.0050259 | -0.001259 | 8.5864e-07 | 4.2006e-08 | 0.0076933 | 0.0076934 | 0.0076934 | 0.97222 | -0.1959 | 0.97205 | -0.19713 | 2.8494
20 | -0.017058 | -0.0042726 | 0.017069 | 0.0042762 | 1.0246e-05 | 3.6409e-06 | 0.026088 | 0.026088 | 0.026088 | 0.97296 | -0.19054 | 0.97356 | -0.1862 | 9.6621
21 | 0.004493 | 0.0011255 | -0.0044917 | -0.0011255 | 1.3618e-06 | -4.7939e-08 | 0.0068777 | 0.0068779 | 0.0068779 | 0.97205 | -0.19713 | 0.97174 | -0.19932 | 2.5474
22 | -0.018636 | -0.004669 | 0.018665 | 0.0046793 | 2.8555e-05 | 1.028e-05 | 0.028483 | 0.028483 | 0.028483 | 0.97356 | -0.1862 | 0.9751 | -0.17514 | 10.5493
23 | 0.0039232 | 0.00098305 | -0.0039227 | -0.00098313 | 5.0005e-07 | -8.2709e-08 | 0.0060075 | 0.0060076 | 0.0060076 | 0.97174 | -0.19932 | 0.97162 | -0.20024 | 2.225
24 | -0.02035 | -0.0051017 | 0.02036 | 0.0051053 | 9.8279e-06 | 3.5761e-06 | 0.031055 | 0.031055 | 0.031055 | 0.9751 | -0.17514 | 0.97559 | -0.17166 | 11.5017
25 | -0.02036 | -0.0051053 | 0.020402 | 0.0051207 | 4.2507e-05 | 1.5465e-05 | 0.031055 | 0.031054 | 0.031055 | 0.97559 | -0.17166 | 0.97769 | -0.15662 | 11.5017
26 | -0.011577 | -0.0029012 | 0.011582 | 0.0029031 | 5.7438e-06 | 1.8349e-06 | 0.017593 | 0.017593 | 0.017593 | 0.97915 | -0.14644 | 0.97965 | -0.14286 | 6.5159
27 | 0.0086532 | 0.0021685 | -0.0086515 | -0.0021681 | 1.6913e-06 | 4.534e-07 | 0.01315 | 0.01315 | 0.01315 | 0.97915 | -0.14644 | 0.97895 | -0.14785 | 4.8705
28 | -0.015434 | -0.0038683 | 0.015442 | 0.0038713 | 8.4496e-06 | 2.9394e-06 | 0.023443 | 0.023443 | 0.023443 | 0.97965 | -0.14286 | 0.9802 | -0.13891 | 8.6826
29 | 0.0065517 | 0.0016418 | -0.006551 | -0.0016417 | 7.0027e-07 | 1.2708e-07 | 0.0099586 | 0.0099586 | 0.0099586 | 0.97895 | -0.14785 | 0.97884 | -0.14863 | 3.6884
30 | 0.0080244 | 0.0020102 | -0.0080238 | -0.0020101 | 6.7e-07 | 1.6742e-07 | 0.012213 | 0.012213 | 0.012213 | 0.97769 | -0.15662 | 0.97761 | -0.15722 | 4.5232
31 | -0.028427 | -0.0071309 | 0.028529 | 0.007169 | 0.00010191 | 3.8097e-05 | 0.043267 | 0.043266 | 0.043267 | 0.97769 | -0.15662 | 0.98131 | -0.13086 | 16.0248
32 | 0.16785 | 0.042421 | -0.16779 | -0.042396 | 6.4327e-05 | 2.4655e-05 | 0.24989 | 0.24989 | 0.24989 | 1 | 0 | 0.9996 | -0.0027233 | 46.2768
33 | 0.1663 | 0.042021 | -0.16616 | -0.041967 | 0.00014009 | 5.3688e-05 | 0.24767 | 0.24767 | 0.24767 | 0.9996 | -0.0027233 | 0.99874 | -0.0087137 | 45.8646
34 | 0.007415 | 0.0018575 | -0.0074137 | -0.0018572 | 1.3215e-06 | 2.9984e-07 | 0.011286 | 0.011286 | 0.011286 | 0.97761 | -0.15722 | 0.97743 | -0.15851 | 4.1801
35 | -0.028529 | -0.007169 | 0.028538 | 0.0071723 | 9.5305e-06 | 3.2531e-06 | 0.043266 | 0.043266 | 0.043266 | 0.98131 | -0.13086 | 0.98164 | -0.12846 | 8.0123
36 | -0.0095613 | -0.0023915 | 0.0095668 | 0.0023931 | 5.4411e-06 | 1.57e-06 | 0.014509 | 0.014508 | 0.014509 | 0.98051 | -0.13679 | 0.98108 | -0.13266 | 5.3735
37 | 0.00075767 | 0.00018955 | -0.00075764 | -0.00018988 | 2.2586e-08 | -3.3406e-07 | 0.0011519 | 0.001152 | 0.001152 | 0.97867 | -0.14999 | 0.97864 | -0.15021 | 0.42666
38 | 0.0084724 | 0.0021208 | -0.0084687 | -0.0021198 | 3.7654e-06 | 9.8693e-07 | 0.012849 | 0.012849 | 0.012849 | 0.98108 | -0.13266 | 0.98063 | -0.13588 | 4.759
39 | -0.018039 | -0.0045139 | 0.018059 | 0.0045208 | 1.9425e-05 | 6.9455e-06 | 0.027358 | 0.027357 | 0.027358 | 0.98108 | -0.13266 | 0.98217 | -0.12487 | 10.1325
40 | 0.007346 | 0.0018384 | -0.007344 | -0.001838 | 2.0447e-06 | 4.5375e-07 | 0.011146 | 0.011146 | 0.011146 | 0.98063 | -0.13588 | 0.98035 | -0.1379 | 4.1282
41 | -0.046071 | -0.011547 | 0.046109 | 0.011562 | 3.7861e-05 | 1.4404e-05 | 0.069799 | 0.069799 | 0.069799 | 0.98217 | -0.12487 | 0.983 | -0.11894 | 25.8515
42 | 0.028012 | 0.0070263 | -0.027986 | -0.0070165 | 2.6479e-05 | 9.8865e-06 | 0.042442 | 0.042442 | 0.042442 | 0.98217 | -0.12487 | 0.98121 | -0.13169 | 15.7191
43 | 0.0041355 | 0.0010363 | -0.0041351 | -0.0010364 | 3.6487e-07 | -4.5619e-08 | 0.0062867 | 0.0062867 | 0.0062867 | 0.97884 | -0.14863 | 0.97875 | -0.14926 | 2.3284
44 | 0.0022861 | 0.00057288 | -0.002286 | -0.00057293 | 3.87e-08 | -5.0293e-08 | 0.0034668 | 0.0034668 | 0.0034668 | 0.98121 | -0.13169 | 0.9812 | -0.13181 | 1.284
45 | 0.0053753 | 0.0013464 | -0.0053748 | -0.0013464 | 5.2816e-07 | 4.2259e-08 | 0.0081515 | 0.0081515 | 0.0081515 | 0.98121 | -0.13169 | 0.98111 | -0.1324 | 3.0191
46 | 0.020324 | 0.0050972 | -0.020304 | -0.0050898 | 2.0317e-05 | 7.3818e-06 | 0.030823 | 0.030824 | 0.030824 | 0.98121 | -0.13169 | 0.9802 | -0.13891 | 11.4161
47 | 0.0025927 | 0.00064912 | -0.0025921 | -0.00064965 | 5.7329e-07 | -5.2971e-07 | 0.003932 | 0.0039323 | 0.0039323 | 0.98111 | -0.1324 | 0.98089 | -0.134 | 1.4564
48 | -0.047532 | -0.011918 | 0.047542 | 0.011922 | 9.9285e-06 | 3.7797e-06 | 0.071953 | 0.071953 | 0.071953 | 0.983 | -0.11894 | 0.98322 | -0.11743 | 26.6494
49 | -0.050073 | -0.012556 | 0.050146 | 0.012584 | 7.329e-05 | 2.7929e-05 | 0.075784 | 0.075784 | 0.075784 | 0.98322 | -0.11743 | 0.9847 | -0.10688 | 28.068
50 | 0.0059277 | 0.001483 | -0.0059277 | -0.001483 | 5.7526e-08 | 7.7637e-09 | 0.0089965 | 0.0089965 | 0.0089965 | 0.98035 | -0.1379 | 0.98034 | -0.13797 | 3.332
51 | 0.0059277 | 0.001483 | -0.0059269 | -0.0014829 | 7.5121e-07 | 1.0141e-07 | 0.0089965 | 0.0089965 | 0.0089965 | 0.98034 | -0.13797 | 0.98021 | -0.13889 | 3.332
52 | 0.005871 | 0.0014705 | -0.0058702 | -0.0014704 | 7.5475e-07 | 1.0053e-07 | 0.0089375 | 0.0089376 | 0.0089376 | 0.97743 | -0.15851 | 0.9773 | -0.15944 | 3.3102
53 | -0.032168 | -0.008082 | 0.032199 | 0.008093 | 3.1258e-05 | 1.0956e-05 | 0.048769 | 0.048768 | 0.048769 | 0.98164 | -0.12846 | 0.98263 | -0.12149 | 9.0312
54 | 0.053254 | 0.013427 | -0.052936 | -0.013309 | 0.00031853 | 0.0001184 | 0.079838 | 0.07984 | 0.07984 | 0.99291 | -0.04918 | 0.98678 | -0.092119 | 14.7851
55 | 0.0089631 | 0.002246 | -0.0089621 | -0.0022457 | 9.8902e-07 | 2.6679e-07 | 0.013432 | 0.013432 | 0.013432 | 0.99291 | -0.04918 | 0.99279 | -0.049977 | 4.975
56 | -0.062218 | -0.015673 | 0.062248 | 0.015685 | 3.017e-05 | 1.1316e-05 | 0.09327 | 0.09327 | 0.09327 | 0.99291 | -0.04918 | 0.9934 | -0.045715 | 17.2723
57 | 0.0042689 | 0.0010692 | -0.0042686 | -0.0010692 | 3.5955e-07 | -3.9339e-08 | 0.0064371 | 0.0064371 | 0.0064371 | 0.98678 | -0.092119 | 0.9867 | -0.092728 | 2.3841
58 | 0.047519 | 0.011952 | -0.047451 | -0.011927 | 6.8028e-05 | 2.5082e-05 | 0.071671 | 0.071671 | 0.071671 | 0.98678 | -0.092119 | 0.98533 | -0.1024 | 13.2725
59 | 0.007448 | 0.0018662 | -0.0074473 | -0.0018661 | 6.7841e-07 | 1.4812e-07 | 0.011163 | 0.011163 | 0.011163 | 0.99279 | -0.049977 | 0.9927 | -0.050636 | 4.1345
60 | -0.063933 | -0.016107 | 0.06405 | 0.016151 | 0.00011739 | 4.4088e-05 | 0.095795 | 0.095794 | 0.095795 | 0.9934 | -0.045715 | 0.99529 | -0.032613 | 17.7398
61 | -0.035564 | -0.0089368 | 0.035575 | 0.0089407 | 1.1058e-05 | 3.9432e-06 | 0.053857 | 0.053857 | 0.053857 | 0.98276 | -0.12054 | 0.98308 | -0.11831 | 9.9735
62 | 0.033756 | 0.0084835 | -0.033751 | -0.0084819 | 4.4471e-06 | 1.5722e-06 | 0.051118 | 0.051118 | 0.051118 | 0.98276 | -0.12054 | 0.98263 | -0.12149 | 9.4664
63 | -0.037458 | -0.0094125 | 0.037463 | 0.0094143 | 5.0749e-06 | 1.8236e-06 | 0.056706 | 0.056706 | 0.056706 | 0.98308 | -0.11831 | 0.98321 | -0.11733 | 10.5011
64 | -0.038701 | -0.0097246 | 0.038713 | 0.0097289 | 1.1795e-05 | 4.257e-06 | 0.05858 | 0.058579 | 0.05858 | 0.98321 | -0.11733 | 0.98352 | -0.11514 | 10.8481
65 | -0.040266 | -0.010118 | 0.040328 | 0.010141 | 6.2718e-05 | 2.2746e-05 | 0.060929 | 0.060929 | 0.060929 | 0.98352 | -0.11514 | 0.9851 | -0.10397 | 11.2832
66 | 0.0011146 | 0.00027908 | -0.0011145 | -0.00027932 | 3.6347e-08 | -2.4926e-07 | 0.0016809 | 0.001681 | 0.001681 | 0.9866 | -0.093396 | 0.98657 | -0.093632 | 0.62259
67 | -0.0025155 | -0.00063018 | 0.0025157 | 0.00062994 | 2.3219e-07 | -2.4087e-07 | 0.0037938 | 0.0037937 | 0.0037938 | 0.9866 | -0.093396 | 0.9867 | -0.092728 | 1.4051
68 | -0.045256 | -0.011376 | 0.045266 | 0.011379 | 9.8692e-06 | 3.6235e-06 | 0.068372 | 0.068372 | 0.068372 | 0.9851 | -0.10397 | 0.98533 | -0.1024 | 12.6615
69 | 0.002766 | 0.00069315 | -0.0027659 | -0.00069321 | 7.9755e-08 | -6.2538e-08 | 0.0041781 | 0.0041781 | 0.0041781 | 0.9851 | -0.10397 | 0.98507 | -0.10417 | 1.5475
70 | 0.0047071 | 0.0011789 | -0.0047063 | -0.0011789 | 7.4916e-07 | -4.7143e-09 | 0.0071666 | 0.0071667 | 0.0071667 | 0.9773 | -0.15944 | 0.97714 | -0.16059 | 2.6543
71 | 0.0030108 | 0.00075399 | -0.0030104 | -0.00075422 | 3.9806e-07 | -2.27e-07 | 0.0045847 | 0.0045848 | 0.0045848 | 0.97714 | -0.16059 | 0.977 | -0.16155 | 1.6981
72 | 0.0020919 | 0.00052402 | -0.0020917 | -0.00052424 | 1.3582e-07 | -2.1629e-07 | 0.0031859 | 0.003186 | 0.003186 | 0.977 | -0.16155 | 0.97694 | -0.16202 | 1.18
73 | -0.00053581 | -0.00013429 | 0.00053582 | 0.00013402 | 8.7055e-09 | -2.6172e-07 | 0.00081398 | 0.00081389 | 0.00081398 | 0.97949 | -0.14395 | 0.97951 | -0.14383 | 0.30148
74 | -0.0010858 | -0.00027187 | 0.0010859 | 0.00027169 | 2.6204e-08 | -1.8422e-07 | 0.0016494 | 0.0016494 | 0.0016494 | 0.97951 | -0.14383 | 0.97954 | -0.14366 | 0.61091
75 | -0.0024001 | -0.00060152 | 0.0024003 | 0.00060133 | 1.5909e-07 | -1.9343e-07 | 0.0035979 | 0.0035978 | 0.0035979 | 0.99263 | -0.051115 | 0.9927 | -0.050636 | 1.3326
76 | 0.0050471 | 0.0012648 | -0.005047 | -0.0012648 | 8.5784e-08 | 1.9405e-09 | 0.0075653 | 0.0075653 | 0.0075653 | 0.9927 | -0.050636 | 0.99268 | -0.050758 | 2.802
77 | 0.0029914 | 0.00074956 | -0.0029913 | -0.00074961 | 6.534e-08 | -4.2197e-08 | 0.0044839 | 0.004484 | 0.004484 | 0.99268 | -0.050758 | 0.99266 | -0.050916 | 1.6607
78 | 0.0015511 | 0.00038865 | -0.0015511 | -0.00038873 | 2.2725e-08 | -7.8346e-08 | 0.0023251 | 0.0023251 | 0.0023251 | 0.99266 | -0.050916 | 0.99265 | -0.051022 | 0.86115
79 | -0.002578 | -0.00064458 | 0.002578 | 0.00064456 | 2.5114e-08 | -2.3445e-08 | 0.0039139 | 0.0039138 | 0.0039139 | 0.97999 | -0.14045 | 0.98 | -0.14038 | 1.4496
80 | 0.0020982 | 0.00052433 | -0.0020979 | -0.00052472 | 2.3938e-07 | -3.8424e-07 | 0.0031853 | 0.0031855 | 0.0031855 | 0.97999 | -0.14045 | 0.97988 | -0.14128 | 1.1798
81 | -0.0032532 | -0.00081378 | 0.0032539 | 0.00081348 | 6.6856e-07 | -2.964e-07 | 0.004939 | 0.0049388 | 0.004939 | 0.98 | -0.14038 | 0.98021 | -0.13889 | 1.8293
82 | 0.0011651 | 0.00029092 | -0.001165 | -0.00029144 | 8.5391e-08 | -5.1796e-07 | 0.0017689 | 0.0017691 | 0.0017691 | 0.97988 | -0.14128 | 0.9798 | -0.14181 | 0.65522
83 | 0.0026731 | 0.00066943 | -0.0026728 | -0.00066961 | 2.1712e-07 | -1.8285e-07 | 0.0040577 | 0.0040578 | 0.0040578 | 0.98021 | -0.13889 | 0.98013 | -0.13947 | 1.5029
84 | 0.001165 | 0.00029144 | -0.0011649 | -0.00029186 | 6.8304e-08 | -4.1417e-07 | 0.0017691 | 0.0017693 | 0.0017693 | 0.9798 | -0.14181 | 0.97975 | -0.14223 | 0.65528
85 | 0.0022858 | 0.00057261 | -0.0022857 | -0.0005727 | 6.8286e-08 | -8.826e-08 | 0.0034702 | 0.0034702 | 0.0034702 | 0.98013 | -0.13947 | 0.9801 | -0.13969 | 1.2853
86 | 0.00054353 | 0.00013611 | -0.00054352 | -0.00013622 | 3.6183e-09 | -1.0577e-07 | 0.00082546 | 0.0008255 | 0.0008255 | 0.97975 | -0.14223 | 0.97974 | -0.14228 | 0.30574
87 | 0.0020228 | 0.00050679 | -0.0020227 | -0.00050692 | 7.2697e-08 | -1.2771e-07 | 0.003071 | 0.003071 | 0.003071 | 0.9801 | -0.13969 | 0.98006 | -0.13995 | 1.1374
88 | -0.08899 | -0.022385 | 0.089192 | 0.022463 | 0.00020177 | 7.7373e-05 | 0.13389 | 0.13389 | 0.13389 | 0.98919 | -0.07517 | 0.99151 | -0.05895 | 49.5905
89 | 0.087593 | 0.022035 | -0.087545 | -0.022017 | 4.8038e-05 | 1.8419e-05 | 0.13179 | 0.13179 | 0.13179 | 0.98919 | -0.07517 | 0.98863 | -0.079104 | 48.8122
90 | -0.090497 | -0.02279 | 0.090659 | 0.022852 | 0.00016218 | 6.2197e-05 | 0.13585 | 0.13585 | 0.13585 | 0.99151 | -0.05895 | 0.99334 | -0.046152 | 50.3161
91 | 0.085316 | 0.021458 | -0.084987 | -0.021332 | 0.00032912 | 0.00012618 | 0.12844 | 0.12844 | 0.12844 | 0.98863 | -0.079104 | 0.9847 | -0.10688 | 47.57
92 | -0.093604 | -0.02359 | 0.09382 | 0.023673 | 0.00021662 | 8.3088e-05 | 0.14026 | 0.14026 | 0.14026 | 0.99334 | -0.046152 | 0.99571 | -0.02966 | 51.9496
93 | 0.034841 | 0.008748 | -0.034826 | -0.0087422 | 1.528e-05 | 5.7645e-06 | 0.052655 | 0.052655 | 0.052655 | 0.9847 | -0.10688 | 0.98425 | -0.11004 | 19.502
94 | 0.067117 | 0.016923 | -0.06709 | -0.016913 | 2.7762e-05 | 1.0448e-05 | 0.10034 | 0.10034 | 0.10034 | 0.99571 | -0.02966 | 0.99529 | -0.032613 | 18.5811
95 | -0.16094 | -0.040597 | 0.16115 | 0.040679 | 0.00021557 | 8.2599e-05 | 0.2406 | 0.2406 | 0.2406 | 0.99571 | -0.02966 | 0.99709 | -0.020123 | 44.5559
96 | 0.033466 | 0.0084014 | -0.033454 | -0.0083968 | 1.2324e-05 | 4.6419e-06 | 0.0506 | 0.0506 | 0.0506 | 0.98425 | -0.11004 | 0.98388 | -0.11269 | 18.7406
97 | -0.16229 | -0.040965 | 0.16242 | 0.041012 | 0.00012326 | 4.7232e-05 | 0.2423 | 0.2423 | 0.2423 | 0.99709 | -0.020123 | 0.99787 | -0.014719 | 44.8713
98 | 0.031952 | 0.0080203 | -0.03193 | -0.0080124 | 2.1238e-05 | 7.9837e-06 | 0.048328 | 0.048328 | 0.048328 | 0.98388 | -0.11269 | 0.98321 | -0.11748 | 17.8993
99 | 0.031584 | 0.0079255 | -0.031566 | -0.0079188 | 1.8024e-05 | 6.772e-06 | 0.047804 | 0.047804 | 0.047804 | 0.98321 | -0.11748 | 0.98263 | -0.1216 | 17.7051
100 | 0.030451 | 0.0076393 | -0.030443 | -0.0076365 | 7.5654e-06 | 2.8376e-06 | 0.046115 | 0.046115 | 0.046115 | 0.98263 | -0.1216 | 0.98238 | -0.12339 | 17.0797
101 | 0.029581 | 0.0074203 | -0.029559 | -0.0074123 | 2.1291e-05 | 7.9738e-06 | 0.044809 | 0.044809 | 0.044809 | 0.98238 | -0.12339 | 0.98165 | -0.12858 | 16.5958
102 | 0.028688 | 0.0071939 | -0.028677 | -0.0071897 | 1.1203e-05 | 4.1887e-06 | 0.043488 | 0.043488 | 0.043488 | 0.98165 | -0.12858 | 0.98125 | -0.1314 | 16.1066
103 | 0.027199 | 0.0068195 | -0.027183 | -0.0068135 | 1.6095e-05 | 5.9992e-06 | 0.041248 | 0.041248 | 0.041248 | 0.98125 | -0.1314 | 0.98065 | -0.13567 | 15.2769
104 | 0.026224 | 0.0065731 | -0.02622 | -0.0065716 | 3.827e-06 | 1.4231e-06 | 0.039792 | 0.039792 | 0.039792 | 0.98065 | -0.13567 | 0.9805 | -0.13673 | 14.7378
105 | 0.01631 | 0.004089 | -0.016275 | -0.0040767 | 3.4946e-05 | 1.229e-05 | 0.024753 | 0.024753 | 0.024753 | 0.9805 | -0.13673 | 0.97834 | -0.15222 | 9.1679
106 | 0.0081293 | 0.0020363 | -0.0081262 | -0.0020355 | 3.1533e-06 | 7.942e-07 | 0.012337 | 0.012337 | 0.012337 | 0.9805 | -0.13673 | 0.98011 | -0.13953 | 4.5692
107 | 0.0051283 | 0.0012836 | -0.0051261 | -0.0012835 | 2.2109e-06 | 1.1929e-07 | 0.0077993 | 0.0077996 | 0.0077996 | 0.97834 | -0.15222 | 0.9779 | -0.15535 | 2.8887
108 | 0.0067639 | 0.0016948 | -0.0067616 | -0.0016943 | 2.271e-06 | 4.4179e-07 | 0.010287 | 0.010288 | 0.010288 | 0.97834 | -0.15222 | 0.978 | -0.15465 | 3.8102
109 | 0.004383 | 0.0010984 | -0.0043827 | -0.0010984 | 3.5529e-07 | -2.4215e-08 | 0.0066664 | 0.0066665 | 0.0066665 | 0.97834 | -0.15222 | 0.97825 | -0.15281 | 2.4691
110 | 0.0070921 | 0.0017763 | -0.0070907 | -0.001776 | 1.4586e-06 | 3.0694e-07 | 0.010767 | 0.010767 | 0.010767 | 0.98011 | -0.13953 | 0.9799 | -0.14102 | 3.9878
111 | 0.0063597 | 0.0015928 | -0.0063596 | -0.0015928 | 6.652e-08 | 1.1185e-08 | 0.009657 | 0.0096571 | 0.0096571 | 0.9799 | -0.14102 | 0.97989 | -0.1411 | 3.5767
112 | 0.0043886 | 0.0010988 | -0.0043879 | -0.0010989 | 6.2929e-07 | -4.3992e-08 | 0.0066639 | 0.006664 | 0.006664 | 0.97989 | -0.1411 | 0.97975 | -0.14213 | 2.4681
113 | 0.0036892 | 0.00092375 | -0.0036884 | -0.00092396 | 7.757e-07 | -2.0023e-07 | 0.0056028 | 0.005603 | 0.005603 | 0.97975 | -0.14213 | 0.97954 | -0.14366 | 2.0752
114 | -0.0010975 | -0.00027505 | 0.0010975 | 0.00027484 | 3.0456e-08 | -2.0742e-07 | 0.0016708 | 0.0016707 | 0.0016708 | 0.97739 | -0.15899 | 0.97742 | -0.15879 | 0.61882
115 | -0.001766 | -0.00044239 | 0.0017661 | 0.00044225 | 5.6894e-08 | -1.3623e-07 | 0.0026885 | 0.0026884 | 0.0026885 | 0.97742 | -0.15879 | 0.97745 | -0.15856 | 0.99573
116 | 0.0054719 | 0.0013711 | -0.005471 | -0.001371 | 9.5358e-07 | 9.0154e-08 | 0.0083254 | 0.0083255 | 0.0083255 | 0.978 | -0.15465 | 0.97782 | -0.15591 | 3.0835
117 | 0.0033114 | 0.00082974 | -0.0033111 | -0.00082984 | 2.4978e-07 | -1.0166e-07 | 0.0050391 | 0.0050391 | 0.0050391 | 0.97782 | -0.15591 | 0.97775 | -0.15646 | 1.8663
118 | 0.0040533 | 0.0010146 | -0.0040523 | -0.0010148 | 9.6487e-07 | -1.388e-07 | 0.0061672 | 0.0061674 | 0.0061674 | 0.9779 | -0.15535 | 0.97766 | -0.15707 | 2.2842
119 | -0.0023545 | -0.00058973 | 0.0023546 | 0.0005896 | 1.1221e-07 | -1.3231e-07 | 0.0035842 | 0.0035842 | 0.0035842 | 0.97745 | -0.15856 | 0.9775 | -0.15821 | 1.3275
120 | -0.0030255 | -0.00075773 | 0.0030256 | 0.00075767 | 1.024e-07 | -5.761e-08 | 0.0046054 | 0.0046053 | 0.0046054 | 0.9775 | -0.15821 | 0.97754 | -0.15797 | 1.7057
121 | -0.16412 | -0.041439 | 0.16426 | 0.041492 | 0.0001386 | 5.3115e-05 | 0.24484 | 0.24484 | 0.24484 | 0.99787 | -0.014719 | 0.99874 | -0.0087137 | 45.341
122 | -0.0036995 | -0.00092657 | 0.0036999 | 0.00092645 | 4.583e-07 | -1.1414e-07 | 0.0056312 | 0.0056311 | 0.0056312 | 0.97754 | -0.15797 | 0.97766 | -0.15707 | 2.0856
123 | 0.001064 | 0.00026664 | -0.001064 | -0.00026666 | 1.6542e-09 | -1.2165e-08 | 0.0016154 | 0.0016154 | 0.0016154 | 0.98006 | -0.13995 | 0.98006 | -0.13996 | 0.59831
124 | 0.00039556 | 9.9134e-05 | -0.00039556 | -9.9136e-05 | 2.1677e-11 | -1.1667e-09 | 0.00060057 | 0.00060057 | 0.00060057 | 0.98006 | -0.13996 | 0.98006 | -0.13996 | 0.22243

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.17045 | 0.04287

## res_load
| p_mw | q_mvar
0 | 0.0006932 | 0.00017373
1 | 0.0029786 | 0.00074651
2 | 0.0017237 | 0.000432
3 | 0.0022326 | 0.00055953
4 | 0.0035915 | 0.00090012
5 | 0.00085482 | 0.00021424
6 | 0.00040151 | 0.00010063
7 | 0.00060521 | 0.00015168
8 | 0.00085988 | 0.00021551
9 | 0.0011378 | 0.00028516
10 | 0.0016293 | 0.00040835
11 | 0.00053285 | 0.00013354
12 | 0.0015674 | 0.00039282
13 | 0.00056844 | 0.00014246
14 | 0.0016852 | 0.00042236
15 | 0.0039227 | 0.00098313
16 | 0.0029234 | 0.00073268
17 | 0.0038515 | 0.00096527
18 | 0.0020998 | 0.00052626
19 | 0.0017921 | 0.00044915
20 | 0.0014953 | 0.00037476
21 | 0.00060873 | 0.00015256
22 | 0.001953 | 0.00048946
23 | 0.0021408 | 0.00053654
24 | 0.00075764 | 0.00018988
25 | 0.0011226 | 0.00028136
26 | 0.0024155 | 0.00060537
27 | 0.0041351 | 0.0010364
28 | 0.002286 | 0.00057293
29 | 0.0027821 | 0.00069726
30 | 0.0048619 | 0.0012185
31 | 0.0025921 | 0.00064965
32 | 0.0014233 | 0.00035671
33 | 0.0025308 | 0.00063429
34 | 0.0014162 | 0.00035494
35 | 0.0015428 | 0.00038665
36 | 0.0036299 | 0.00090974
37 | 0.0011481 | 0.00028775
38 | 0.0015141 | 0.00037947
39 | 0.0016853 | 0.00042238
40 | 0.0018086 | 0.00045329
41 | 0.0018824 | 0.00047177
42 | 0.001552 | 0.00038896
43 | 0.001238 | 0.00031027
44 | 0.001553 | 0.00038923
45 | 0.0014009 | 0.00035111
46 | 0.0011145 | 0.00027932
47 | 0.0017528 | 0.0004393
48 | 0.0021619 | 0.00054182
49 | 0.0027659 | 0.00069321
50 | 0.0021847 | 0.00054753
51 | 0.0011632 | 0.00029151
52 | 0.0016955 | 0.00042494
53 | 0.0009185 | 0.0002302
54 | 0.0020917 | 0.00052424
55 | 0.00053581 | 0.00013429
56 | 0.00055002 | 0.00013785
57 | 0.0024001 | 0.00060152
58 | 0.0020556 | 0.00051519
59 | 0.0014402 | 0.00036095
60 | 0.0015511 | 0.00038873
61 | 0.00047981 | 0.00012025
62 | 0.00067519 | 0.00016922
63 | 0.00093284 | 0.00023379
64 | 0.00038703 | 9.6999e-05
65 | 0.00062142 | 0.00015574
66 | 0.00026298 | 6.5909e-05
67 | 0.00054352 | 0.00013622
68 | 0.001397 | 0.00035012
69 | 0.0013055 | 0.00032719
70 | 0.0022284 | 0.0005585
71 | 0.0029441 | 0.00073787
72 | 0.0013598 | 0.0003408
73 | 0.0030392 | 0.0007617
74 | 0.0011413 | 0.00028603
75 | 0.0015021 | 0.00037646
76 | 0.00034647 | 8.6833e-05
77 | 0.0011151 | 0.00027947
78 | 0.00086259 | 0.00021618
79 | 0.0008714 | 0.00021839
80 | 0.0014773 | 0.00037024
81 | 0.00095926 | 0.00024041
82 | 0.0017808 | 0.00044632
83 | 0.001034 | 0.00025915
84 | 0.00073095 | 0.00018319
85 | 0.0019711 | 0.00049399
86 | 0.00069873 | 0.00017512
87 | 0.0010975 | 0.00027505
88 | 0.00066851 | 0.00016754
89 | 0.0012897 | 0.00032322
90 | 0.0021596 | 0.00054125
91 | 0.0033111 | 0.00082984
92 | 0.0026026 | 0.00065227
93 | 0.0043827 | 0.0010984
94 | 0.0010728 | 0.00026886
95 | 0.00058845 | 0.00014748
96 | 0.00067085 | 0.00016813
97 | 0.001701 | 0.0004263
98 | 0.001898 | 0.00047568
99 | 0.00067391 | 0.0001689
100 | 0.00035239 | 8.8317e-05
101 | 0.00095871 | 0.00024028
102 | 0.00066842 | 0.00016752
103 | 0.00039556 | 9.9136e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1