## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1511-1_3_2_node_37 | 0.4 | n |  | TRUE
1 | bus_LV_1511-1_3_2_node_38 | 0.4 | n |  | TRUE
2 | bus_LV_1511-1_3_2_node_39 | 0.4 | n |  | TRUE
3 | bus_LV_1511-1_3_2_node_40 | 0.4 | n |  | TRUE
4 | bus_LV_1511-1_3_2_node_54 | 0.4 | n |  | TRUE
5 | bus_LV_1511-1_3_2_node_41 | 0.4 | n |  | TRUE
6 | bus_LV_1511-1_3_2_node_42 | 0.4 | n |  | TRUE
7 | bus_LV_1511-1_3_2_node_43 | 0.4 | n |  | TRUE
8 | bus_LV_1511-1_3_2_node_44 | 0.4 | n |  | TRUE
9 | bus_LV_1511-1_3_2_node_45 | 0.4 | n |  | TRUE
10 | bus_LV_1511-1_3_2_node_99 | 0.4 | n |  | TRUE
11 | bus_LV_1511-1_3_2_node_55 | 0.4 | n |  | TRUE
12 | bus_LV_1511-1_3_2_node_56 | 0.4 | n |  | TRUE
13 | bus_LV_1511-1_3_2_node_61 | 0.4 | n |  | TRUE
14 | bus_LV_1511-1_3_2_node_57 | 0.4 | n |  | TRUE
15 | bus_LV_1511-1_3_2_node_58 | 0.4 | n |  | TRUE
16 | bus_LV_1511-1_3_2_node_59 | 0.4 | n |  | TRUE
17 | bus_LV_1511-1_3_2_node_62 | 0.4 | n |  | TRUE
18 | bus_LV_1511-1_3_2_node_60 | 0.4 | n |  | TRUE
19 | bus_LV_1511-1_3_2_node_66 | 0.4 | n |  | TRUE
20 | bus_LV_1511-1_3_2_node_63 | 0.4 | n |  | TRUE
21 | bus_LV_1511-1_3_2_node_64 | 0.4 | n |  | TRUE
22 | bus_LV_1511-1_3_2_node_67 | 0.4 | n |  | TRUE
23 | bus_LV_1511-1_3_2_node_68 | 0.4 | n |  | TRUE
24 | bus_MV_0_node_37 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1511-1_3_2_load_37 | 0 | 0.0033768 | 0.00084632 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1511-1_3_2_load_38 | 1 | 0.00033032 | 8.2787e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1511-1_3_2_load_39 | 2 | 0.0037357 | 0.00093625 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1511-1_3_2_load_40 | 3 | 0.00025075 | 6.2843e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1511-1_3_2_load_54 | 4 | 0.0006748 | 0.00016912 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1511-1_3_2_load_41 | 5 | 0.0010274 | 0.00025749 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1511-1_3_2_load_42 | 6 | 0.0023622 | 0.00059203 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1511-1_3_2_load_44 | 8 | 0.0030093 | 0.00075419 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1511-1_3_2_load_99 | 10 | 0.0022414 | 0.00056176 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1511-1_3_2_load_57 | 14 | 0.0008627 | 0.00021621 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1511-1_3_2_load_59 | 16 | 0.00052662 | 0.00013198 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1511-1_3_2_load_62 | 17 | 0.00050048 | 0.00012543 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1511-1_3_2_load_60 | 18 | 0.001579 | 0.00039573 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1511-1_3_2_load_66 | 19 | 0.00069917 | 0.00017523 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1511-1_3_2_load_63 | 20 | 0.0014237 | 0.00035682 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1511-1_3_2_load_67 | 22 | 0.001363 | 0.00034161 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1511-1_3_2_load_68 | 23 | 0.00024959 | 6.2554e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 0 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1511-1_3_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.12507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1511-1_3_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0090756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1511-1_3_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0094026 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1511-1_3_2_line_3 | NAYY 4x150 SE | 3 | 4 | 0.015245 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1511-1_3_2_line_4 | NAYY 4x150 SE | 4 | 11 | 0.020801 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1511-1_3_2_line_5 | NAYY 4x150 SE | 5 | 6 | 0.028054 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1511-1_3_2_line_6 | NAYY 4x150 SE | 5 | 7 | 0.027054 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1511-1_3_2_line_7 | NAYY 4x150 SE | 6 | 8 | 0.019931 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1511-1_3_2_line_8 | NAYY 4x150 SE | 7 | 9 | 0.042435 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1511-1_3_2_line_9 | NAYY 4x150 SE | 9 | 10 | 0.036842 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1511-1_3_2_line_10 | NAYY 4x150 SE | 9 | 11 | 0.1236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1511-1_3_2_line_11 | NAYY 4x150 SE | 11 | 12 | 0.14109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1511-1_3_2_line_12 | NAYY 4x150 SE | 12 | 13 | 0.12398 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1511-1_3_2_line_13 | NAYY 4x150 SE | 12 | 14 | 0.031658 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1511-1_3_2_line_14 | NAYY 4x150 SE | 13 | 18 | 0.058319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1511-1_3_2_line_15 | NAYY 4x150 SE | 14 | 15 | 0.01554 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1511-1_3_2_line_16 | NAYY 4x150 SE | 15 | 16 | 0.0067163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1511-1_3_2_line_17 | NAYY 4x150 SE | 16 | 17 | 0.06805 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1511-1_3_2_line_18 | NAYY 4x150 SE | 18 | 19 | 0.21413 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1511-1_3_2_line_19 | NAYY 4x150 SE | 19 | 22 | 0.089098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1511-1_3_2_line_20 | NAYY 4x150 SE | 19 | 21 | 0.087969 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1511-1_3_2_line_21 | NAYY 4x150 SE | 20 | 21 | 0.049085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1511-1_3_2_line_22 | NAYY 4x150 SE | 22 | 23 | 0.0042415 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1511-1_3_2_trafo_37 | 0.25 MVA 20/0.4 kV | 24 | 0 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2673097.6007 | 1196360.206 | 2673079.8734 | 1196358.5385 | 2673051.5805 | 1196362.1284 | 2673030.9777 | 1196367.9693 | 2673011.8556 | 1196379.8208 | 2672987.5188 | 1196404.7463
1 | 2673106.6364 | 1196361.056 | 2673097.6007 | 1196360.206
2 | 2672987.5188 | 1196404.7463 | 2672980.95 | 1196411.4739
3 | 2672965.7585 | 1196412.7556 | 2672980.95 | 1196411.4739 | 2672980.95 | 1196411.4739
4 | 2672945.0308 | 1196414.5043 | 2672965.7585 | 1196412.7556
5 | 2672956.0355 | 1196246.6043 | 2672983.9539 | 1196243.8443
6 | 2672929.1131 | 1196249.2659 | 2672956.0355 | 1196246.6043
7 | 2673003.7885 | 1196241.8834 | 2672983.9539 | 1196243.8443
8 | 2672929.1131 | 1196249.2659 | 2672933.1842 | 1196291.4966
9 | 2672969.977 | 1196288.1099 | 2672933.1842 | 1196291.4966
10 | 2672945.0308 | 1196414.5043 | 2672933.1842 | 1196291.4966
11 | 2672945.0308 | 1196414.5043 | 2672958.5613 | 1196554.9209
12 | 2672958.5613 | 1196554.9209 | 2672970.4479 | 1196678.3072
13 | 2672958.5613 | 1196554.9209 | 2672986.6896 | 1196540.3945
14 | 2672970.4479 | 1196678.3072 | 2672988.2795 | 1196677.8467 | 2673018.5177 | 1196678.8941 | 2673023.0031 | 1196674.6574 | 2673022.6799 | 1196670.6154
15 | 2673000.497 | 1196533.2638 | 2672986.6896 | 1196540.3945
16 | 2673000.497 | 1196533.2638 | 2673007.0627 | 1196531.85
17 | 2673073.5875 | 1196517.5246 | 2673007.0627 | 1196531.85
18 | 2673022.6799 | 1196670.6154 | 2673229.1488 | 1196727.3987
19 | 2673305.9785 | 1196730.759 | 2673303.1234 | 1196720.0446 | 2673301.4292 | 1196718.4228 | 2673299.0246 | 1196717.5817 | 2673292.6601 | 1196719.1158 | 2673281.526 | 1196723.193 | 2673273.4502 | 1196724.5059 | 2673261.279 | 1196724.3234 | 2673242.9628 | 1196722.6759 | 2673237.8355 | 1196722.0905 | 2673234.4414 | 1196722.4269 | 2673231.5239 | 1196724.2812 | 2673229.2811 | 1196727.0221 | 2673229.1488 | 1196727.3987
20 | 2673243.3322 | 1196807.554 | 2673247.8002 | 1196802.8726 | 2673249.6702 | 1196797.6034 | 2673250.6337 | 1196792.3342 | 2673250.4992 | 1196785.9065 | 2673249.5461 | 1196780.3803 | 2673246.4552 | 1196772.1375 | 2673237.6474 | 1196754.8525 | 2673231.0049 | 1196744.2648 | 2673228.199 | 1196738.249 | 2673227.4125 | 1196734.0479 | 2673227.9314 | 1196730.8635 | 2673229.1488 | 1196727.3987
21 | 2673243.3322 | 1196807.554 | 2673250.9225 | 1196810.4154 | 2673286.7147 | 1196829.999 | 2673286.8642 | 1196830.0869
22 | 2673307.0706 | 1196734.8575 | 2673305.9785 | 1196730.759

## bus_geodata
| x | y | coords
0 | 2673097.6007 | 1196360.206
1 | 2672987.5188 | 1196404.7463
2 | 2673106.6364 | 1196361.056
3 | 2672980.95 | 1196411.4739
4 | 2672965.7585 | 1196412.7556
5 | 2672956.0355 | 1196246.6043
6 | 2672983.9539 | 1196243.8443
7 | 2672929.1131 | 1196249.2659
8 | 2673003.7885 | 1196241.8834
9 | 2672933.1842 | 1196291.4966
10 | 2672969.977 | 1196288.1099
11 | 2672945.0308 | 1196414.5043
12 | 2672958.5613 | 1196554.9209
13 | 2672970.4479 | 1196678.3072
14 | 2672986.6896 | 1196540.3945
15 | 2673000.497 | 1196533.2638
16 | 2673007.0627 | 1196531.85
17 | 2673073.5875 | 1196517.5246
18 | 2673022.6799 | 1196670.6154
19 | 2673229.1488 | 1196727.3987
20 | 2673286.8642 | 1196830.0869
21 | 2673243.3322 | 1196807.554
22 | 2673305.9785 | 1196730.759
23 | 2673307.0706 | 1196734.8575
24 | 2673097.6007 | 1196360.206

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 1 | 0 | -0.021745 | -0.0052467
1 | 0.99693 | -0.021566 | 0.00033032 | 8.2787e-05
2 | 0.99995 | -0.00033842 | 0.0037357 | 0.00093625
3 | 0.99671 | -0.023161 | 0.00025075 | 6.2843e-05
4 | 0.99634 | -0.02571 | 0.0006748 | 0.00016912
5 | 0.9937 | -0.044335 | 0.0010274 | 0.00025749
6 | 0.99349 | -0.04586 | 0.0023622 | 0.00059203
7 | 0.99395 | -0.042584 | 0 | 0
8 | 0.9934 | -0.046466 | 0.0030093 | 0.00075419
9 | 0.99434 | -0.039838 | 0 | 0
10 | 0.99422 | -0.040673 | 0.0022414 | 0.00056176
11 | 0.99587 | -0.029049 | 0 | 0
12 | 0.99441 | -0.039405 | 0 | 0
13 | 0.99347 | -0.04613 | 0 | 0
14 | 0.99433 | -0.040012 | 0.0008627 | 0.00021621
15 | 0.9943 | -0.040175 | 0 | 0
16 | 0.99429 | -0.040245 | 0.00052662 | 0.00013198
17 | 0.99425 | -0.040591 | 0.00050048 | 0.00012543
18 | 0.99302 | -0.049292 | 0.001579 | 0.00039573
19 | 0.99187 | -0.057468 | 0.00069917 | 0.00017523
20 | 0.99159 | -0.059457 | 0.0014237 | 0.00035682
21 | 0.99169 | -0.058747 | 0 | 0
22 | 0.99167 | -0.05893 | 0.001363 | 0.00034161
23 | 0.99166 | -0.058941 | 0.00024959 | 6.2554e-05
24 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.01721 | 0.0043104 | -0.017158 | -0.0042924 | 5.1178e-05 | 1.8048e-05 | 0.025607 | 0.025608 | 0.025608 | 1 | 0 | 0.99693 | -0.021566 | 9.4844
1 | 0.0037359 | 0.0009362 | -0.0037357 | -0.00093625 | 1.7501e-07 | -5.175e-08 | 0.005559 | 0.005559 | 0.005559 | 1 | 0 | 0.99995 | -0.00033842 | 2.0589
2 | 0.016828 | 0.0042096 | -0.016824 | -0.0042083 | 3.7008e-06 | 1.3008e-06 | 0.025115 | 0.025115 | 0.025115 | 0.99693 | -0.021566 | 0.99671 | -0.023161 | 9.3018
3 | 0.016574 | 0.0041454 | -0.016568 | -0.0041434 | 5.823e-06 | 2.041e-06 | 0.02474 | 0.024741 | 0.024741 | 0.99671 | -0.023161 | 0.99634 | -0.02571 | 9.1632
4 | 0.015893 | 0.0039743 | -0.015886 | -0.0039717 | 7.3109e-06 | 2.5411e-06 | 0.023733 | 0.023733 | 0.023733 | 0.99634 | -0.02571 | 0.99587 | -0.029049 | 8.7899
5 | 0.0053729 | 0.0013461 | -0.0053718 | -0.0013461 | 1.1332e-06 | 7.2479e-08 | 0.0080455 | 0.0080456 | 0.0080456 | 0.9937 | -0.044335 | 0.99349 | -0.04586 | 2.9798
6 | -0.0064003 | -0.0016036 | 0.0064018 | 0.0016039 | 1.5506e-06 | 2.4581e-07 | 0.0095839 | 0.0095838 | 0.0095839 | 0.9937 | -0.044335 | 0.99395 | -0.042584 | 3.5496
7 | 0.0030095 | 0.00075403 | -0.0030093 | -0.00075419 | 2.5269e-07 | -1.6088e-07 | 0.0045075 | 0.0045076 | 0.0045076 | 0.99349 | -0.04586 | 0.9934 | -0.046466 | 1.6695
8 | -0.0064018 | -0.0016039 | 0.0064042 | 0.0016043 | 2.4321e-06 | 3.8519e-07 | 0.0095838 | 0.0095836 | 0.0095838 | 0.99395 | -0.042584 | 0.99434 | -0.039838 | 3.5495
9 | 0.0022417 | 0.00056138 | -0.0022414 | -0.00056176 | 2.5871e-07 | -3.7833e-07 | 0.0033545 | 0.0033547 | 0.0033547 | 0.99434 | -0.039838 | 0.99422 | -0.040673 | 1.2425
10 | -0.0086459 | -0.0021656 | 0.0086588 | 0.002169 | 1.291e-05 | 3.3596e-06 | 0.012938 | 0.012938 | 0.012938 | 0.99434 | -0.039838 | 0.99587 | -0.029049 | 4.7919
11 | 0.0072269 | 0.0018027 | -0.0072166 | -0.0018006 | 1.0261e-05 | 2.1134e-06 | 0.010795 | 0.010796 | 0.010796 | 0.99587 | -0.029049 | 0.99441 | -0.039405 | 3.9985
12 | 0.0053266 | 0.0013285 | -0.0053217 | -0.0013282 | 4.9126e-06 | 2.8255e-07 | 0.0079683 | 0.0079689 | 0.0079689 | 0.99441 | -0.039405 | 0.99347 | -0.04613 | 2.9514
13 | 0.00189 | 0.00047213 | -0.0018899 | -0.00047248 | 1.5795e-07 | -3.4991e-07 | 0.0028276 | 0.0028278 | 0.0028278 | 0.99441 | -0.039405 | 0.99433 | -0.040012 | 1.0473
14 | 0.0053217 | 0.0013282 | -0.0053194 | -0.0013281 | 2.311e-06 | 1.3406e-07 | 0.0079689 | 0.0079692 | 0.0079692 | 0.99347 | -0.04613 | 0.99302 | -0.049292 | 2.9515
15 | 0.0010272 | 0.00025627 | -0.0010271 | -0.00025646 | 2.2901e-08 | -1.9275e-07 | 0.0015367 | 0.0015368 | 0.0015368 | 0.99433 | -0.040012 | 0.9943 | -0.040175 | 0.56919
16 | 0.0010271 | 0.00025646 | -0.0010271 | -0.00025654 | 9.8983e-09 | -8.3304e-08 | 0.0015368 | 0.0015368 | 0.0015368 | 0.9943 | -0.040175 | 0.99429 | -0.040245 | 0.5692
17 | 0.00050051 | 0.00012456 | -0.00050048 | -0.00012543 | 2.3814e-08 | -8.734e-07 | 0.00074872 | 0.00074903 | 0.00074903 | 0.99429 | -0.040245 | 0.99425 | -0.040591 | 0.27742
18 | 0.0037404 | 0.00093236 | -0.0037362 | -0.00093351 | 4.1958e-06 | -1.1533e-06 | 0.0056031 | 0.0056041 | 0.0056041 | 0.99302 | -0.049292 | 0.99187 | -0.057468 | 2.0756
19 | 0.0016129 | 0.00040308 | -0.0016126 | -0.0004041 | 3.2548e-07 | -1.0246e-06 | 0.0024193 | 0.0024197 | 0.0024197 | 0.99187 | -0.057468 | 0.99167 | -0.05893 | 0.8962
20 | 0.0014241 | 0.0003552 | -0.0014239 | -0.00035624 | 2.5047e-07 | -1.0389e-06 | 0.0021359 | 0.0021363 | 0.0021363 | 0.99187 | -0.057468 | 0.99169 | -0.058747 | 0.79121
21 | -0.0014237 | -0.00035682 | 0.0014239 | 0.00035624 | 1.398e-07 | -5.7947e-07 | 0.0021365 | 0.0021363 | 0.0021365 | 0.99159 | -0.059457 | 0.99169 | -0.058747 | 0.7913
22 | 0.00024959 | 6.2499e-05 | -0.00024959 | -6.2554e-05 | 3.7124e-10 | -5.4578e-08 | 0.0003745 | 0.00037452 | 0.00037452 | 0.99167 | -0.05893 | 0.99166 | -0.058941 | 0.13871

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.025122 | 0.006093

## res_load
| p_mw | q_mvar
0 | 0.0033768 | 0.00084632
1 | 0.00033032 | 8.2787e-05
2 | 0.0037357 | 0.00093625
3 | 0.00025075 | 6.2843e-05
4 | 0.0006748 | 0.00016912
5 | 0.0010274 | 0.00025749
6 | 0.0023622 | 0.00059203
7 | 0.0030093 | 0.00075419
8 | 0.0022414 | 0.00056176
9 | 0.0008627 | 0.00021621
10 | 0.00052662 | 0.00013198
11 | 0.00050048 | 0.00012543
12 | 0.001579 | 0.00039573
13 | 0.00069917 | 0.00017523
14 | 0.0014237 | 0.00035682
15 | 0.001363 | 0.00034161
16 | 0.00024959 | 6.2554e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1