## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1511-5_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1511-5_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1511-5_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1511-5_0_3_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1511-5_0_3_node_36 | 0.4 | n |  | TRUE
5 | bus_LV_1511-5_0_3_node_29 | 0.4 | n |  | TRUE
6 | bus_LV_1511-5_0_3_node_30 | 0.4 | n |  | TRUE
7 | bus_LV_1511-5_0_3_node_27 | 0.4 | n |  | TRUE
8 | bus_LV_1511-5_0_3_node_14 | 0.4 | n |  | TRUE
9 | bus_LV_1511-5_0_3_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_1511-5_0_3_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_1511-5_0_3_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1511-5_0_3_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1511-5_0_3_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1511-5_0_3_node_35 | 0.4 | n |  | TRUE
15 | bus_LV_1511-5_0_3_node_22 | 0.4 | n |  | TRUE
16 | bus_LV_1511-5_0_3_node_21 | 0.4 | n |  | TRUE
17 | bus_LV_1511-5_0_3_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_1511-5_0_3_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_1511-5_0_3_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_1511-5_0_3_node_34 | 0.4 | n |  | TRUE
21 | bus_LV_1511-5_0_3_node_40 | 0.4 | n |  | TRUE
22 | bus_LV_1511-5_0_3_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_1511-5_0_3_node_11 | 0.4 | n |  | TRUE
24 | bus_LV_1511-5_0_3_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_1511-5_0_3_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_1511-5_0_3_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_1511-5_0_3_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_1511-5_0_3_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_1511-5_0_3_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_1511-5_0_3_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_1511-5_0_3_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_1511-5_0_3_node_38 | 0.4 | n |  | TRUE
33 | bus_LV_1511-5_0_3_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_1511-5_0_3_node_28 | 0.4 | n |  | TRUE
35 | bus_LV_1511-5_0_3_node_42 | 0.4 | n |  | TRUE
36 | bus_LV_1511-5_0_3_node_39 | 0.4 | n |  | TRUE
37 | bus_LV_1511-5_0_3_node_37 | 0.4 | n |  | TRUE
38 | bus_LV_1511-5_0_3_node_31 | 0.4 | n |  | TRUE
39 | bus_LV_1511-5_0_3_node_32 | 0.4 | n |  | TRUE
40 | bus_LV_1511-5_0_3_node_33 | 0.4 | n |  | TRUE
41 | bus_MV_136_1_node_143 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1511-5_0_3_load_0 | 0 | 0.016994 | 0.0042591 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1511-5_0_3_load_1 | 1 | 0.0013951 | 0.00034964 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1511-5_0_3_load_36 | 4 | 0.0026656 | 0.00066806 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1511-5_0_3_load_27 | 7 | 0.0044504 | 0.0011154 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1511-5_0_3_load_5 | 9 | 0.020091 | 0.0050354 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1511-5_0_3_load_6 | 10 | 0.011146 | 0.0027936 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1511-5_0_3_load_35 | 14 | 0.00235 | 0.00058896 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1511-5_0_3_load_22 | 15 | 0.0017479 | 0.00043806 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1511-5_0_3_load_21 | 16 | 0.020463 | 0.0051284 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1511-5_0_3_load_10 | 17 | 0.0026261 | 0.00065817 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1511-5_0_3_load_13 | 18 | 0.0011826 | 0.00029638 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1511-5_0_3_load_12 | 19 | 0.0045588 | 0.0011425 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1511-5_0_3_load_34 | 20 | 0.0085253 | 0.0021366 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1511-5_0_3_load_40 | 21 | 0.031846 | 0.0079814 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1511-5_0_3_load_11 | 23 | 0.023943 | 0.0060007 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1511-5_0_3_load_15 | 24 | 0.0046994 | 0.0011778 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1511-5_0_3_load_18 | 26 | 0.0096213 | 0.0024113 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1511-5_0_3_load_19 | 27 | 0.0055138 | 0.0013819 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1511-5_0_3_load_23 | 29 | 0.0034459 | 0.00086362 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1511-5_0_3_load_38 | 32 | 0.0038015 | 0.00095273 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1511-5_0_3_load_25 | 33 | 0.0088899 | 0.002228 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1511-5_0_3_load_28 | 34 | 0.0045947 | 0.0011515 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1511-5_0_3_load_42 | 35 | 0.0062921 | 0.0015769 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1511-5_0_3_load_39 | 36 | 0.0032913 | 0.00082489 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1511-5_0_3_load_37 | 37 | 0.0023407 | 0.00058663 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1511-5_0_3_load_31 | 38 | 0.0072311 | 0.0018123 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1511-5_0_3_load_32 | 39 | 0.0052826 | 0.0013239 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 21 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1511-5_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.019208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1511-5_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.010933 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1511-5_0_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.023423 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1511-5_0_3_line_3 | NAYY 4x150 SE | 3 | 4 | 0.025907 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1511-5_0_3_line_4 | NAYY 4x150 SE | 4 | 8 | 0.025495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1511-5_0_3_line_5 | NAYY 4x150 SE | 5 | 6 | 0.014809 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1511-5_0_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.029941 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1511-5_0_3_line_7 | NAYY 4x150 SE | 6 | 36 | 0.010751 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1511-5_0_3_line_8 | NAYY 4x150 SE | 7 | 34 | 0.013176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1511-5_0_3_line_9 | NAYY 4x150 SE | 8 | 19 | 0.0094679 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1511-5_0_3_line_10 | NAYY 4x150 SE | 8 | 12 | 0.022949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1511-5_0_3_line_11 | NAYY 4x150 SE | 9 | 10 | 0.012036 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1511-5_0_3_line_12 | NAYY 4x150 SE | 9 | 11 | 0.018267 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
13 | LV_1511-5_0_3_line_13 | NAYY 4x150 SE | 10 | 12 | 0.026619 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1511-5_0_3_line_14 | NAYY 4x150 SE | 11 | 13 | 0.024089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
15 | LV_1511-5_0_3_line_15 | NAYY 4x150 SE | 12 | 14 | 0.0036091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1511-5_0_3_line_16 | NAYY 4x150 SE | 13 | 15 | 0.013261 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
17 | LV_1511-5_0_3_line_17 | NAYY 4x150 SE | 13 | 16 | 0.0038711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1511-5_0_3_line_18 | NAYY 4x150 SE | 14 | 20 | 0.033182 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1511-5_0_3_line_19 | NAYY 4x150 SE | 15 | 21 | 0.019957 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
20 | LV_1511-5_0_3_line_20 | NAYY 4x150 SE | 16 | 22 | 0.022086 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1511-5_0_3_line_21 | NAYY 4x150 SE | 17 | 18 | 0.0046957 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1511-5_0_3_line_22 | NAYY 4x150 SE | 18 | 23 | 0.00535 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1511-5_0_3_line_23 | NAYY 4x150 SE | 19 | 23 | 0.017271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1511-5_0_3_line_24 | NAYY 4x150 SE | 20 | 40 | 0.014148 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1511-5_0_3_line_25 | NAYY 4x150 SE | 21 | 32 | 0.0018857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1511-5_0_3_line_26 | NAYY 4x150 SE | 22 | 25 | 0.02449 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1511-5_0_3_line_27 | NAYY 4x150 SE | 24 | 25 | 0.026988 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1511-5_0_3_line_28 | NAYY 4x150 SE | 25 | 26 | 0.034011 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1511-5_0_3_line_29 | NAYY 4x150 SE | 26 | 27 | 0.0096402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1511-5_0_3_line_30 | NAYY 4x150 SE | 27 | 28 | 0.012204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1511-5_0_3_line_31 | NAYY 4x150 SE | 28 | 29 | 0.021036 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1511-5_0_3_line_32 | NAYY 4x150 SE | 28 | 30 | 0.006472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1511-5_0_3_line_33 | NAYY 4x150 SE | 30 | 31 | 0.023998 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1511-5_0_3_line_34 | NAYY 4x150 SE | 31 | 33 | 0.0031906 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1511-5_0_3_line_35 | NAYY 4x150 SE | 32 | 37 | 0.016083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1511-5_0_3_line_36 | NAYY 4x150 SE | 34 | 35 | 0.051287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1511-5_0_3_line_37 | NAYY 4x150 SE | 36 | 37 | 0.015108 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1511-5_0_3_line_38 | NAYY 4x150 SE | 38 | 39 | 0.018772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1511-5_0_3_line_39 | NAYY 4x150 SE | 38 | 40 | 0.022305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1511-5_0_3_trafo_40 | 0.25 MVA 20/0.4 kV | 41 | 21 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2672960.1553 | 1195756.4293 | 2672940.9841 | 1195755.2331
1 | 2672962.5746 | 1195764.7368 | 2672962.9406 | 1195756.603 | 2672960.1553 | 1195756.4293
2 | 2672986.0559 | 1195765.4348 | 2672984.8297 | 1195765.3976 | 2672962.5746 | 1195764.7368
3 | 2672986.0559 | 1195765.4348 | 2672987.0236 | 1195739.5455
4 | 2672992.3246 | 1195715.0364 | 2672987.5155 | 1195726.3846 | 2672987.0236 | 1195739.5455
5 | 2672914.5007 | 1195757.0127 | 2672916.569 | 1195742.3513
6 | 2672914.5007 | 1195757.0127 | 2672884.6969 | 1195754.1488
7 | 2672916.569 | 1195742.3513 | 2672918.3824 | 1195731.7542
8 | 2672871.5349 | 1195753.921 | 2672881.7691 | 1195753.8675 | 2672884.6969 | 1195754.1488
9 | 2672992.3246 | 1195715.0364 | 2672983.4389 | 1195711.7675
10 | 2673001.2762 | 1195693.8995 | 2672992.3246 | 1195715.0364
11 | 2672967.2042 | 1195675.643 | 2672977.8138 | 1195681.3269
12 | 2672950.9557 | 1195667.303 | 2672958.4693 | 1195670.9635 | 2672967.2042 | 1195675.643
13 | 2673001.2762 | 1195693.8995 | 2672998.2029 | 1195692.2499 | 2672977.8138 | 1195681.3269
14 | 2672926.924 | 1195666.0981 | 2672942.7901 | 1195665.8692 | 2672950.9557 | 1195667.303
15 | 2673001.2762 | 1195693.8995 | 2673004.3204 | 1195695.8383
16 | 2672926.924 | 1195666.0981 | 2672926.0479 | 1195679.3297
17 | 2672926.924 | 1195666.0981 | 2672925.9413 | 1195662.3538
18 | 2673004.3204 | 1195695.8383 | 2673032.3082 | 1195713.6626
19 | 2672926.0479 | 1195679.3297 | 2672925.2242 | 1195691.7707 | 2672923.9612 | 1195699.1517
20 | 2672920.3348 | 1195640.9916 | 2672925.9413 | 1195662.3538
21 | 2672961.5723 | 1195706.2569 | 2672960.2513 | 1195706.0064 | 2672957.6484 | 1195703.8956
22 | 2672961.5723 | 1195706.2569 | 2672966.8285 | 1195707.2538
23 | 2672983.4389 | 1195711.7675 | 2672975.789 | 1195708.9532 | 2672966.8285 | 1195707.2538
24 | 2673044.2419 | 1195721.2627 | 2673032.3082 | 1195713.6626
25 | 2672923.6431 | 1195701.0104 | 2672923.9612 | 1195699.1517
26 | 2672912.1972 | 1195617.8896 | 2672916.0799 | 1195628.7657 | 2672920.3348 | 1195640.9916
27 | 2672912.1972 | 1195617.8896 | 2672903.8753 | 1195592.2165
28 | 2672912.1972 | 1195617.8896 | 2672879.5711 | 1195627.4976
29 | 2672879.5711 | 1195627.4976 | 2672870.3236 | 1195630.2209
30 | 2672858.6164 | 1195633.6685 | 2672870.3236 | 1195630.2209
31 | 2672858.6164 | 1195633.6685 | 2672854.8379 | 1195612.9767
32 | 2672858.6164 | 1195633.6685 | 2672854.9006 | 1195634.0902 | 2672852.169 | 1195634.4127
33 | 2672849.8918 | 1195636.2083 | 2672851.6515 | 1195646.2468 | 2672853.8117 | 1195645.9174 | 2672852.169 | 1195634.4127
34 | 2672849.8918 | 1195636.2083 | 2672849.37 | 1195633.0606
35 | 2672920.9305 | 1195716.863 | 2672923.6431 | 1195701.0104
36 | 2672871.5349 | 1195753.921 | 2672821.0953 | 1195744.6389
37 | 2672920.9305 | 1195716.863 | 2672918.3824 | 1195731.7542
38 | 2673052.0459 | 1195700.3777 | 2673056.7389 | 1195682.2022
39 | 2673044.2419 | 1195721.2627 | 2673051.6479 | 1195701.9192 | 2673052.0459 | 1195700.3777

## bus_geodata
| x | y | coords
0 | 2672960.1553 | 1195756.4293
1 | 2672940.9841 | 1195755.2331
2 | 2672962.5746 | 1195764.7368
3 | 2672986.0559 | 1195765.4348
4 | 2672987.0236 | 1195739.5455
5 | 2672914.5007 | 1195757.0127
6 | 2672916.569 | 1195742.3513
7 | 2672884.6969 | 1195754.1488
8 | 2672992.3246 | 1195715.0364
9 | 2672967.2042 | 1195675.643
10 | 2672977.8138 | 1195681.3269
11 | 2672950.9557 | 1195667.303
12 | 2673001.2762 | 1195693.8995
13 | 2672926.924 | 1195666.0981
14 | 2673004.3204 | 1195695.8383
15 | 2672926.0479 | 1195679.3297
16 | 2672925.9413 | 1195662.3538
17 | 2672957.6484 | 1195703.8956
18 | 2672961.5723 | 1195706.2569
19 | 2672983.4389 | 1195711.7675
20 | 2673032.3082 | 1195713.6626
21 | 2672923.9612 | 1195699.1517
22 | 2672920.3348 | 1195640.9916
23 | 2672966.8285 | 1195707.2538
24 | 2672903.8753 | 1195592.2165
25 | 2672912.1972 | 1195617.8896
26 | 2672879.5711 | 1195627.4976
27 | 2672870.3236 | 1195630.2209
28 | 2672858.6164 | 1195633.6685
29 | 2672854.8379 | 1195612.9767
30 | 2672852.169 | 1195634.4127
31 | 2672849.8918 | 1195636.2083
32 | 2672923.6431 | 1195701.0104
33 | 2672849.37 | 1195633.0606
34 | 2672871.5349 | 1195753.921
35 | 2672821.0953 | 1195744.6389
36 | 2672918.3824 | 1195731.7542
37 | 2672920.9305 | 1195716.863
38 | 2673052.0459 | 1195700.3777
39 | 2673056.7389 | 1195682.2022
40 | 2673044.2419 | 1195721.2627
41 | 2672926.924 | 1195666.0981

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98419 | -0.111 | 0.016994 | 0.0042591
1 | 0.98415 | -0.11128 | 0.0013951 | 0.00034964
2 | 0.98448 | -0.10893 | 0 | 0
3 | 0.98511 | -0.1045 | 0 | 0
4 | 0.9858 | -0.0996 | 0.0026656 | 0.00066806
5 | 0.99849 | -0.010576 | 0 | 0
6 | 0.99881 | -0.0083019 | 0 | 0
7 | 0.99783 | -0.015179 | 0.0044504 | 0.0011154
8 | 0.98658 | -0.094089 | 0 | 0
9 | 0.99283 | -0.049999 | 0.020091 | 0.0050354
10 | 0.9913 | -0.060731 | 0.011146 | 0.0027936
11 | 0.99425 | -0.040024 | 0 | 0
12 | 0.98835 | -0.08155 | 0 | 0
13 | 0.99613 | -0.026913 | 0 | 0
14 | 0.98823 | -0.082413 | 0.00235 | 0.00058896
15 | 0.99767 | -0.016214 | 0.0017479 | 0.00043806
16 | 0.99584 | -0.028963 | 0.020463 | 0.0051284
17 | 0.98539 | -0.10249 | 0.0026261 | 0.00065817
18 | 0.98541 | -0.10236 | 0.0011826 | 0.00029638
19 | 0.98613 | -0.097227 | 0.0045588 | 0.0011425
20 | 0.98722 | -0.089557 | 0.0085253 | 0.0021366
21 | 1 | 0 | -0.18964 | -0.047544
22 | 0.99482 | -0.036125 | 0 | 0
23 | 0.98544 | -0.10215 | 0.023943 | 0.0060007
24 | 0.99351 | -0.045365 | 0.0046994 | 0.0011778
25 | 0.99369 | -0.044082 | 0 | 0
26 | 0.99234 | -0.053542 | 0.0096213 | 0.0024113
27 | 0.9921 | -0.055287 | 0.0055138 | 0.0013819
28 | 0.99188 | -0.056815 | 0 | 0
29 | 0.99178 | -0.05755 | 0.0034459 | 0.00086362
30 | 0.9918 | -0.057399 | 0 | 0
31 | 0.99149 | -0.059564 | 0 | 0
32 | 0.99993 | -0.0004665 | 0.0038015 | 0.00095273
33 | 0.99145 | -0.059852 | 0.0088899 | 0.002228
34 | 0.99763 | -0.016617 | 0.0045947 | 0.0011515
35 | 0.99717 | -0.019856 | 0.0062921 | 0.0015769
36 | 0.99905 | -0.0066515 | 0.0032913 | 0.00082489
37 | 0.99945 | -0.0038366 | 0.0023407 | 0.00058663
38 | 0.98656 | -0.094233 | 0.0072311 | 0.0018123
39 | 0.98641 | -0.09525 | 0.0052826 | 0.0013239
40 | 0.98696 | -0.091371 | 0 | 0
41 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0013951 | 0.00034942 | -0.0013951 | -0.00034964 | 5.3328e-08 | -2.2358e-07 | 0.0021093 | 0.0021093 | 0.0021093 | 0.98419 | -0.111 | 0.98415 | -0.11128 | 0.78124
1 | -0.018389 | -0.0046086 | 0.018395 | 0.0046104 | 5.2734e-06 | 1.8893e-06 | 0.027803 | 0.027803 | 0.027803 | 0.98419 | -0.111 | 0.98448 | -0.10893 | 10.2974
2 | -0.018395 | -0.0046104 | 0.018406 | 0.0046145 | 1.1298e-05 | 4.0474e-06 | 0.027803 | 0.027803 | 0.027803 | 0.98448 | -0.10893 | 0.98511 | -0.1045 | 10.2974
3 | -0.018406 | -0.0046145 | 0.018418 | 0.004619 | 1.2496e-05 | 4.4762e-06 | 0.027803 | 0.027803 | 0.027803 | 0.98511 | -0.1045 | 0.9858 | -0.0996 | 10.2973
4 | -0.021084 | -0.005287 | 0.0211 | 0.0052929 | 1.6114e-05 | 5.8725e-06 | 0.031826 | 0.031826 | 0.031826 | 0.9858 | -0.0996 | 0.98658 | -0.094089 | 11.7875
5 | -0.015352 | -0.0038483 | 0.015357 | 0.00385 | 4.837e-06 | 1.6666e-06 | 0.022879 | 0.022879 | 0.022879 | 0.99849 | -0.010576 | 0.99881 | -0.0083019 | 8.4736
6 | 0.015352 | 0.0038483 | -0.015342 | -0.0038449 | 9.7796e-06 | 3.37e-06 | 0.022879 | 0.022879 | 0.022879 | 0.99849 | -0.010576 | 0.99783 | -0.015179 | 8.4737
7 | -0.015357 | -0.00385 | 0.01536 | 0.0038512 | 3.5115e-06 | 1.2098e-06 | 0.022879 | 0.022879 | 0.022879 | 0.99881 | -0.0083019 | 0.99905 | -0.0066515 | 8.4736
8 | 0.010892 | 0.0027295 | -0.01089 | -0.0027289 | 2.1689e-06 | 6.6213e-07 | 0.016242 | 0.016242 | 0.016242 | 0.99783 | -0.015179 | 0.99763 | -0.016617 | 6.0156
9 | 0.032344 | 0.00811 | -0.032329 | -0.0081047 | 1.406e-05 | 5.287e-06 | 0.048784 | 0.048784 | 0.048784 | 0.98658 | -0.094089 | 0.98613 | -0.097227 | 18.0682
10 | -0.053444 | -0.013403 | 0.053537 | 0.013438 | 9.3052e-05 | 3.5496e-05 | 0.08061 | 0.08061 | 0.08061 | 0.98658 | -0.094089 | 0.98835 | -0.08155 | 29.8556
11 | 0.08846 | 0.022241 | -0.088328 | -0.022191 | 0.00013207 | 5.064e-05 | 0.13261 | 0.13261 | 0.13261 | 0.99283 | -0.049999 | 0.9913 | -0.060731 | 49.113
12 | -0.10855 | -0.027277 | 0.1087 | 0.027334 | 0.0001509 | 5.7566e-05 | 0.16272 | 0.16272 | 0.16272 | 0.99283 | -0.049999 | 0.99425 | -0.040024 | 30.1328
13 | 0.077181 | 0.019397 | -0.076958 | -0.019312 | 0.00022302 | 8.5434e-05 | 0.11587 | 0.11587 | 0.11587 | 0.9913 | -0.060731 | 0.98835 | -0.08155 | 42.9162
14 | -0.1087 | -0.027334 | 0.1089 | 0.02741 | 0.00019899 | 7.591e-05 | 0.16272 | 0.16272 | 0.16272 | 0.99425 | -0.040024 | 0.99613 | -0.026913 | 30.1328
15 | 0.023421 | 0.0058731 | -0.023419 | -0.0058721 | 2.8005e-06 | 1.0309e-06 | 0.035264 | 0.035264 | 0.035264 | 0.98835 | -0.08155 | 0.98823 | -0.082413 | 13.0606
16 | -0.16166 | -0.040649 | 0.16191 | 0.040741 | 0.00024138 | 9.2491e-05 | 0.24154 | 0.24154 | 0.24154 | 0.99613 | -0.026913 | 0.99767 | -0.016214 | 44.7296
17 | 0.052764 | 0.013239 | -0.052749 | -0.013233 | 1.5008e-05 | 5.722e-06 | 0.078823 | 0.078823 | 0.078823 | 0.99613 | -0.026913 | 0.99584 | -0.028963 | 29.1938
18 | 0.021069 | 0.0052832 | -0.021048 | -0.0052756 | 2.084e-05 | 7.5906e-06 | 0.031725 | 0.031725 | 0.031725 | 0.98823 | -0.082413 | 0.98722 | -0.089557 | 11.7501
19 | -0.16365 | -0.041179 | 0.16402 | 0.041322 | 0.00037114 | 0.00014222 | 0.24415 | 0.24415 | 0.24415 | 0.99767 | -0.016214 | 1 | 0 | 45.2124
20 | 0.032286 | 0.0081047 | -0.032254 | -0.0080927 | 3.2081e-05 | 1.2052e-05 | 0.048247 | 0.048247 | 0.048247 | 0.99584 | -0.028963 | 0.99482 | -0.036125 | 17.8694
21 | -0.0026261 | -0.00065817 | 0.0026262 | 0.00065813 | 4.608e-08 | -4.2096e-08 | 0.0039657 | 0.0039656 | 0.0039657 | 0.98539 | -0.10249 | 0.98541 | -0.10236 | 1.4688
22 | -0.0038087 | -0.0009545 | 0.0038088 | 0.00095448 | 1.1043e-07 | -2.5685e-08 | 0.0057513 | 0.0057513 | 0.0057513 | 0.98541 | -0.10236 | 0.98544 | -0.10215 | 2.1301
23 | 0.027771 | 0.0069622 | -0.027752 | -0.0069551 | 1.8925e-05 | 7.0588e-06 | 0.041905 | 0.041905 | 0.041905 | 0.98613 | -0.097227 | 0.98544 | -0.10215 | 15.5204
24 | 0.012523 | 0.0031389 | -0.012519 | -0.0031379 | 3.1454e-06 | 1.0289e-06 | 0.018875 | 0.018875 | 0.018875 | 0.98722 | -0.089557 | 0.98696 | -0.091371 | 6.9908
25 | 0.024812 | 0.0062222 | -0.024811 | -0.0062216 | 1.6042e-06 | 5.9225e-07 | 0.036923 | 0.036923 | 0.036923 | 1 | 0 | 0.99993 | -0.0004665 | 13.675
26 | 0.032254 | 0.0080927 | -0.032218 | -0.0080793 | 3.5573e-05 | 1.3364e-05 | 0.048247 | 0.048247 | 0.048247 | 0.99482 | -0.036125 | 0.99369 | -0.044082 | 17.8694
27 | -0.0046994 | -0.0011778 | 0.0047003 | 0.0011778 | 8.3429e-07 | -2.8665e-08 | 0.0070385 | 0.0070384 | 0.0070385 | 0.99351 | -0.045365 | 0.99369 | -0.044082 | 2.6069
28 | 0.027518 | 0.0069015 | -0.027482 | -0.0068881 | 3.6041e-05 | 1.3422e-05 | 0.041209 | 0.041209 | 0.041209 | 0.99369 | -0.044082 | 0.99234 | -0.053542 | 15.2627
29 | 0.017861 | 0.0044768 | -0.017856 | -0.0044753 | 4.3148e-06 | 1.535e-06 | 0.026782 | 0.026782 | 0.026782 | 0.99234 | -0.053542 | 0.9921 | -0.055287 | 9.9193
30 | 0.012343 | 0.0030934 | -0.01234 | -0.0030925 | 2.6099e-06 | 8.4623e-07 | 0.018512 | 0.018512 | 0.018512 | 0.9921 | -0.055287 | 0.99188 | -0.056815 | 6.8564
31 | 0.0034462 | 0.00086349 | -0.0034459 | -0.00086362 | 3.5086e-07 | -1.3654e-07 | 0.00517 | 0.0051701 | 0.0051701 | 0.99188 | -0.056815 | 0.99178 | -0.05755 | 1.9148
32 | 0.0088937 | 0.002229 | -0.008893 | -0.0022288 | 7.1893e-07 | 1.9298e-07 | 0.013342 | 0.013342 | 0.013342 | 0.99188 | -0.056815 | 0.9918 | -0.057399 | 4.9416
33 | 0.008893 | 0.0022288 | -0.0088903 | -0.0022281 | 2.6658e-06 | 7.1571e-07 | 0.013342 | 0.013342 | 0.013342 | 0.9918 | -0.057399 | 0.99149 | -0.059564 | 4.9416
34 | 0.0088903 | 0.0022281 | -0.0088899 | -0.002228 | 3.5443e-07 | 9.5171e-08 | 0.013342 | 0.013342 | 0.013342 | 0.99149 | -0.059564 | 0.99145 | -0.059852 | 4.9416
35 | 0.021009 | 0.0052689 | -0.021 | -0.0052653 | 9.8104e-06 | 3.5624e-06 | 0.031266 | 0.031266 | 0.031266 | 0.99993 | -0.0004665 | 0.99945 | -0.0038366 | 11.5799
36 | 0.0062949 | 0.0015774 | -0.0062921 | -0.0015769 | 2.8213e-06 | 4.1576e-07 | 0.0093891 | 0.0093893 | 0.0093893 | 0.99763 | -0.016617 | 0.99717 | -0.019856 | 3.4775
37 | -0.018652 | -0.0046761 | 0.018659 | 0.0046787 | 7.2757e-06 | 2.6004e-06 | 0.027781 | 0.027781 | 0.027781 | 0.99905 | -0.0066515 | 0.99945 | -0.0038366 | 10.2892
38 | 0.0052833 | 0.001324 | -0.0052826 | -0.0013239 | 7.4383e-07 | 4.6428e-08 | 0.0079688 | 0.0079688 | 0.0079688 | 0.98656 | -0.094233 | 0.98641 | -0.09525 | 2.9514
39 | -0.012514 | -0.0031363 | 0.012519 | 0.0031379 | 4.9588e-06 | 1.6223e-06 | 0.018875 | 0.018875 | 0.018875 | 0.98656 | -0.094233 | 0.98696 | -0.091371 | 6.9909

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.22148 | 0.055525

## res_load
| p_mw | q_mvar
0 | 0.016994 | 0.0042591
1 | 0.0013951 | 0.00034964
2 | 0.0026656 | 0.00066806
3 | 0.0044504 | 0.0011154
4 | 0.020091 | 0.0050354
5 | 0.011146 | 0.0027936
6 | 0.00235 | 0.00058896
7 | 0.0017479 | 0.00043806
8 | 0.020463 | 0.0051284
9 | 0.0026261 | 0.00065817
10 | 0.0011826 | 0.00029638
11 | 0.0045588 | 0.0011425
12 | 0.0085253 | 0.0021366
13 | 0.031846 | 0.0079814
14 | 0.023943 | 0.0060007
15 | 0.0046994 | 0.0011778
16 | 0.0096213 | 0.0024113
17 | 0.0055138 | 0.0013819
18 | 0.0034459 | 0.00086362
19 | 0.0038015 | 0.00095273
20 | 0.0088899 | 0.002228
21 | 0.0045947 | 0.0011515
22 | 0.0062921 | 0.0015769
23 | 0.0032913 | 0.00082489
24 | 0.0023407 | 0.00058663
25 | 0.0072311 | 0.0018123
26 | 0.0052826 | 0.0013239

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1