## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1511-9_2_2_node_513 | 0.4 | n |  | TRUE
1 | bus_LV_1511-9_2_2_node_110 | 0.4 | n |  | TRUE
2 | bus_LV_1511-9_2_2_node_515 | 0.4 | n |  | TRUE
3 | bus_LV_1511-9_2_2_node_34 | 0.4 | n |  | TRUE
4 | bus_LV_1511-9_2_2_node_514 | 0.4 | n |  | TRUE
5 | bus_LV_1511-9_2_2_node_516 | 0.4 | n |  | TRUE
6 | bus_LV_1511-9_2_2_node_517 | 0.4 | n |  | TRUE
7 | bus_LV_1511-9_2_2_node_518 | 0.4 | n |  | TRUE
8 | bus_LV_1511-9_2_2_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1511-9_2_2_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_1511-9_2_2_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_1511-9_2_2_node_18 | 0.4 | n |  | TRUE
12 | bus_LV_1511-9_2_2_node_519 | 0.4 | n |  | TRUE
13 | bus_LV_1511-9_2_2_node_66 | 0.4 | n |  | TRUE
14 | bus_LV_1511-9_2_2_node_520 | 0.4 | n |  | TRUE
15 | bus_LV_1511-9_2_2_node_521 | 0.4 | n |  | TRUE
16 | bus_LV_1511-9_2_2_node_522 | 0.4 | n |  | TRUE
17 | bus_LV_1511-9_2_2_node_523 | 0.4 | n |  | TRUE
18 | bus_LV_1511-9_2_2_node_524 | 0.4 | n |  | TRUE
19 | bus_LV_1511-9_2_2_node_525 | 0.4 | n |  | TRUE
20 | bus_LV_1511-9_2_2_node_526 | 0.4 | n |  | TRUE
21 | bus_LV_1511-9_2_2_node_23 | 0.4 | n |  | TRUE
22 | bus_LV_1511-9_2_2_node_21 | 0.4 | n |  | TRUE
23 | bus_LV_1511-9_2_2_node_22 | 0.4 | n |  | TRUE
24 | bus_LV_1511-9_2_2_node_287 | 0.4 | n |  | TRUE
25 | bus_LV_1511-9_2_2_node_61 | 0.4 | n |  | TRUE
26 | bus_LV_1511-9_2_2_node_62 | 0.4 | n |  | TRUE
27 | bus_LV_1511-9_2_2_node_63 | 0.4 | n |  | TRUE
28 | bus_LV_1511-9_2_2_node_64 | 0.4 | n |  | TRUE
29 | bus_LV_1511-9_2_2_node_241 | 0.4 | n |  | TRUE
30 | bus_LV_1511-9_2_2_node_65 | 0.4 | n |  | TRUE
31 | bus_LV_1511-9_2_2_node_70 | 0.4 | n |  | TRUE
32 | bus_LV_1511-9_2_2_node_289 | 0.4 | n |  | TRUE
33 | bus_LV_1511-9_2_2_node_69 | 0.4 | n |  | TRUE
34 | bus_LV_1511-9_2_2_node_159 | 0.4 | n |  | TRUE
35 | bus_LV_1511-9_2_2_node_157 | 0.4 | n |  | TRUE
36 | bus_LV_1511-9_2_2_node_154 | 0.4 | n |  | TRUE
37 | bus_LV_1511-9_2_2_node_102 | 0.4 | n |  | TRUE
38 | bus_LV_1511-9_2_2_node_103 | 0.4 | n |  | TRUE
39 | bus_LV_1511-9_2_2_node_104 | 0.4 | n |  | TRUE
40 | bus_LV_1511-9_2_2_node_105 | 0.4 | n |  | TRUE
41 | bus_LV_1511-9_2_2_node_106 | 0.4 | n |  | TRUE
42 | bus_LV_1511-9_2_2_node_107 | 0.4 | n |  | TRUE
43 | bus_LV_1511-9_2_2_node_108 | 0.4 | n |  | TRUE
44 | bus_LV_1511-9_2_2_node_109 | 0.4 | n |  | TRUE
45 | bus_LV_1511-9_2_2_node_111 | 0.4 | n |  | TRUE
46 | bus_LV_1511-9_2_2_node_112 | 0.4 | n |  | TRUE
47 | bus_LV_1511-9_2_2_node_266 | 0.4 | n |  | TRUE
48 | bus_LV_1511-9_2_2_node_204 | 0.4 | n |  | TRUE
49 | bus_LV_1511-9_2_2_node_160 | 0.4 | n |  | TRUE
50 | bus_LV_1511-9_2_2_node_244 | 0.4 | n |  | TRUE
51 | bus_LV_1511-9_2_2_node_161 | 0.4 | n |  | TRUE
52 | bus_LV_1511-9_2_2_node_162 | 0.4 | n |  | TRUE
53 | bus_LV_1511-9_2_2_node_163 | 0.4 | n |  | TRUE
54 | bus_LV_1511-9_2_2_node_249 | 0.4 | n |  | TRUE
55 | bus_LV_1511-9_2_2_node_200 | 0.4 | n |  | TRUE
56 | bus_LV_1511-9_2_2_node_201 | 0.4 | n |  | TRUE
57 | bus_LV_1511-9_2_2_node_205 | 0.4 | n |  | TRUE
58 | bus_LV_1511-9_2_2_node_239 | 0.4 | n |  | TRUE
59 | bus_LV_1511-9_2_2_node_240 | 0.4 | n |  | TRUE
60 | bus_LV_1511-9_2_2_node_246 | 0.4 | n |  | TRUE
61 | bus_LV_1511-9_2_2_node_242 | 0.4 | n |  | TRUE
62 | bus_LV_1511-9_2_2_node_245 | 0.4 | n |  | TRUE
63 | bus_LV_1511-9_2_2_node_248 | 0.4 | n |  | TRUE
64 | bus_LV_1511-9_2_2_node_250 | 0.4 | n |  | TRUE
65 | bus_LV_1511-9_2_2_node_252 | 0.4 | n |  | TRUE
66 | bus_LV_1511-9_2_2_node_253 | 0.4 | n |  | TRUE
67 | bus_LV_1511-9_2_2_node_276 | 0.4 | n |  | TRUE
68 | bus_LV_1511-9_2_2_node_256 | 0.4 | n |  | TRUE
69 | bus_LV_1511-9_2_2_node_254 | 0.4 | n |  | TRUE
70 | bus_LV_1511-9_2_2_node_255 | 0.4 | n |  | TRUE
71 | bus_LV_1511-9_2_2_node_257 | 0.4 | n |  | TRUE
72 | bus_LV_1511-9_2_2_node_258 | 0.4 | n |  | TRUE
73 | bus_LV_1511-9_2_2_node_259 | 0.4 | n |  | TRUE
74 | bus_LV_1511-9_2_2_node_268 | 0.4 | n |  | TRUE
75 | bus_LV_1511-9_2_2_node_267 | 0.4 | n |  | TRUE
76 | bus_LV_1511-9_2_2_node_264 | 0.4 | n |  | TRUE
77 | bus_LV_1511-9_2_2_node_260 | 0.4 | n |  | TRUE
78 | bus_LV_1511-9_2_2_node_261 | 0.4 | n |  | TRUE
79 | bus_LV_1511-9_2_2_node_262 | 0.4 | n |  | TRUE
80 | bus_LV_1511-9_2_2_node_263 | 0.4 | n |  | TRUE
81 | bus_LV_1511-9_2_2_node_269 | 0.4 | n |  | TRUE
82 | bus_LV_1511-9_2_2_node_270 | 0.4 | n |  | TRUE
83 | bus_LV_1511-9_2_2_node_265 | 0.4 | n |  | TRUE
84 | bus_LV_1511-9_2_2_node_278 | 0.4 | n |  | TRUE
85 | bus_LV_1511-9_2_2_node_271 | 0.4 | n |  | TRUE
86 | bus_LV_1511-9_2_2_node_272 | 0.4 | n |  | TRUE
87 | bus_LV_1511-9_2_2_node_274 | 0.4 | n |  | TRUE
88 | bus_LV_1511-9_2_2_node_275 | 0.4 | n |  | TRUE
89 | bus_LV_1511-9_2_2_node_279 | 0.4 | n |  | TRUE
90 | bus_LV_1511-9_2_2_node_277 | 0.4 | n |  | TRUE
91 | bus_LV_1511-9_2_2_node_280 | 0.4 | n |  | TRUE
92 | bus_LV_1511-9_2_2_node_281 | 0.4 | n |  | TRUE
93 | bus_LV_1511-9_2_2_node_282 | 0.4 | n |  | TRUE
94 | bus_LV_1511-9_2_2_node_283 | 0.4 | n |  | TRUE
95 | bus_LV_1511-9_2_2_node_284 | 0.4 | n |  | TRUE
96 | bus_LV_1511-9_2_2_node_285 | 0.4 | n |  | TRUE
97 | bus_LV_1511-9_2_2_node_286 | 0.4 | n |  | TRUE
98 | bus_LV_1511-9_2_2_node_288 | 0.4 | n |  | TRUE
99 | bus_MV_0_node_268 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1511-9_2_2_load_515 | 2 | 0.00037759 | 9.4634e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1511-9_2_2_load_34 | 3 | 0.0002599 | 6.5136e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1511-9_2_2_load_514 | 4 | 0.00010155 | 2.545e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1511-9_2_2_load_516 | 5 | 0.00021147 | 5.2999e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1511-9_2_2_load_517 | 6 | 0.00018584 | 4.6577e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1511-9_2_2_load_518 | 7 | 0.0004856 | 0.0001217 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1511-9_2_2_load_6 | 8 | 0.00012379 | 3.1024e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1511-9_2_2_load_8 | 9 | 0.00022022 | 5.5192e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1511-9_2_2_load_18 | 11 | 0.0004081 | 0.00010228 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1511-9_2_2_load_519 | 12 | 0.00026045 | 6.5276e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1511-9_2_2_load_520 | 14 | 0.00015816 | 3.9638e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1511-9_2_2_load_521 | 15 | 0.00011864 | 2.9733e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1511-9_2_2_load_522 | 16 | 0.00011075 | 2.7757e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1511-9_2_2_load_523 | 17 | 6.6416e-05 | 1.6645e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1511-9_2_2_load_524 | 18 | 0.00014805 | 3.7105e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1511-9_2_2_load_525 | 19 | 0.00033065 | 8.2868e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1511-9_2_2_load_526 | 20 | 0.00011758 | 2.9468e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1511-9_2_2_load_23 | 21 | 0.00022235 | 5.5725e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1511-9_2_2_load_21 | 22 | 0.00023415 | 5.8684e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1511-9_2_2_load_287 | 24 | 0.00029849 | 7.4808e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1511-9_2_2_load_61 | 25 | 0.00088664 | 0.00022221 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1511-9_2_2_load_64 | 28 | 7.5905e-05 | 1.9024e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1511-9_2_2_load_241 | 29 | 0.00038804 | 9.7253e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1511-9_2_2_load_65 | 30 | 0.00013738 | 3.443e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1511-9_2_2_load_289 | 32 | 0.00046686 | 0.00011701 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1511-9_2_2_load_69 | 33 | 0.00033841 | 8.4815e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1511-9_2_2_load_159 | 34 | 0.00014488 | 3.631e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1511-9_2_2_load_157 | 35 | 0.00029112 | 7.2962e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1511-9_2_2_load_154 | 36 | 0.00015006 | 3.7609e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1511-9_2_2_load_102 | 37 | 0.0007401 | 0.00018549 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1511-9_2_2_load_106 | 41 | 0.00010342 | 2.5919e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1511-9_2_2_load_107 | 42 | 0.00012881 | 3.2283e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1511-9_2_2_load_108 | 43 | 0.0001579 | 3.9572e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1511-9_2_2_load_111 | 45 | 0.00013625 | 3.4148e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1511-9_2_2_load_112 | 46 | 9.5515e-05 | 2.3938e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1511-9_2_2_load_266 | 47 | 8.454e-05 | 2.1188e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1511-9_2_2_load_244 | 50 | 0.00017363 | 4.3515e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1511-9_2_2_load_161 | 51 | 9.6009e-05 | 2.4062e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1511-9_2_2_load_163 | 53 | 7.2058e-05 | 1.8059e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1511-9_2_2_load_249 | 54 | 8.0789e-05 | 2.0248e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1511-9_2_2_load_200 | 55 | 0.00014843 | 3.72e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1511-9_2_2_load_205 | 57 | 0.00011869 | 2.9746e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1511-9_2_2_load_239 | 58 | 0.00018027 | 4.5179e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1511-9_2_2_load_246 | 60 | 0.00061746 | 0.00015475 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1511-9_2_2_load_242 | 61 | 9.2735e-05 | 2.3241e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1511-9_2_2_load_245 | 62 | 0.00016378 | 4.1047e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1511-9_2_2_load_248 | 63 | 0.00041609 | 0.00010428 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1511-9_2_2_load_250 | 64 | 0.00019717 | 4.9414e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1511-9_2_2_load_276 | 67 | 0.00041842 | 0.00010487 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1511-9_2_2_load_254 | 69 | 9.6864e-05 | 2.4276e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1511-9_2_2_load_255 | 70 | 0.0036611 | 0.00091756 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1511-9_2_2_load_259 | 73 | 0.0019916 | 0.00049913 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1511-9_2_2_load_268 | 74 | 0.0001818 | 4.5563e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1511-9_2_2_load_267 | 75 | 0.00083137 | 0.00020836 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1511-9_2_2_load_264 | 76 | 0.0014759 | 0.00036991 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1511-9_2_2_load_260 | 77 | 0.0035185 | 0.00088183 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1511-9_2_2_load_261 | 78 | 0.0011198 | 0.00028064 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1511-9_2_2_load_262 | 79 | 0.00069601 | 0.00017444 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1511-9_2_2_load_270 | 82 | 0.0002295 | 5.7518e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1511-9_2_2_load_278 | 84 | 0.00031861 | 7.9851e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1511-9_2_2_load_271 | 85 | 0.00029102 | 7.2936e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1511-9_2_2_load_272 | 86 | 0.00060922 | 0.00015268 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1511-9_2_2_load_274 | 87 | 0.00026973 | 6.7601e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1511-9_2_2_load_275 | 88 | 0.00084007 | 0.00021054 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1511-9_2_2_load_279 | 89 | 7.9908e-05 | 2.0027e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1511-9_2_2_load_277 | 90 | 0.00012304 | 3.0837e-05 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1511-9_2_2_load_280 | 91 | 0.00012437 | 3.117e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1511-9_2_2_load_282 | 93 | 0.00021337 | 5.3474e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1511-9_2_2_load_283 | 94 | 0.00015636 | 3.9187e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1511-9_2_2_load_284 | 95 | 0.00040862 | 0.00010241 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1511-9_2_2_load_285 | 96 | 0.00012945 | 3.2444e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 74 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1511-9_2_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.19313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1511-9_2_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.12737 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1511-9_2_2_line_2 | NAYY 4x150 SE | 0 | 3 | 0.14575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1511-9_2_2_line_3 | NAYY 4x150 SE | 1 | 4 | 0.018897 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1511-9_2_2_line_4 | NAYY 4x150 SE | 1 | 41 | 0.30064 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1511-9_2_2_line_5 | NAYY 4x150 SE | 4 | 5 | 0.06301 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1511-9_2_2_line_6 | NAYY 4x150 SE | 5 | 6 | 0.022802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1511-9_2_2_line_7 | NAYY 4x150 SE | 6 | 7 | 0.091569 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1511-9_2_2_line_8 | NAYY 4x150 SE | 8 | 9 | 0.016622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1511-9_2_2_line_9 | NAYY 4x150 SE | 9 | 10 | 0.22461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1511-9_2_2_line_10 | NAYY 4x150 SE | 10 | 11 | 0.10124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1511-9_2_2_line_11 | NAYY 4x150 SE | 11 | 21 | 0.094682 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1511-9_2_2_line_12 | NAYY 4x150 SE | 12 | 13 | 0.028521 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1511-9_2_2_line_13 | NAYY 4x150 SE | 12 | 14 | 0.035403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1511-9_2_2_line_14 | NAYY 4x150 SE | 13 | 32 | 0.15591 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1511-9_2_2_line_15 | NAYY 4x150 SE | 13 | 27 | 0.17477 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1511-9_2_2_line_16 | NAYY 4x150 SE | 14 | 15 | 0.043678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1511-9_2_2_line_17 | NAYY 4x150 SE | 15 | 16 | 0.077272 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1511-9_2_2_line_18 | NAYY 4x150 SE | 16 | 17 | 0.013918 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1511-9_2_2_line_19 | NAYY 4x150 SE | 17 | 18 | 0.0082021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1511-9_2_2_line_20 | NAYY 4x150 SE | 18 | 19 | 0.0014453 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1511-9_2_2_line_21 | NAYY 4x150 SE | 19 | 20 | 0.022626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1511-9_2_2_line_22 | NAYY 4x150 SE | 20 | 21 | 0.045527 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1511-9_2_2_line_23 | NAYY 4x150 SE | 22 | 23 | 0.093189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1511-9_2_2_line_24 | NAYY 4x150 SE | 23 | 24 | 0.11075 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1511-9_2_2_line_25 | NAYY 4x150 SE | 24 | 98 | 0.013701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1511-9_2_2_line_26 | NAYY 4x150 SE | 24 | 97 | 0.12185 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1511-9_2_2_line_27 | NAYY 4x150 SE | 25 | 26 | 0.04519 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1511-9_2_2_line_28 | NAYY 4x150 SE | 25 | 27 | 0.020959 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1511-9_2_2_line_29 | NAYY 4x150 SE | 26 | 28 | 0.05193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1511-9_2_2_line_30 | NAYY 4x150 SE | 26 | 29 | 0.4114 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1511-9_2_2_line_31 | NAYY 4x150 SE | 27 | 30 | 0.043776 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1511-9_2_2_line_32 | NAYY 4x150 SE | 28 | 31 | 0.1988 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1511-9_2_2_line_33 | NAYY 4x150 SE | 29 | 59 | 0.01393 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1511-9_2_2_line_34 | NAYY 4x150 SE | 31 | 35 | 0.11013 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1511-9_2_2_line_35 | NAYY 4x150 SE | 31 | 36 | 0.01386 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1511-9_2_2_line_36 | NAYY 4x150 SE | 32 | 98 | 0.017231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1511-9_2_2_line_37 | NAYY 4x150 SE | 33 | 34 | 0.012354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1511-9_2_2_line_38 | NAYY 4x150 SE | 34 | 49 | 0.0053292 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1511-9_2_2_line_39 | NAYY 4x150 SE | 34 | 50 | 0.40843 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1511-9_2_2_line_40 | NAYY 4x150 SE | 37 | 38 | 0.12188 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1511-9_2_2_line_41 | NAYY 4x150 SE | 37 | 39 | 0.013259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1511-9_2_2_line_42 | NAYY 4x150 SE | 38 | 40 | 0.21937 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1511-9_2_2_line_43 | NAYY 4x150 SE | 38 | 41 | 0.20382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1511-9_2_2_line_44 | NAYY 4x150 SE | 39 | 42 | 0.22043 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1511-9_2_2_line_45 | NAYY 4x150 SE | 39 | 43 | 0.035789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1511-9_2_2_line_46 | NAYY 4x150 SE | 40 | 44 | 0.031723 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1511-9_2_2_line_47 | NAYY 4x150 SE | 42 | 45 | 0.0028 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1511-9_2_2_line_48 | NAYY 4x150 SE | 43 | 46 | 0.0017464 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1511-9_2_2_line_49 | NAYY 4x150 SE | 44 | 47 | 0.30023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1511-9_2_2_line_50 | NAYY 4x150 SE | 45 | 48 | 0.74164 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1511-9_2_2_line_51 | NAYY 4x150 SE | 47 | 84 | 0.19912 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1511-9_2_2_line_52 | NAYY 4x150 SE | 47 | 83 | 0.20741 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1511-9_2_2_line_53 | NAYY 4x150 SE | 48 | 57 | 0.16713 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1511-9_2_2_line_54 | NAYY 4x150 SE | 49 | 51 | 0.089085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1511-9_2_2_line_55 | NAYY 4x150 SE | 50 | 61 | 0.0070467 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1511-9_2_2_line_56 | NAYY 4x150 SE | 51 | 52 | 0.019032 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1511-9_2_2_line_57 | NAYY 4x150 SE | 52 | 53 | 0.067943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1511-9_2_2_line_58 | NAYY 4x150 SE | 53 | 54 | 0.50673 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
59 | LV_1511-9_2_2_line_59 | NAYY 4x150 SE | 54 | 64 | 0.018386 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
60 | LV_1511-9_2_2_line_60 | NAYY 4x150 SE | 55 | 56 | 0.11738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1511-9_2_2_line_61 | NAYY 4x150 SE | 56 | 57 | 0.28194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1511-9_2_2_line_62 | NAYY 4x150 SE | 58 | 59 | 0.029864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1511-9_2_2_line_63 | NAYY 4x150 SE | 58 | 60 | 0.098476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1511-9_2_2_line_64 | NAYY 4x150 SE | 59 | 61 | 0.12344 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1511-9_2_2_line_65 | NAYY 4x150 SE | 60 | 62 | 0.0017181 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1511-9_2_2_line_66 | NAYY 4x150 SE | 62 | 63 | 0.19213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1511-9_2_2_line_67 | NAYY 4x150 SE | 64 | 65 | 0.015795 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
68 | LV_1511-9_2_2_line_68 | NAYY 4x150 SE | 65 | 66 | 0.045079 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
69 | LV_1511-9_2_2_line_69 | NAYY 4x150 SE | 66 | 67 | 0.035163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1511-9_2_2_line_70 | NAYY 4x150 SE | 66 | 68 | 0.29859 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
71 | LV_1511-9_2_2_line_71 | NAYY 4x150 SE | 68 | 69 | 0.065966 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
72 | LV_1511-9_2_2_line_72 | NAYY 4x150 SE | 69 | 70 | 0.14716 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
73 | LV_1511-9_2_2_line_73 | NAYY 4x150 SE | 70 | 71 | 0.01069 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
74 | LV_1511-9_2_2_line_74 | NAYY 4x150 SE | 71 | 72 | 0.098466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
75 | LV_1511-9_2_2_line_75 | NAYY 4x150 SE | 71 | 73 | 0.040439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1511-9_2_2_line_76 | NAYY 4x150 SE | 72 | 74 | 0.20259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
77 | LV_1511-9_2_2_line_77 | NAYY 4x150 SE | 72 | 75 | 0.071918 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1511-9_2_2_line_78 | NAYY 4x150 SE | 73 | 76 | 0.28979 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1511-9_2_2_line_79 | NAYY 4x150 SE | 76 | 83 | 0.31638 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1511-9_2_2_line_80 | NAYY 4x150 SE | 76 | 78 | 0.2162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1511-9_2_2_line_81 | NAYY 4x150 SE | 77 | 78 | 0.080095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1511-9_2_2_line_82 | NAYY 4x150 SE | 78 | 79 | 0.0065922 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1511-9_2_2_line_83 | NAYY 4x150 SE | 80 | 81 | 0.15977 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1511-9_2_2_line_84 | NAYY 4x150 SE | 80 | 82 | 0.24939 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1511-9_2_2_line_85 | NAYY 4x150 SE | 81 | 85 | 0.26468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1511-9_2_2_line_86 | NAYY 4x150 SE | 81 | 86 | 0.30132 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1511-9_2_2_line_87 | NAYY 4x150 SE | 82 | 87 | 0.16258 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1511-9_2_2_line_88 | NAYY 4x150 SE | 84 | 89 | 0.19719 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1511-9_2_2_line_89 | NAYY 4x150 SE | 86 | 88 | 0.26573 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1511-9_2_2_line_90 | NAYY 4x150 SE | 87 | 89 | 0.12517 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1511-9_2_2_line_91 | NAYY 4x150 SE | 87 | 90 | 0.18536 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1511-9_2_2_line_92 | NAYY 4x150 SE | 91 | 92 | 0.041897 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1511-9_2_2_line_93 | NAYY 4x150 SE | 91 | 93 | 0.032061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1511-9_2_2_line_94 | NAYY 4x150 SE | 92 | 94 | 0.009669 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1511-9_2_2_line_95 | NAYY 4x150 SE | 94 | 95 | 0.018386 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1511-9_2_2_line_96 | NAYY 4x150 SE | 95 | 96 | 0.0053633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1511-9_2_2_line_97 | NAYY 4x150 SE | 96 | 97 | 0.076193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1511-9_2_2_trafo_268 | 0.25 MVA 20/0.4 kV | 99 | 74 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24
0 | 2672760.0609 | 1192176.204 | 2672764.763 | 1192139.9951 | 2672763.8974 | 1192115.2587 | 2672756.9271 | 1192091.6153 | 2672744.5911 | 1192067.2175 | 2672742.5459 | 1192042.9337 | 2672745.0552 | 1192009.6109 | 2672748.88 | 1191987.8666
1 | 2672748.88 | 1191987.8666 | 2672817.5663 | 1191921.9179 | 2672822.1611 | 1191915.2365 | 2672823.2693 | 1191906.2446 | 2672825.6534 | 1191895.7784 | 2672828.2995 | 1191892.4616
2 | 2672748.88 | 1191987.8666 | 2672632.3525 | 1192075.4151
3 | 2672760.0609 | 1192176.204 | 2672757.9051 | 1192193.6104 | 2672758.2579 | 1192194.921
4 | 2672760.0609 | 1192176.204 | 2672766.1765 | 1192189.8754 | 2672819.3111 | 1192255.2162 | 2672831.449 | 1192283.3029 | 2672842.2705 | 1192305.5479 | 2672861.9576 | 1192322.1863 | 2672882.1233 | 1192330.8259 | 2672907.7684 | 1192329.6041 | 2672926.2299 | 1192321.0684 | 2672952.8186 | 1192304.9939 | 2672970.9453 | 1192293.7865
5 | 2672767.6859 | 1192254.8604 | 2672769.9638 | 1192252.0587 | 2672772.2126 | 1192245.1819 | 2672766.1912 | 1192224.3962 | 2672763.9374 | 1192216.0194 | 2672758.2579 | 1192194.921
6 | 2672767.6859 | 1192254.8604 | 2672766.8758 | 1192255.8567 | 2672765.645 | 1192261.7786 | 2672770.9354 | 1192273.7168 | 2672771.6254 | 1192276.0279
7 | 2672817.7846 | 1192347.4306 | 2672797.5188 | 1192332.6086 | 2672789.0713 | 1192325.1458 | 2672773.5332 | 1192304.5779 | 2672771.1481 | 1192298.2229 | 2672771.4997 | 1192290.6226 | 2672773.2941 | 1192281.6168 | 2672771.6254 | 1192276.0279
8 | 2672489.5048 | 1192285.7718 | 2672490.4256 | 1192290.7344 | 2672492.852 | 1192302.0522
9 | 2672515.0207 | 1192466.7042 | 2672518.6639 | 1192459.8442 | 2672532.1041 | 1192455.4266 | 2672547.758 | 1192458.307 | 2672559.004 | 1192456.2865 | 2672564.0598 | 1192451.7673 | 2672562.0858 | 1192436.6455 | 2672553.5593 | 1192425.6244 | 2672547.9755 | 1192417.7409 | 2672538.039 | 1192401.0327 | 2672536.9975 | 1192386.3335 | 2672532.2456 | 1192377.1038 | 2672525.2375 | 1192364.0777 | 2672512.4151 | 1192339.5299 | 2672503.9026 | 1192327.9643 | 2672497.4231 | 1192315.345 | 2672494.1345 | 1192308.0341 | 2672492.852 | 1192302.0522
10 | 2672515.0207 | 1192466.7042 | 2672523.3448 | 1192479.9574 | 2672525.1946 | 1192487.7178 | 2672524.3546 | 1192497.9026 | 2672520.5607 | 1192507.1288 | 2672503.9153 | 1192547.6959 | 2672499.3349 | 1192560.4694
11 | 2672467.6805 | 1192649.7016 | 2672475.1333 | 1192627.962 | 2672499.3349 | 1192560.4694
12 | 2672576.4225 | 1192882.3526 | 2672574.4223 | 1192879.46 | 2672555.1421 | 1192876.4911 | 2672550.7523 | 1192873.1826
13 | 2672550.7523 | 1192873.1826 | 2672548.2456 | 1192871.2933 | 2672544.61 | 1192867.4803 | 2672536.4117 | 1192852.7054 | 2672530.8482 | 1192844.2773
14 | 2672576.4225 | 1192882.3526 | 2672687.8513 | 1192773.3062
15 | 2672410.7797 | 1192925.1275 | 2672430.531 | 1192926.3228 | 2672436.5937 | 1192921.0708 | 2672540.3395 | 1192897.7911 | 2672574.1485 | 1192886.95 | 2672576.4225 | 1192882.3526
16 | 2672530.8482 | 1192844.2773 | 2672518.6414 | 1192825.7851 | 2672507.8675 | 1192807.1563
17 | 2672507.8675 | 1192807.1563 | 2672507.1283 | 1192805.8781 | 2672497.2523 | 1192785.4796 | 2672479.569 | 1192743.1735 | 2672476.8181 | 1192736.4346
18 | 2672476.8181 | 1192736.4346 | 2672471.5578 | 1192723.5486
19 | 2672468.458 | 1192715.9549 | 2672471.5578 | 1192723.5486
20 | 2672467.9117 | 1192714.6168 | 2672468.458 | 1192715.9549
21 | 2672467.9117 | 1192714.6168 | 2672461.2977 | 1192698.4144 | 2672459.807 | 1192693.5104
22 | 2672467.6805 | 1192649.7016 | 2672459.131 | 1192674.6406 | 2672457.9218 | 1192681.9637 | 2672458.8418 | 1192690.3354 | 2672459.807 | 1192693.5104
23 | 2672736.2484 | 1192642.9828 | 2672726.6296 | 1192643.4773 | 2672708.151 | 1192649.7677 | 2672673.3802 | 1192667.4894 | 2672664.5054 | 1192674.5191 | 2672656.7983 | 1192685.8324
24 | 2672736.2484 | 1192642.9828 | 2672734.4588 | 1192650.9769 | 2672730.9083 | 1192655.2141 | 2672713.4972 | 1192676.5375 | 2672708.0743 | 1192691.2027 | 2672701.2307 | 1192731.1879 | 2672697.8148 | 1192744.0396
25 | 2672693.6817 | 1192757.0895 | 2672696.238 | 1192749.9719 | 2672697.8148 | 1192744.0396
26 | 2672814.2024 | 1192780.1238 | 2672697.8148 | 1192744.0396
27 | 2672391.32 | 1192988.0186 | 2672396.892 | 1192971.0314 | 2672402.5496 | 1192960.1934 | 2672406.3162 | 1192945.5852
28 | 2672410.7797 | 1192925.1275 | 2672409.3081 | 1192933.9817 | 2672406.3162 | 1192945.5852
29 | 2672391.32 | 1192988.0186 | 2672371.0086 | 1192972.6527 | 2672350.2763 | 1192956.2103
30 | 2672391.32 | 1192988.0186 | 2672265.3771 | 1193379.6679
31 | 2672410.7797 | 1192925.1275 | 2672409.5053 | 1192917.6854 | 2672407.2169 | 1192912.1544 | 2672402.1683 | 1192907.3016 | 2672395.8826 | 1192902.645 | 2672389.3093 | 1192896.5507 | 2672384.8693 | 1192891.8053
32 | 2672254.0062 | 1192787.9175 | 2672266.541 | 1192804.7233 | 2672275.8823 | 1192825.2706 | 2672284.718 | 1192863.6892 | 2672290.4672 | 1192886.8947 | 2672297.6769 | 1192899.6228 | 2672320.8768 | 1192925.7854 | 2672347.5198 | 1192954.0242 | 2672350.2763 | 1192956.2103
33 | 2672265.8676 | 1193393.5898 | 2672265.3771 | 1193379.6679
34 | 2672254.0062 | 1192787.9175 | 2672260.0065 | 1192783.4095 | 2672262.3436 | 1192769.1514 | 2672262.5955 | 1192757.1361 | 2672266.1243 | 1192747.095 | 2672274.4066 | 1192732.8976 | 2672283.012 | 1192714.6795 | 2672291.4573 | 1192687.0094
35 | 2672254.0062 | 1192787.9175 | 2672248.047 | 1192788.3903 | 2672240.7811 | 1192785.3341
36 | 2672687.8513 | 1192773.3062 | 2672693.6817 | 1192757.0895
37 | 2672749.8404 | 1193527.9116 | 2672751.5157 | 1193540.1514
38 | 2672751.7379 | 1193522.9317 | 2672749.8404 | 1193527.9116 | 2672749.8404 | 1193527.9116
39 | 2672345.1308 | 1193472.9393 | 2672749.8404 | 1193527.9116
40 | 2673025.7694 | 1192167.5011 | 2673012.6387 | 1192146.4839 | 2672987.5285 | 1192120.0396 | 2672969.6974 | 1192086.2131 | 2672967.9787 | 1192074.6074 | 2672965.1842 | 1192064.3228
41 | 2672955.4903 | 1192055.277 | 2672965.1842 | 1192064.3228
42 | 2673025.7694 | 1192167.5011 | 2673039.4019 | 1192168.0233 | 2673071.1423 | 1192168.4109 | 2673097.9874 | 1192162.6352 | 2673117.1777 | 1192157.5332 | 2673150.1671 | 1192149.9317 | 2673179.7159 | 1192141.8991 | 2673198.5642 | 1192132.9798 | 2673208.3826 | 1192112.5099 | 2673217.025 | 1192101.5423 | 2673221.8957 | 1192099.7453
43 | 2673025.7694 | 1192167.5011 | 2673013.1106 | 1192182.1554 | 2673013.8518 | 1192193.26 | 2673019.4816 | 1192201.7115 | 2673033.1269 | 1192211.7951 | 2673049.8038 | 1192224.5841 | 2673057.689 | 1192236.8766 | 2673058.3487 | 1192245.2785 | 2673050.1703 | 1192256.9968 | 2673031.6945 | 1192266.6772 | 2673014.4271 | 1192271.0469 | 2672992.1248 | 1192280.6918 | 2672970.9453 | 1192293.7865
44 | 2672955.4903 | 1192055.277 | 2672967.1924 | 1192039.6881 | 2672971.6955 | 1192037.4083 | 2672976.3783 | 1192037.8879 | 2672983.1721 | 1192040.3166 | 2672988.2999 | 1192039.3118 | 2672991.3194 | 1192036.1579 | 2673047.6065 | 1191983.0905 | 2673082.9197 | 1191936.9828 | 2673098.1676 | 1191912.0319 | 2673099.988 | 1191902.5034
45 | 2672955.4903 | 1192055.277 | 2672923.781 | 1192038.6822
46 | 2673240.0072 | 1192124.8708 | 2673236.1356 | 1192121.6548 | 2673233.6307 | 1192117.644 | 2673230.3116 | 1192109.1538 | 2673226.0695 | 1192102.5647 | 2673221.8957 | 1192099.7453
47 | 2673100.5134 | 1191899.7532 | 2673099.988 | 1191902.5034
48 | 2672922.2337 | 1192037.8725 | 2672923.781 | 1192038.6822
49 | 2673240.0072 | 1192124.8708 | 2673241.7359 | 1192146.2047 | 2673240.6836 | 1192166.1482 | 2673235.9731 | 1192205.9255 | 2673237.699 | 1192233.0851 | 2673236.2348 | 1192243.7069 | 2673229.2298 | 1192251.7149 | 2673224.1611 | 1192255.9888 | 2673219.4624 | 1192264.2918 | 2673218.2381 | 1192275.8727 | 2673216.7042 | 1192290.9518 | 2673214.5928 | 1192308.9924 | 2673222.8846 | 1192338.4781 | 2673229.9797 | 1192352.9959 | 2673234.016 | 1192365.7862 | 2673235.8236 | 1192376.3035 | 2673238.6352 | 1192388.8788 | 2673242.6286 | 1192397.077 | 2673246.968 | 1192401.9219 | 2673254.5101 | 1192408.0272
50 | 2673100.5134 | 1191899.7532 | 2673547.5139 | 1191307.9629
51 | 2673254.5101 | 1192408.0272 | 2673393.8843 | 1192265.8229
52 | 2673313.7829 | 1192597.6017 | 2673304.0844 | 1192587.7992 | 2673298.3822 | 1192577.8457 | 2673293.6708 | 1192561.6894 | 2673289.4015 | 1192551.1419 | 2673275.7823 | 1192528.4504 | 2673272.7051 | 1192520.7637 | 2673271.8752 | 1192513.2157 | 2673278.5133 | 1192480.3773 | 2673277.8767 | 1192473.8433 | 2673273.5556 | 1192459.4263 | 2673269.7663 | 1192443.2813 | 2673264.5424 | 1192419.1585 | 2673261.0386 | 1192413.3121 | 2673254.5101 | 1192408.0272
53 | 2673547.5139 | 1191307.9629 | 2673539.9765 | 1191303.3342 | 2673532.6648 | 1191292.7381 | 2673527.2673 | 1191288.9473 | 2673524.1856 | 1191284.7069 | 2673520.4833 | 1191281.9487 | 2673518.4473 | 1191275.7533 | 2673511.8319 | 1191269.9241 | 2673508.2585 | 1191260.3968 | 2673500.2051 | 1191228.2453 | 2673489.8665 | 1191215.7665 | 2673484.9021 | 1191205.8774 | 2673485.6104 | 1191202.2173 | 2673481.1019 | 1191198.6709 | 2673478.9606 | 1191192.352 | 2673471.7095 | 1191176.1867 | 2673470.3958 | 1191167.1066
54 | 2672751.7379 | 1193522.9317 | 2672754.0176 | 1193520.369 | 2672759.7632 | 1193518.6044 | 2672765.5898 | 1193518.3196 | 2672772.0028 | 1193520.5878 | 2672775.0083 | 1193526.0276 | 2672777.2204 | 1193537.1612 | 2672779.9572 | 1193560.9198 | 2672786.4604 | 1193578.9431 | 2672790.8861 | 1193583.5199
55 | 2672345.1308 | 1193472.9393 | 2672338.9282 | 1193469.5949
56 | 2672806.0619 | 1193594.7688 | 2672795.5984 | 1193588.3932 | 2672790.8861 | 1193583.5199
57 | 2672806.0619 | 1193594.7688 | 2672815.916 | 1193596.7232 | 2672825.9223 | 1193597.4565 | 2672834.527 | 1193596.2382 | 2672842.937 | 1193593.4834 | 2672845.9325 | 1193590.9739 | 2672848.4435 | 1193586.3128 | 2672849.2962 | 1193583.2658 | 2672848.0311 | 1193578.2474 | 2672842.9889 | 1193574.2058 | 2672837.0048 | 1193571.7759
58 | 2673321.0884 | 1193421.9653 | 2672837.0048 | 1193571.7759
59 | 2673321.0884 | 1193421.9653 | 2673319.4964 | 1193416.9191 | 2673320.7186 | 1193403.8815
60 | 2673291.286 | 1191000.0811 | 2673281.4507 | 1191003.0958 | 2673265.9962 | 1191007.3092 | 2673255.8876 | 1191007.1076 | 2673240.1795 | 1191002.1347 | 2673234.5002 | 1191002.6433 | 2673222.2245 | 1191008.7968 | 2673211.8324 | 1191019.3093 | 2673188.4942 | 1191027.2065 | 2673183.5396 | 1191029.8807
61 | 2673291.286 | 1191000.0811 | 2673299.876 | 1191002.8657 | 2673321.9019 | 1191011.2293 | 2673342.4158 | 1191016.6616 | 2673350.034 | 1191015.3652 | 2673365.6073 | 1191014.5222 | 2673382.6197 | 1191023.1803 | 2673406.4414 | 1191040.5383 | 2673415.8273 | 1191053.0275 | 2673425.1306 | 1191070.9968 | 2673447.3702 | 1191088.6245 | 2673458.0654 | 1191107.4893 | 2673460.4754 | 1191120.4933 | 2673456.6832 | 1191137.468 | 2673451.7072 | 1191144.0442 | 2673453.5061 | 1191150.3034 | 2673463.6094 | 1191155.8862 | 2673466.8264 | 1191159.0498 | 2673470.1562 | 1191165.4501 | 2673470.3958 | 1191167.1066
62 | 2672265.8676 | 1193393.5898 | 2672266.2879 | 1193405.4797 | 2672268.1561 | 1193423.349
63 | 2672169.6974 | 1193421.5238 | 2672268.1561 | 1193423.349
64 | 2672265.8676 | 1193393.5898 | 2672287.9625 | 1193393.7233 | 2672290.0953 | 1193396.9955 | 2672290.6274 | 1193431.8005 | 2672291.8041 | 1193435.3391 | 2672310.4555 | 1193454.2424 | 2672338.9282 | 1193469.5949
65 | 2672169.6974 | 1193421.5238 | 2672168.1078 | 1193422.1756
66 | 2672168.1078 | 1193422.1756 | 2672053.5576 | 1193267.9325
67 | 2673316.2809 | 1193388.8517 | 2673320.8644 | 1193402.3271 | 2673320.7186 | 1193403.8815
68 | 2673318.1308 | 1193347.3828 | 2673310.7035 | 1193357.5979 | 2673309.3949 | 1193362.3737 | 2673311.0323 | 1193374.3009 | 2673316.2809 | 1193388.8517
69 | 2673318.1308 | 1193347.3828 | 2673322.7818 | 1193346.0167 | 2673331.4633 | 1193350.3924 | 2673335.8541 | 1193355.9495 | 2673337.3544 | 1193364.1395 | 2673333.0419 | 1193367.1107
70 | 2673281.2641 | 1193051.0755 | 2673318.1308 | 1193347.3828
71 | 2673281.2641 | 1193051.0755 | 2673243.2982 | 1193039.6817 | 2673233.9556 | 1193034.4754 | 2673228.4566 | 1193024.1464 | 2673229.4595 | 1193020.3462
72 | 2673229.4595 | 1193020.3462 | 2673230.7027 | 1193015.6354 | 2673232.1086 | 1193012.2506 | 2673236.4115 | 1193010.0797 | 2673252.4728 | 1193010.054 | 2673257.9273 | 1193008.4532 | 2673261.9451 | 1193005.2893 | 2673265.3506 | 1192992.3677 | 2673263.3652 | 1192972.7427 | 2673255.986 | 1192947.2593 | 2673251.1037 | 1192927.0208 | 2673247.2358 | 1192917.9458 | 2673240.2239 | 1192910.3888 | 2673238.89 | 1192904.1959
73 | 2673236.6391 | 1192893.746 | 2673238.89 | 1192904.1959
74 | 2673236.6391 | 1192893.746 | 2673229.3661 | 1192895.6804 | 2673225.7542 | 1192898.6936 | 2673224.5576 | 1192904.2823 | 2673226.0147 | 1192910.4149 | 2673229.525 | 1192924.4218 | 2673229.5287 | 1192940.9318 | 2673228.0816 | 1192950.7978 | 2673223.987 | 1192959.6085 | 2673218.6059 | 1192964.5456 | 2673212.1432 | 1192966.301 | 2673206.7457 | 1192965.112 | 2673203.7079 | 1192962.3176
75 | 2673236.6391 | 1192893.746 | 2673246.3977 | 1192879.9349 | 2673267.0077 | 1192868.5851
76 | 2673203.7079 | 1192962.3176 | 2673195.6179 | 1192964.3755 | 2673166.1972 | 1192961.0137 | 2673132.9106 | 1192954.0138 | 2673124.8724 | 1192947.4672 | 2673119.4917 | 1192932.4258 | 2673114.9077 | 1192913.9365 | 2673114.9311 | 1192899.5504 | 2673122.1485 | 1192887.1978 | 2673167.6693 | 1192853.1337
77 | 2673203.7079 | 1192962.3176 | 2673203.3513 | 1192958.4443 | 2673206.7706 | 1192946.2566 | 2673208.1803 | 1192939.4475 | 2673206.8136 | 1192934.0275 | 2673202.0743 | 1192928.8776 | 2673190.906 | 1192922.7262 | 2673185.6222 | 1192919.7042 | 2673181.0837 | 1192914.9681 | 2673179.5224 | 1192908.623 | 2673179.5701 | 1192904.7268
78 | 2673459.5094 | 1192673.3959 | 2673457.2515 | 1192677.0417 | 2673456.3838 | 1192685.6251 | 2673442.4992 | 1192713.8049 | 2673437.8118 | 1192722.4415 | 2673428.8076 | 1192726.9004 | 2673412.9312 | 1192731.0526 | 2673399.7287 | 1192740.9521 | 2673388.3454 | 1192752.9308 | 2673385.7019 | 1192762.7377 | 2673382.6076 | 1192771.3827 | 2673377.759 | 1192774.5251 | 2673371.7686 | 1192776.2861 | 2673365.5321 | 1192780.0897 | 2673355.9613 | 1192793.4693 | 2673348.292 | 1192801.6024 | 2673331.6298 | 1192813.2941 | 2673327.4259 | 1192819.1906 | 2673312.2292 | 1192842.5518 | 2673308.2701 | 1192847.762 | 2673301.8253 | 1192849.284 | 2673279.9535 | 1192855.6533 | 2673275.0582 | 1192861.9972 | 2673268.3394 | 1192867.8518 | 2673267.0077 | 1192868.5851
79 | 2673313.7829 | 1192597.6017 | 2673327.9907 | 1192585.9354 | 2673350.7589 | 1192563.1229 | 2673362.3235 | 1192555.0265 | 2673374.966 | 1192552.9024 | 2673398.8401 | 1192551.8166 | 2673436.2377 | 1192551.364 | 2673461.6365 | 1192556.4787 | 2673477.8547 | 1192562.3924 | 2673489.6821 | 1192570.776 | 2673498.0588 | 1192579.5619 | 2673502.069 | 1192589.4504 | 2673501.2594 | 1192599.5021 | 2673492.9871 | 1192618.8343 | 2673487.1931 | 1192635.6177 | 2673485.4941 | 1192639.2657 | 2673477.3891 | 1192656.1541 | 2673468.565 | 1192665.1845 | 2673463.1078 | 1192667.5857 | 2673459.5094 | 1192673.3959
80 | 2673459.5094 | 1192673.3959 | 2673575.1665 | 1192856.0642
81 | 2673584.2621 | 1192931.1671 | 2673581.3324 | 1192913.152 | 2673571.862 | 1192893.5572 | 2673570.1573 | 1192887.7549 | 2673570.3402 | 1192882.7987 | 2673574.1285 | 1192873.5174 | 2673573.1124 | 1192869.3691 | 2673571.4091 | 1192863.4446 | 2673571.8003 | 1192860.1475 | 2673575.1665 | 1192856.0642 | 2673575.1665 | 1192856.0642
82 | 2673575.1665 | 1192856.0642 | 2673581.5033 | 1192854.2471
83 | 2673796.7184 | 1192642.808 | 2673823.3843 | 1192650.8306 | 2673845.8321 | 1192630.6398 | 2673887.7049 | 1192617.1596 | 2673922.3444 | 1192620.8784 | 2673941.1207 | 1192623.3118 | 2673944.7265 | 1192625.7689
84 | 2673796.7184 | 1192642.808 | 2673797.1489 | 1192607.9146 | 2673806.8021 | 1192576.2257 | 2673800.8815 | 1192555.6181 | 2673758.4437 | 1192530.202 | 2673735.5635 | 1192519.2913 | 2673720.0383 | 1192515.9202 | 2673717.7376 | 1192512.7011 | 2673722.746 | 1192504.0465 | 2673734.8158 | 1192493.3665 | 2673743.5313 | 1192477.7423 | 2673744.6468 | 1192456.5099 | 2673744.6468 | 1192456.5099
85 | 2673944.7265 | 1192625.7689 | 2673946.4061 | 1192620.0196 | 2673953.0139 | 1192604.7253 | 2673955.0173 | 1192596.2116 | 2673954.883 | 1192587.3491 | 2673955.6926 | 1192576.7416 | 2673961.7214 | 1192568.1999 | 2673961.7509 | 1192558.4166 | 2673967.7374 | 1192535.4212 | 2673979.3037 | 1192515.5522 | 2673990.8355 | 1192504.0322 | 2674001.5455 | 1192491.7684 | 2674013.2174 | 1192473.2349 | 2674026.7454 | 1192450.722 | 2674039.4023 | 1192416.6803 | 2674056.3767 | 1192392.2867
86 | 2673944.7265 | 1192625.7689 | 2673937.8067 | 1192630.5419 | 2673927.0151 | 1192663.0059 | 2673929.7235 | 1192689.9666 | 2673918.3604 | 1192706.3917 | 2673914.9018 | 1192724.093 | 2673917.4265 | 1192749.2726 | 2673911.3819 | 1192762.8061 | 2673905.0281 | 1192768.053 | 2673901.8482 | 1192779.2538 | 2673897.0575 | 1192787.5552 | 2673891.6899 | 1192791.3357 | 2673882.8753 | 1192798.3311 | 2673875.7806 | 1192814.809 | 2673859.9665 | 1192830.5788 | 2673852.295 | 1192844.3925 | 2673846.0034 | 1192844.615 | 2673833.3108 | 1192853.9195 | 2673824.7646 | 1192880.6633
87 | 2673609.1421 | 1192390.7803 | 2673609.1421 | 1192390.7803 | 2673613.8959 | 1192389.1823 | 2673618.0089 | 1192391.9568 | 2673622.0975 | 1192396.721 | 2673633.1882 | 1192399.926 | 2673643.4307 | 1192404.5437 | 2673647.3656 | 1192412.4969 | 2673651.6172 | 1192422.5886 | 2673655.3037 | 1192430.8945 | 2673662.4598 | 1192436.6527 | 2673677.4723 | 1192438.9611 | 2673736.8285 | 1192450.6768 | 2673744.6468 | 1192456.5099
88 | 2673393.8843 | 1192265.8229 | 2673401.0728 | 1192267.9516 | 2673408.1505 | 1192272.0631 | 2673412.3279 | 1192284.5107 | 2673417.9627 | 1192296.8538 | 2673419.7942 | 1192315.3429 | 2673427.0509 | 1192326.5943 | 2673429.2533 | 1192337.8391 | 2673433.4131 | 1192351.0981 | 2673440.5465 | 1192364.9384 | 2673450.2764 | 1192377.7877 | 2673477.997 | 1192406.8231 | 2673479.9907 | 1192415.8085 | 2673484.7721 | 1192419.4027 | 2673489.6318 | 1192420.3518 | 2673495.0255 | 1192419.1712
89 | 2673695.2254 | 1193109.5909 | 2673701.9634 | 1193104.9071 | 2673721.9269 | 1193070.2655 | 2673735.6274 | 1193044.6966 | 2673741.627 | 1193029.1946 | 2673745.8903 | 1193018.4962 | 2673763.1201 | 1192986.7673 | 2673794.2321 | 1192946.9157 | 2673798.5207 | 1192928.6243 | 2673809.75 | 1192905.6934 | 2673822.7651 | 1192886.9204 | 2673824.7646 | 1192880.6633
90 | 2673495.0255 | 1192419.1712 | 2673517.67 | 1192414.2147 | 2673532.0522 | 1192410.1333 | 2673538.2584 | 1192405.7292 | 2673545.39 | 1192403.571 | 2673553.1901 | 1192405.3235 | 2673562.5887 | 1192410.9868 | 2673569.4608 | 1192410.7156 | 2673583.582 | 1192408.6435 | 2673595.476 | 1192404.187 | 2673604.3448 | 1192395.9133 | 2673609.1421 | 1192390.7803
91 | 2673609.1421 | 1192390.7803 | 2673571.5083 | 1192209.2855
92 | 2672846.7573 | 1192803.5006 | 2672851.5583 | 1192804.871 | 2672854.4228 | 1192808.1412 | 2672854.8691 | 1192813.4275 | 2672854.951 | 1192821.0998 | 2672850.8916 | 1192831.4455 | 2672846.6058 | 1192838.7459
93 | 2672831.1368 | 1192866.8263 | 2672844.4306 | 1192842.4512 | 2672846.6058 | 1192838.7459
94 | 2672846.7573 | 1192803.5006 | 2672837.3169 | 1192805.5911
95 | 2672825.1654 | 1192817.3856 | 2672827.5461 | 1192810.5044 | 2672833.7174 | 1192806.3881 | 2672837.3169 | 1192805.5911
96 | 2672825.1654 | 1192817.3856 | 2672824.5201 | 1192819.2506 | 2672823.5485 | 1192822.4982
97 | 2672814.2024 | 1192780.1238 | 2672811.7051 | 1192792.4008 | 2672809.1418 | 1192814.4828 | 2672808.9702 | 1192828.5781 | 2672809.5455 | 1192833.299 | 2672815.5278 | 1192835.3063 | 2672820.0041 | 1192833.2929 | 2672822.3031 | 1192826.6614 | 2672823.5485 | 1192822.4982

## bus_geodata
| x | y | coords
0 | 2672748.88 | 1191987.8666
1 | 2672760.0609 | 1192176.204
2 | 2672828.2995 | 1191892.4616
3 | 2672632.3525 | 1192075.4151
4 | 2672758.2579 | 1192194.921
5 | 2672767.6859 | 1192254.8604
6 | 2672771.6254 | 1192276.0279
7 | 2672817.7846 | 1192347.4306
8 | 2672489.5048 | 1192285.7718
9 | 2672492.852 | 1192302.0522
10 | 2672515.0207 | 1192466.7042
11 | 2672499.3349 | 1192560.4694
12 | 2672550.7523 | 1192873.1826
13 | 2672576.4225 | 1192882.3526
14 | 2672530.8482 | 1192844.2773
15 | 2672507.8675 | 1192807.1563
16 | 2672476.8181 | 1192736.4346
17 | 2672471.5578 | 1192723.5486
18 | 2672468.458 | 1192715.9549
19 | 2672467.9117 | 1192714.6168
20 | 2672459.807 | 1192693.5104
21 | 2672467.6805 | 1192649.7016
22 | 2672656.7983 | 1192685.8324
23 | 2672736.2484 | 1192642.9828
24 | 2672697.8148 | 1192744.0396
25 | 2672406.3162 | 1192945.5852
26 | 2672391.32 | 1192988.0186
27 | 2672410.7797 | 1192925.1275
28 | 2672350.2763 | 1192956.2103
29 | 2672265.3771 | 1193379.6679
30 | 2672384.8693 | 1192891.8053
31 | 2672254.0062 | 1192787.9175
32 | 2672687.8513 | 1192773.3062
33 | 2672751.5157 | 1193540.1514
34 | 2672749.8404 | 1193527.9116
35 | 2672291.4573 | 1192687.0094
36 | 2672240.7811 | 1192785.3341
37 | 2672965.1842 | 1192064.3228
38 | 2673025.7694 | 1192167.5011
39 | 2672955.4903 | 1192055.277
40 | 2673221.8957 | 1192099.7453
41 | 2672970.9453 | 1192293.7865
42 | 2673099.988 | 1191902.5034
43 | 2672923.781 | 1192038.6822
44 | 2673240.0072 | 1192124.8708
45 | 2673100.5134 | 1191899.7532
46 | 2672922.2337 | 1192037.8725
47 | 2673254.5101 | 1192408.0272
48 | 2673547.5139 | 1191307.9629
49 | 2672751.7379 | 1193522.9317
50 | 2672345.1308 | 1193472.9393
51 | 2672790.8861 | 1193583.5199
52 | 2672806.0619 | 1193594.7688
53 | 2672837.0048 | 1193571.7759
54 | 2673321.0884 | 1193421.9653
55 | 2673183.5396 | 1191029.8807
56 | 2673291.286 | 1191000.0811
57 | 2673470.3958 | 1191167.1066
58 | 2672268.1561 | 1193423.349
59 | 2672265.8676 | 1193393.5898
60 | 2672169.6974 | 1193421.5238
61 | 2672338.9282 | 1193469.5949
62 | 2672168.1078 | 1193422.1756
63 | 2672053.5576 | 1193267.9325
64 | 2673320.7186 | 1193403.8815
65 | 2673316.2809 | 1193388.8517
66 | 2673318.1308 | 1193347.3828
67 | 2673333.0419 | 1193367.1107
68 | 2673281.2641 | 1193051.0755
69 | 2673229.4595 | 1193020.3462
70 | 2673238.89 | 1192904.1959
71 | 2673236.6391 | 1192893.746
72 | 2673203.7079 | 1192962.3176
73 | 2673267.0077 | 1192868.5851
74 | 2673167.6693 | 1192853.1337
75 | 2673179.5701 | 1192904.7268
76 | 2673459.5094 | 1192673.3959
77 | 2673584.2621 | 1192931.1671
78 | 2673575.1665 | 1192856.0642
79 | 2673581.5033 | 1192854.2471
80 | 2673796.7184 | 1192642.808
81 | 2673944.7265 | 1192625.7689
82 | 2673744.6468 | 1192456.5099
83 | 2673313.7829 | 1192597.6017
84 | 2673393.8843 | 1192265.8229
85 | 2674056.3767 | 1192392.2867
86 | 2673824.7646 | 1192880.6633
87 | 2673609.1421 | 1192390.7803
88 | 2673695.2254 | 1193109.5909
89 | 2673495.0255 | 1192419.1712
90 | 2673571.5083 | 1192209.2855
91 | 2672846.6058 | 1192838.7458
92 | 2672846.7573 | 1192803.5006
93 | 2672831.1368 | 1192866.8263
94 | 2672837.3169 | 1192805.5911
95 | 2672825.1654 | 1192817.3856
96 | 2672823.5485 | 1192822.4982
97 | 2672814.2024 | 1192780.1238
98 | 2672693.6817 | 1192757.0895
99 | 2673167.6693 | 1192853.1337

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9789 | -0.15763 | 0 | 0
1 | 0.97907 | -0.15628 | 0 | 0
2 | 0.97883 | -0.15814 | 0.00037759 | 9.4634e-05
3 | 0.97884 | -0.15803 | 0.0002599 | 6.5136e-05
4 | 0.97905 | -0.15647 | 0.00010155 | 2.545e-05
5 | 0.97897 | -0.15706 | 0.00021147 | 5.2999e-05
6 | 0.97894 | -0.15722 | 0.00018584 | 4.6577e-05
7 | 0.97888 | -0.15769 | 0.0004856 | 0.0001217
8 | 0.972 | -0.20531 | 0.00012379 | 3.1024e-05
9 | 0.972 | -0.20529 | 0.00022022 | 5.5192e-05
10 | 0.97212 | -0.20445 | 0 | 0
11 | 0.97217 | -0.20405 | 0.0004081 | 0.00010228
12 | 0.97285 | -0.19896 | 0.00026045 | 6.5276e-05
13 | 0.97294 | -0.19825 | 0 | 0
14 | 0.97274 | -0.19974 | 0.00015816 | 3.9638e-05
15 | 0.97263 | -0.20062 | 0.00011864 | 2.9733e-05
16 | 0.97243 | -0.20209 | 0.00011075 | 2.7757e-05
17 | 0.97239 | -0.20234 | 6.6416e-05 | 1.6645e-05
18 | 0.97238 | -0.20248 | 0.00014805 | 3.7105e-05
19 | 0.97237 | -0.2025 | 0.00033065 | 8.2868e-05
20 | 0.97234 | -0.20277 | 0.00011758 | 2.9468e-05
21 | 0.97227 | -0.20326 | 0.00022235 | 5.5725e-05
22 | 0.97234 | -0.20274 | 0.00023415 | 5.8684e-05
23 | 0.97237 | -0.2025 | 0 | 0
24 | 0.97241 | -0.20221 | 0.00029849 | 7.4808e-05
25 | 0.97419 | -0.18903 | 0.00088664 | 0.00022221
26 | 0.97454 | -0.18642 | 0 | 0
27 | 0.97405 | -0.19005 | 0 | 0
28 | 0.9745 | -0.18672 | 7.5905e-05 | 1.9024e-05
29 | 0.97806 | -0.16028 | 0.00038804 | 9.7253e-05
30 | 0.97404 | -0.19011 | 0.00013738 | 3.443e-05
31 | 0.97437 | -0.18769 | 0 | 0
32 | 0.97248 | -0.20169 | 0.00046686 | 0.00011701
33 | 0.98435 | -0.11406 | 0.00033841 | 8.4815e-05
34 | 0.98435 | -0.11402 | 0.00014488 | 3.631e-05
35 | 0.97432 | -0.18803 | 0.00029112 | 7.2962e-05
36 | 0.97437 | -0.18771 | 0.00015006 | 3.7609e-05
37 | 0.98002 | -0.14922 | 0.0007401 | 0.00018549
38 | 0.98029 | -0.1471 | 0 | 0
39 | 0.98001 | -0.14935 | 0 | 0
40 | 0.98133 | -0.13906 | 0 | 0
41 | 0.97978 | -0.15096 | 0.00010342 | 2.5919e-05
42 | 0.97984 | -0.15088 | 0.00012881 | 3.2283e-05
43 | 0.98 | -0.14945 | 0.0001579 | 3.9572e-05
44 | 0.98148 | -0.1379 | 0 | 0
45 | 0.97984 | -0.15089 | 0.00013625 | 3.4148e-05
46 | 0.98 | -0.14945 | 9.5515e-05 | 2.3938e-05
47 | 0.98289 | -0.12684 | 8.454e-05 | 2.1188e-05
48 | 0.97956 | -0.15363 | 0 | 0
49 | 0.98442 | -0.11354 | 0 | 0
50 | 0.97965 | -0.14861 | 0.00017363 | 4.3515e-05
51 | 0.98551 | -0.10558 | 9.6009e-05 | 2.4062e-05
52 | 0.98574 | -0.10386 | 0 | 0
53 | 0.98658 | -0.097723 | 7.2058e-05 | 1.8059e-05
54 | 0.98974 | -0.074622 | 8.0789e-05 | 2.0248e-05
55 | 0.9794 | -0.15487 | 0.00014843 | 3.72e-05
56 | 0.97943 | -0.15468 | 0 | 0
57 | 0.97949 | -0.15418 | 0.00011869 | 2.9746e-05
58 | 0.97813 | -0.15978 | 0.00018027 | 4.5179e-05
59 | 0.97819 | -0.15934 | 0 | 0
60 | 0.97796 | -0.16103 | 0.00061746 | 0.00015475
61 | 0.97957 | -0.14919 | 9.2735e-05 | 2.3241e-05
62 | 0.97796 | -0.16104 | 0.00016378 | 4.1047e-05
63 | 0.97784 | -0.16189 | 0.00041609 | 0.00010428
64 | 0.98986 | -0.073775 | 0.00019717 | 4.9414e-05
65 | 0.98996 | -0.07303 | 0 | 0
66 | 0.99025 | -0.070906 | 0 | 0
67 | 0.99023 | -0.071056 | 0.00041842 | 0.00010487
68 | 0.99226 | -0.056177 | 0 | 0
69 | 0.9927 | -0.05292 | 9.6864e-05 | 2.4276e-05
70 | 0.9937 | -0.045575 | 0.0036611 | 0.00091756
71 | 0.9938 | -0.044844 | 0 | 0
72 | 0.99579 | -0.030405 | 0 | 0
73 | 0.99293 | -0.051195 | 0.0019916 | 0.00049913
74 | 1 | 0 | -0.030002 | -0.0072159
75 | 0.9957 | -0.031009 | 0.00083137 | 0.00020836
76 | 0.98752 | -0.091073 | 0.0014759 | 0.00036991
77 | 0.98544 | -0.10584 | 0.0035185 | 0.00088183
78 | 0.98585 | -0.10294 | 0.0011198 | 0.00028064
79 | 0.98584 | -0.10298 | 0.00069601 | 0.00017444
80 | 0.97987 | -0.14983 | 0 | 0
81 | 0.97947 | -0.15287 | 0 | 0
82 | 0.9805 | -0.14505 | 0.0002295 | 5.7518e-05
83 | 0.98472 | -0.11267 | 0 | 0
84 | 0.98209 | -0.13292 | 0.00031861 | 7.9851e-05
85 | 0.97935 | -0.1537 | 0.00029102 | 7.2936e-05
86 | 0.97883 | -0.15753 | 0.00060922 | 0.00015268
87 | 0.98097 | -0.14152 | 0.00026973 | 6.7601e-05
88 | 0.97851 | -0.15989 | 0.00084007 | 0.00021054
89 | 0.98139 | -0.13825 | 7.9908e-05 | 2.0027e-05
90 | 0.98093 | -0.14177 | 0.00012304 | 3.0837e-05
91 | 0.97206 | -0.20475 | 0.00012437 | 3.117e-05
92 | 0.97209 | -0.20459 | 0 | 0
93 | 0.97205 | -0.20482 | 0.00021337 | 5.3474e-05
94 | 0.97209 | -0.20456 | 0.00015636 | 3.9187e-05
95 | 0.9721 | -0.20446 | 0.00040862 | 0.00010241
96 | 0.97211 | -0.20441 | 0.00012945 | 3.2444e-05
97 | 0.97223 | -0.20357 | 0 | 0
98 | 0.97244 | -0.20198 | 0 | 0
99 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00063753 | -0.00015635 | 0.00063764 | 0.00015397 | 1.128e-07 | -2.385e-06 | 0.00096789 | 0.00096705 | 0.00096789 | 0.9789 | -0.15763 | 0.97907 | -0.15628 | 0.35848
1 | 0.00037762 | 9.3043e-05 | -0.00037759 | -9.4634e-05 | 2.6162e-08 | -1.591e-06 | 0.00057345 | 0.00057402 | 0.00057402 | 0.9789 | -0.15763 | 0.97883 | -0.15814 | 0.2126
2 | 0.00025991 | 6.3309e-05 | -0.0002599 | -6.5136e-05 | 1.4173e-08 | -1.8267e-06 | 0.00039444 | 0.00039509 | 0.00039509 | 0.9789 | -0.15763 | 0.97884 | -0.15803 | 0.14633
3 | 0.0009846 | 0.00024432 | -0.00098458 | -0.00024454 | 2.6375e-08 | -2.2749e-07 | 0.0014955 | 0.0014956 | 0.0014956 | 0.97907 | -0.15628 | 0.97905 | -0.15647 | 0.55394
4 | -0.0016222 | -0.00039828 | 0.0016234 | 0.00039494 | 1.137e-06 | -3.3463e-06 | 0.0024626 | 0.0024613 | 0.0024626 | 0.97907 | -0.15628 | 0.97978 | -0.15096 | 0.91207
5 | 0.00088303 | 0.00021909 | -0.00088296 | -0.00021986 | 7.0751e-08 | -7.651e-07 | 0.0013413 | 0.0013416 | 0.0013416 | 0.97905 | -0.15647 | 0.97897 | -0.15706 | 0.49688
6 | 0.00067149 | 0.00016686 | -0.00067148 | -0.00016714 | 1.4809e-08 | -2.81e-07 | 0.0010201 | 0.0010202 | 0.0010202 | 0.97897 | -0.15706 | 0.97894 | -0.15722 | 0.37787
7 | 0.00048563 | 0.00012056 | -0.0004856 | -0.0001217 | 3.1117e-08 | -1.1392e-06 | 0.00073776 | 0.00073817 | 0.00073817 | 0.97894 | -0.15722 | 0.97888 | -0.15769 | 0.2734
8 | -0.00012379 | -3.1024e-05 | 0.00012379 | 3.0819e-05 | 3.7235e-10 | -2.0589e-07 | 0.00018951 | 0.00018943 | 0.00018951 | 0.972 | -0.20531 | 0.972 | -0.20529 | 0.070187
9 | -0.00034401 | -8.6011e-05 | 0.00034405 | 8.3241e-05 | 3.8787e-08 | -2.7694e-06 | 0.00052656 | 0.00052557 | 0.00052656 | 0.972 | -0.20529 | 0.97212 | -0.20445 | 0.19502
10 | -0.00034405 | -8.3241e-05 | 0.00034406 | 8.1993e-05 | 1.7436e-08 | -1.2486e-06 | 0.00052557 | 0.00052514 | 0.00052557 | 0.97212 | -0.20445 | 0.97217 | -0.20405 | 0.19466
11 | -0.00075217 | -0.00018427 | 0.00075225 | 0.00018313 | 7.8076e-08 | -1.1441e-06 | 0.0011498 | 0.0011494 | 0.0011498 | 0.97217 | -0.20405 | 0.97227 | -0.20326 | 0.42584
12 | -0.0022863 | -0.00056464 | 0.0022865 | 0.00056437 | 2.1725e-07 | -2.7061e-07 | 0.0034939 | 0.0034938 | 0.0034939 | 0.97285 | -0.19896 | 0.97294 | -0.19825 | 1.2941
13 | 0.0020258 | 0.00049936 | -0.0020256 | -0.00049972 | 2.117e-07 | -3.5811e-07 | 0.0030956 | 0.0030957 | 0.0030957 | 0.97285 | -0.19896 | 0.97274 | -0.19974 | 1.1466
14 | 0.0020331 | 0.00050109 | -0.0020321 | -0.00050266 | 9.3896e-07 | -1.5742e-06 | 0.0031063 | 0.003107 | 0.003107 | 0.97294 | -0.19825 | 0.97248 | -0.20169 | 1.1507
15 | -0.0043195 | -0.0010655 | 0.0043243 | 0.0010651 | 4.7501e-06 | -3.4595e-07 | 0.0066001 | 0.0065994 | 0.0066001 | 0.97294 | -0.19825 | 0.97405 | -0.19005 | 2.4445
16 | 0.0018674 | 0.00046008 | -0.0018672 | -0.00046054 | 2.2198e-07 | -4.5677e-07 | 0.0028538 | 0.002854 | 0.002854 | 0.97274 | -0.19974 | 0.97263 | -0.20062 | 1.057
17 | 0.0017486 | 0.00043081 | -0.0017482 | -0.00043163 | 3.4442e-07 | -8.2635e-07 | 0.0026725 | 0.0026728 | 0.0026728 | 0.97263 | -0.20062 | 0.97243 | -0.20209 | 0.98993
18 | 0.0016375 | 0.00040388 | -0.0016374 | -0.00040403 | 5.4428e-08 | -1.5173e-07 | 0.0025033 | 0.0025034 | 0.0025034 | 0.97243 | -0.20209 | 0.97239 | -0.20234 | 0.92719
19 | 0.001571 | 0.00038738 | -0.001571 | -0.00038747 | 2.9524e-08 | -9.0389e-08 | 0.0024018 | 0.0024018 | 0.0024018 | 0.97239 | -0.20234 | 0.97238 | -0.20248 | 0.88956
20 | 0.0014229 | 0.00035037 | -0.0014229 | -0.00035038 | 4.2673e-09 | -1.6287e-08 | 0.0021753 | 0.0021753 | 0.0021753 | 0.97238 | -0.20248 | 0.97237 | -0.2025 | 0.80565
21 | 0.0010923 | 0.00026752 | -0.0010922 | -0.00026778 | 3.9343e-08 | -2.6552e-07 | 0.0016693 | 0.0016694 | 0.0016694 | 0.97237 | -0.2025 | 0.97234 | -0.20277 | 0.61829
22 | 0.00097466 | 0.00023831 | -0.00097459 | -0.00023885 | 6.3031e-08 | -5.4041e-07 | 0.0014894 | 0.0014896 | 0.0014896 | 0.97234 | -0.20277 | 0.97227 | -0.20326 | 0.55172
23 | -0.00023415 | -5.8684e-05 | 0.00023416 | 5.7531e-05 | 7.4578e-09 | -1.153e-06 | 0.00035833 | 0.00035792 | 0.00035833 | 0.97234 | -0.20274 | 0.97237 | -0.2025 | 0.13271
24 | -0.00023416 | -5.7531e-05 | 0.00023417 | 5.616e-05 | 8.841e-09 | -1.3704e-06 | 0.00035792 | 0.00035744 | 0.00035792 | 0.97237 | -0.2025 | 0.97241 | -0.20221 | 0.13256
25 | -0.0015652 | -0.00038599 | 0.0015652 | 0.00038584 | 4.8949e-08 | -1.5115e-07 | 0.0023928 | 0.0023927 | 0.0023928 | 0.97241 | -0.20221 | 0.97244 | -0.20198 | 0.88622
26 | 0.0010325 | 0.00025503 | -0.0010323 | -0.00025646 | 1.8955e-07 | -1.4384e-06 | 0.0015786 | 0.0015792 | 0.0015792 | 0.97241 | -0.20221 | 0.97223 | -0.20357 | 0.58488
27 | -0.0053489 | -0.0013212 | 0.0053508 | 0.0013213 | 1.879e-06 | 1.5986e-07 | 0.0081632 | 0.008163 | 0.0081632 | 0.97419 | -0.18903 | 0.97454 | -0.18642 | 3.0234
28 | 0.0044623 | 0.001099 | -0.0044617 | -0.001099 | 6.0634e-07 | -2.7706e-08 | 0.006809 | 0.0068091 | 0.0068091 | 0.97419 | -0.18903 | 0.97405 | -0.19005 | 2.5219
29 | 0.00051718 | 0.00012496 | -0.00051716 | -0.0001256 | 2.0128e-08 | -6.3926e-07 | 0.00078803 | 0.00078825 | 0.00078825 | 0.97454 | -0.18642 | 0.9745 | -0.18672 | 0.29194
30 | -0.005868 | -0.0014463 | 0.0058885 | 0.0014491 | 2.0564e-05 | 2.7648e-06 | 0.0089511 | 0.0089492 | 0.0089511 | 0.97454 | -0.18642 | 0.97806 | -0.16028 | 3.3152
31 | 0.00013738 | 3.3886e-05 | -0.00013738 | -3.443e-05 | 1.202e-09 | -5.4442e-07 | 0.00020968 | 0.00020987 | 0.00020987 | 0.97405 | -0.19005 | 0.97404 | -0.19011 | 0.07773
32 | 0.00044125 | 0.00010658 | -0.0004412 | -0.00010903 | 5.6151e-08 | -2.4549e-06 | 0.00067235 | 0.00067322 | 0.00067322 | 0.9745 | -0.18672 | 0.97437 | -0.18769 | 0.24934
33 | -0.0062766 | -0.0015463 | 0.0062774 | 0.0015464 | 7.9106e-07 | 1.294e-07 | 0.0095396 | 0.0095395 | 0.0095396 | 0.97806 | -0.16028 | 0.97819 | -0.15934 | 3.5332
34 | 0.00029113 | 7.1595e-05 | -0.00029112 | -7.2962e-05 | 1.3569e-08 | -1.3664e-06 | 0.00044412 | 0.00044461 | 0.00044461 | 0.97437 | -0.18769 | 0.97432 | -0.18803 | 0.16467
35 | 0.00015006 | 3.7436e-05 | -0.00015006 | -3.7609e-05 | 4.5409e-10 | -1.7246e-07 | 0.00022911 | 0.00022917 | 0.00022917 | 0.97437 | -0.18769 | 0.97437 | -0.18771 | 0.084877
36 | 0.0015653 | 0.00038565 | -0.0015652 | -0.00038584 | 6.1557e-08 | -1.901e-07 | 0.0023927 | 0.0023927 | 0.0023927 | 0.97248 | -0.20169 | 0.97244 | -0.20198 | 0.8862
37 | -0.00033841 | -8.4815e-05 | 0.00033842 | 8.4658e-05 | 2.0172e-09 | -1.5627e-07 | 0.00051157 | 0.00051152 | 0.00051157 | 0.98435 | -0.11406 | 0.98435 | -0.11402 | 0.18947
38 | -0.0084529 | -0.0020872 | 0.0084535 | 0.0020873 | 5.4202e-07 | 1.4072e-07 | 0.012767 | 0.012767 | 0.012767 | 0.98435 | -0.11402 | 0.98442 | -0.11354 | 4.7285
39 | 0.0079696 | 0.0019662 | -0.0079327 | -0.0019572 | 3.6928e-05 | 9.036e-06 | 0.012036 | 0.012038 | 0.012038 | 0.98435 | -0.11402 | 0.97965 | -0.14861 | 4.4586
40 | -0.0015259 | -0.00036253 | 0.0015263 | 0.00036115 | 4.0569e-07 | -1.3801e-06 | 0.0023099 | 0.0023094 | 0.0023099 | 0.98002 | -0.14922 | 0.98029 | -0.1471 | 0.85552
41 | 0.0007858 | 0.00017705 | -0.00078579 | -0.00017721 | 1.1645e-08 | -1.6259e-07 | 0.0011863 | 0.0011864 | 0.0011864 | 0.98002 | -0.14922 | 0.98001 | -0.14935 | 0.4394
42 | -0.003254 | -0.00077978 | 0.0032573 | 0.00077829 | 3.322e-06 | -1.4909e-06 | 0.0049268 | 0.0049258 | 0.0049268 | 0.98029 | -0.1471 | 0.98133 | -0.13906 | 1.8247
43 | 0.0017277 | 0.00041862 | -0.0017268 | -0.00042086 | 8.7163e-07 | -2.2331e-06 | 0.0026174 | 0.0026183 | 0.0026183 | 0.98029 | -0.1471 | 0.97978 | -0.15096 | 0.96975
44 | 0.00053238 | 0.00011417 | -0.00053229 | -0.00011691 | 8.855e-08 | -2.7429e-06 | 0.00080192 | 0.00080279 | 0.00080279 | 0.98001 | -0.14935 | 0.97984 | -0.15088 | 0.29733
45 | 0.00025341 | 6.3039e-05 | -0.00025341 | -6.3489e-05 | 3.3049e-09 | -4.4967e-07 | 0.00038461 | 0.00038477 | 0.00038477 | 0.98001 | -0.14935 | 0.98 | -0.14945 | 0.14251
46 | -0.0032573 | -0.00077829 | 0.0032578 | 0.00077807 | 4.8029e-07 | -2.1612e-07 | 0.0049258 | 0.0049257 | 0.0049258 | 0.98133 | -0.13906 | 0.98148 | -0.1379 | 1.8244
47 | 0.00040348 | 8.4631e-05 | -0.00040348 | -8.4666e-05 | 6.444e-10 | -3.502e-08 | 0.00060728 | 0.00060729 | 0.00060729 | 0.97984 | -0.15088 | 0.97984 | -0.15089 | 0.22492
48 | 9.5515e-05 | 2.3916e-05 | -9.5515e-05 | -2.3938e-05 | 2.2959e-11 | -2.1995e-08 | 0.00014502 | 0.00014503 | 0.00014503 | 0.98 | -0.14945 | 0.98 | -0.14945 | 0.053715
49 | -0.0032578 | -0.00077807 | 0.0032623 | 0.00077602 | 4.5442e-06 | -2.0519e-06 | 0.0049257 | 0.0049244 | 0.0049257 | 0.98148 | -0.1379 | 0.98289 | -0.12684 | 1.8243
50 | 0.00026722 | 5.0518e-05 | -0.00026715 | -5.9828e-05 | 7.4768e-08 | -9.3099e-06 | 0.00040061 | 0.00040339 | 0.00040339 | 0.97984 | -0.15089 | 0.97956 | -0.15363 | 0.14941
51 | 0.0027699 | 0.00066877 | -0.0027677 | -0.00067045 | 2.176e-06 | -1.6847e-06 | 0.0041844 | 0.0041853 | 0.0041853 | 0.98289 | -0.12684 | 0.98209 | -0.13292 | 1.5501
52 | -0.0061167 | -0.001466 | 0.0061278 | 0.0014676 | 1.1041e-05 | 1.6129e-06 | 0.0092368 | 0.0092359 | 0.0092368 | 0.98289 | -0.12684 | 0.98472 | -0.11267 | 3.421
53 | 0.00026715 | 5.9828e-05 | -0.00026713 | -6.1926e-05 | 1.7e-08 | -2.0972e-06 | 0.00040339 | 0.00040408 | 0.00040408 | 0.97956 | -0.15363 | 0.97949 | -0.15418 | 0.14966
54 | -0.0084535 | -0.0020873 | 0.0084625 | 0.0020897 | 9.0604e-06 | 2.3509e-06 | 0.012767 | 0.012767 | 0.012767 | 0.98442 | -0.11354 | 0.98551 | -0.10558 | 4.7285
55 | 0.0077591 | 0.0019136 | -0.0077585 | -0.0019135 | 6.0962e-07 | 1.4575e-07 | 0.011775 | 0.011775 | 0.011775 | 0.97965 | -0.14861 | 0.97957 | -0.14919 | 4.3609
56 | -0.0085585 | -0.0021137 | 0.0085605 | 0.0021142 | 1.9798e-06 | 5.1889e-07 | 0.012911 | 0.012911 | 0.012911 | 0.98551 | -0.10558 | 0.98574 | -0.10386 | 4.782
57 | -0.0085605 | -0.0021142 | 0.0085676 | 0.0021161 | 7.0675e-06 | 1.8514e-06 | 0.012911 | 0.012911 | 0.012911 | 0.98574 | -0.10386 | 0.98658 | -0.097723 | 4.782
58 | -0.0086396 | -0.0021341 | 0.0086664 | 0.0021315 | 2.6791e-05 | -2.6788e-06 | 0.01302 | 0.013015 | 0.01302 | 0.98658 | -0.097723 | 0.98974 | -0.074622 | 2.4111
59 | -0.0087472 | -0.0021517 | 0.0087482 | 0.0021516 | 9.8995e-07 | -9.1884e-08 | 0.013137 | 0.013137 | 0.013137 | 0.98974 | -0.074622 | 0.98986 | -0.073775 | 2.4327
60 | -0.00014843 | -3.72e-05 | 0.00014844 | 3.5725e-05 | 3.7162e-09 | -1.4757e-06 | 0.00022551 | 0.00022499 | 0.00022551 | 0.9794 | -0.15487 | 0.97943 | -0.15468 | 0.083523
61 | -0.00014844 | -3.5725e-05 | 0.00014844 | 3.218e-05 | 8.8588e-09 | -3.5451e-06 | 0.00022499 | 0.00022383 | 0.00022499 | 0.97943 | -0.15468 | 0.97949 | -0.15418 | 0.083331
62 | -0.0013779 | -0.00034169 | 0.0013779 | 0.00034135 | 8.1771e-08 | -3.4342e-07 | 0.0020948 | 0.0020947 | 0.0020948 | 0.97813 | -0.15978 | 0.97819 | -0.15934 | 0.77586
63 | 0.0011976 | 0.00029651 | -0.0011974 | -0.00029767 | 2.0372e-07 | -1.1575e-06 | 0.0018206 | 0.001821 | 0.001821 | 0.97813 | -0.15978 | 0.97796 | -0.16103 | 0.67445
64 | -0.0076553 | -0.0018878 | 0.0076657 | 0.0018903 | 1.0426e-05 | 2.4581e-06 | 0.011634 | 0.011634 | 0.011634 | 0.97819 | -0.15934 | 0.97957 | -0.14919 | 4.309
65 | 0.00057992 | 0.00014292 | -0.00057992 | -0.00014294 | 8.3311e-10 | -2.1237e-08 | 0.00088152 | 0.00088153 | 0.00088153 | 0.97796 | -0.16103 | 0.97796 | -0.16104 | 0.32649
66 | 0.00041614 | 0.00010189 | -0.00041609 | -0.00010428 | 4.8e-08 | -2.3919e-06 | 0.00063233 | 0.00063318 | 0.00063318 | 0.97796 | -0.16104 | 0.97784 | -0.16189 | 0.23451
67 | -0.0089454 | -0.002201 | 0.0089463 | 0.002201 | 8.8921e-07 | -6.4105e-08 | 0.013433 | 0.013433 | 0.013433 | 0.98986 | -0.073775 | 0.98996 | -0.07303 | 2.4876
68 | -0.0089463 | -0.002201 | 0.0089488 | 0.0022008 | 2.5377e-06 | -1.8346e-07 | 0.013433 | 0.013432 | 0.013433 | 0.98996 | -0.07303 | 0.99025 | -0.070906 | 2.4876
69 | 0.00041843 | 0.00010442 | -0.00041842 | -0.00010487 | 8.6723e-09 | -4.4901e-07 | 0.0006286 | 0.00062876 | 0.00062876 | 0.99025 | -0.070906 | 0.99023 | -0.071056 | 0.23288
70 | -0.0093672 | -0.0023052 | 0.0093857 | 0.0023046 | 1.8415e-05 | -6.1531e-07 | 0.014061 | 0.014058 | 0.014061 | 0.99025 | -0.070906 | 0.99226 | -0.056177 | 2.6039
71 | -0.0093857 | -0.0023046 | 0.0093897 | 0.0023044 | 4.0674e-06 | -1.4051e-07 | 0.014058 | 0.014058 | 0.014058 | 0.99226 | -0.056177 | 0.9927 | -0.05292 | 2.6034
72 | -0.0094866 | -0.0023287 | 0.0094958 | 0.0023285 | 9.2612e-06 | -2.4702e-07 | 0.014203 | 0.014202 | 0.014203 | 0.9927 | -0.05292 | 0.9937 | -0.045575 | 2.6302
73 | -0.013157 | -0.003246 | 0.013158 | 0.0032463 | 1.2922e-06 | 2.2002e-07 | 0.019684 | 0.019684 | 0.019684 | 0.9937 | -0.045575 | 0.9938 | -0.044844 | 3.6452
74 | -0.028196 | -0.0069494 | 0.028251 | 0.0069679 | 5.465e-05 | 1.8462e-05 | 0.042177 | 0.042177 | 0.042177 | 0.9938 | -0.044844 | 0.99579 | -0.030405 | 7.8106
75 | 0.015038 | 0.0037031 | -0.015025 | -0.0036988 | 1.2768e-05 | 4.3871e-06 | 0.022494 | 0.022494 | 0.022494 | 0.9938 | -0.044844 | 0.99293 | -0.051195 | 8.331
76 | -0.029083 | -0.0071753 | 0.029202 | 0.0072159 | 0.00011915 | 4.0534e-05 | 0.043419 | 0.043417 | 0.043419 | 0.99579 | -0.030405 | 1 | 0 | 8.0405
77 | 0.00083144 | 0.00020745 | -0.00083137 | -0.00020836 | 6.9254e-08 | -9.0886e-07 | 0.0012421 | 0.0012424 | 0.0012424 | 0.99579 | -0.030405 | 0.9957 | -0.031009 | 0.46016
78 | 0.013034 | 0.0031996 | -0.012965 | -0.0031769 | 6.8831e-05 | 2.2745e-05 | 0.019509 | 0.019511 | 0.019511 | 0.99293 | -0.051195 | 0.98752 | -0.091073 | 7.2261
79 | 0.0061446 | 0.00147 | -0.0061278 | -0.0014676 | 1.6838e-05 | 2.4398e-06 | 0.0092345 | 0.0092359 | 0.0092359 | 0.98752 | -0.091073 | 0.98472 | -0.11267 | 3.4207
80 | 0.0053445 | 0.001337 | -0.0053357 | -0.0013363 | 8.7487e-06 | 6.0347e-07 | 0.0080523 | 0.0080533 | 0.0080533 | 0.98752 | -0.091073 | 0.98585 | -0.10294 | 2.9827
81 | -0.0035185 | -0.00088183 | 0.00352 | 0.00088135 | 1.4107e-06 | -4.7826e-07 | 0.005313 | 0.0053126 | 0.005313 | 0.98544 | -0.10584 | 0.98585 | -0.10294 | 1.9678
82 | 0.00069601 | 0.00017435 | -0.00069601 | -0.00017444 | 4.5397e-09 | -8.2308e-08 | 0.0010505 | 0.0010505 | 0.0010505 | 0.98585 | -0.10294 | 0.98584 | -0.10298 | 0.38909
83 | 0.0017422 | 0.00042442 | -0.0017415 | -0.00042617 | 6.9575e-07 | -1.7441e-06 | 0.0026414 | 0.0026421 | 0.0026421 | 0.97987 | -0.14983 | 0.97947 | -0.15287 | 0.97855
84 | -0.0017422 | -0.00042442 | 0.0017433 | 0.0004217 | 1.0853e-06 | -2.726e-06 | 0.0026414 | 0.0026403 | 0.0026414 | 0.97987 | -0.14983 | 0.9805 | -0.14505 | 0.97829
85 | 0.00029105 | 6.9617e-05 | -0.00029102 | -7.2936e-05 | 3.2204e-08 | -3.3185e-06 | 0.000441 | 0.00044217 | 0.00044217 | 0.97947 | -0.15287 | 0.97935 | -0.1537 | 0.16377
86 | 0.0014505 | 0.00035655 | -0.0014496 | -0.00035999 | 9.115e-07 | -3.4394e-06 | 0.0022011 | 0.0022024 | 0.0022024 | 0.97947 | -0.15287 | 0.97883 | -0.15753 | 0.81572
87 | -0.0019728 | -0.00047922 | 0.0019737 | 0.00047751 | 9.0587e-07 | -1.7031e-06 | 0.0029886 | 0.0029879 | 0.0029886 | 0.9805 | -0.14505 | 0.98097 | -0.14152 | 1.1069
88 | 0.0024491 | 0.0005906 | -0.0024474 | -0.00059244 | 1.6873e-06 | -1.8445e-06 | 0.0037026 | 0.0037034 | 0.0037034 | 0.98209 | -0.13292 | 0.98139 | -0.13825 | 1.3716
89 | 0.00084034 | 0.00020731 | -0.00084007 | -0.00021054 | 2.7036e-07 | -3.2351e-06 | 0.0012763 | 0.0012775 | 0.0012775 | 0.97883 | -0.15753 | 0.97851 | -0.15989 | 0.47315
90 | -0.0023665 | -0.00057361 | 0.0023675 | 0.00057242 | 1.0024e-06 | -1.1953e-06 | 0.0035828 | 0.0035823 | 0.0035828 | 0.98097 | -0.14152 | 0.98139 | -0.13825 | 1.327
91 | 0.00012305 | 2.8499e-05 | -0.00012304 | -3.0837e-05 | 4.0116e-09 | -2.3384e-06 | 0.00018584 | 0.00018665 | 0.00018665 | 0.98097 | -0.14152 | 0.98093 | -0.14177 | 0.069129
92 | -0.00033774 | -8.4248e-05 | 0.00033775 | 8.3731e-05 | 6.9816e-09 | -5.167e-07 | 0.00051686 | 0.00051667 | 0.00051686 | 0.97206 | -0.20475 | 0.97209 | -0.20459 | 0.19143
93 | 0.00021337 | 5.3078e-05 | -0.00021337 | -5.3474e-05 | 2.1333e-09 | -3.9662e-07 | 0.00032648 | 0.00032662 | 0.00032662 | 0.97206 | -0.20475 | 0.97205 | -0.20482 | 0.12097
94 | -0.00033775 | -8.3731e-05 | 0.00033775 | 8.3612e-05 | 1.6105e-09 | -1.1925e-07 | 0.00051667 | 0.00051663 | 0.00051667 | 0.97209 | -0.20459 | 0.97209 | -0.20456 | 0.19136
95 | -0.00049411 | -0.0001228 | 0.00049411 | 0.00012257 | 6.5561e-09 | -2.2542e-07 | 0.00075598 | 0.00075589 | 0.00075598 | 0.97209 | -0.20456 | 0.9721 | -0.20446 | 0.27999
96 | -0.00090273 | -0.00022498 | 0.00090274 | 0.00022492 | 6.3861e-09 | -6.4036e-08 | 0.0013814 | 0.0013813 | 0.0013814 | 0.9721 | -0.20446 | 0.97211 | -0.20441 | 0.51162
97 | -0.0010322 | -0.00025736 | 0.0010323 | 0.00025646 | 1.1859e-07 | -8.9913e-07 | 0.0015795 | 0.0015792 | 0.0015795 | 0.97211 | -0.20441 | 0.97223 | -0.20357 | 0.585

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.030183 | 0.0072615

## res_load
| p_mw | q_mvar
0 | 0.00037759 | 9.4634e-05
1 | 0.0002599 | 6.5136e-05
2 | 0.00010155 | 2.545e-05
3 | 0.00021147 | 5.2999e-05
4 | 0.00018584 | 4.6577e-05
5 | 0.0004856 | 0.0001217
6 | 0.00012379 | 3.1024e-05
7 | 0.00022022 | 5.5192e-05
8 | 0.0004081 | 0.00010228
9 | 0.00026045 | 6.5276e-05
10 | 0.00015816 | 3.9638e-05
11 | 0.00011864 | 2.9733e-05
12 | 0.00011075 | 2.7757e-05
13 | 6.6416e-05 | 1.6645e-05
14 | 0.00014805 | 3.7105e-05
15 | 0.00033065 | 8.2868e-05
16 | 0.00011758 | 2.9468e-05
17 | 0.00022235 | 5.5725e-05
18 | 0.00023415 | 5.8684e-05
19 | 0.00029849 | 7.4808e-05
20 | 0.00088664 | 0.00022221
21 | 7.5905e-05 | 1.9024e-05
22 | 0.00038804 | 9.7253e-05
23 | 0.00013738 | 3.443e-05
24 | 0.00046686 | 0.00011701
25 | 0.00033841 | 8.4815e-05
26 | 0.00014488 | 3.631e-05
27 | 0.00029112 | 7.2962e-05
28 | 0.00015006 | 3.7609e-05
29 | 0.0007401 | 0.00018549
30 | 0.00010342 | 2.5919e-05
31 | 0.00012881 | 3.2283e-05
32 | 0.0001579 | 3.9572e-05
33 | 0.00013625 | 3.4148e-05
34 | 9.5515e-05 | 2.3938e-05
35 | 8.454e-05 | 2.1188e-05
36 | 0.00017363 | 4.3515e-05
37 | 9.6009e-05 | 2.4062e-05
38 | 7.2058e-05 | 1.8059e-05
39 | 8.0789e-05 | 2.0248e-05
40 | 0.00014843 | 3.72e-05
41 | 0.00011869 | 2.9746e-05
42 | 0.00018027 | 4.5179e-05
43 | 0.00061746 | 0.00015475
44 | 9.2735e-05 | 2.3241e-05
45 | 0.00016378 | 4.1047e-05
46 | 0.00041609 | 0.00010428
47 | 0.00019717 | 4.9414e-05
48 | 0.00041842 | 0.00010487
49 | 9.6864e-05 | 2.4276e-05
50 | 0.0036611 | 0.00091756
51 | 0.0019916 | 0.00049913
52 | 0.0001818 | 4.5563e-05
53 | 0.00083137 | 0.00020836
54 | 0.0014759 | 0.00036991
55 | 0.0035185 | 0.00088183
56 | 0.0011198 | 0.00028064
57 | 0.00069601 | 0.00017444
58 | 0.0002295 | 5.7518e-05
59 | 0.00031861 | 7.9851e-05
60 | 0.00029102 | 7.2936e-05
61 | 0.00060922 | 0.00015268
62 | 0.00026973 | 6.7601e-05
63 | 0.00084007 | 0.00021054
64 | 7.9908e-05 | 2.0027e-05
65 | 0.00012304 | 3.0837e-05
66 | 0.00012437 | 3.117e-05
67 | 0.00021337 | 5.3474e-05
68 | 0.00015636 | 3.9187e-05
69 | 0.00040862 | 0.00010241
70 | 0.00012945 | 3.2444e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1