## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1631-100_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1631-100_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1631-100_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1631-100_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1631-100_0_2_node_11 | 0.4 | n |  | TRUE
5 | bus_LV_1631-100_0_2_node_12 | 0.4 | n |  | TRUE
6 | bus_LV_1631-100_0_2_node_8 | 0.4 | n |  | TRUE
7 | bus_LV_1631-100_0_2_node_10 | 0.4 | n |  | TRUE
8 | bus_LV_1631-100_0_2_node_13 | 0.4 | n |  | TRUE
9 | bus_LV_1631-100_0_2_node_4 | 0.4 | n |  | TRUE
10 | bus_LV_1631-100_0_2_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_1631-100_0_2_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1631-100_0_2_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_1631-100_0_2_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1631-100_0_2_node_26 | 0.4 | n |  | TRUE
15 | bus_LV_1631-100_0_2_node_39 | 0.4 | n |  | TRUE
16 | bus_LV_1631-100_0_2_node_43 | 0.4 | n |  | TRUE
17 | bus_LV_1631-100_0_2_node_40 | 0.4 | n |  | TRUE
18 | bus_LV_1631-100_0_2_node_25 | 0.4 | n |  | TRUE
19 | bus_LV_1631-100_0_2_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_1631-100_0_2_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_1631-100_0_2_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_1631-100_0_2_node_23 | 0.4 | n |  | TRUE
23 | bus_LV_1631-100_0_2_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_1631-100_0_2_node_27 | 0.4 | n |  | TRUE
25 | bus_LV_1631-100_0_2_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_1631-100_0_2_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_1631-100_0_2_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_1631-100_0_2_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_1631-100_0_2_node_22 | 0.4 | n |  | TRUE
30 | bus_LV_1631-100_0_2_node_42 | 0.4 | n |  | TRUE
31 | bus_LV_1631-100_0_2_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_1631-100_0_2_node_35 | 0.4 | n |  | TRUE
33 | bus_LV_1631-100_0_2_node_36 | 0.4 | n |  | TRUE
34 | bus_LV_1631-100_0_2_node_38 | 0.4 | n |  | TRUE
35 | bus_LV_1631-100_0_2_node_28 | 0.4 | n |  | TRUE
36 | bus_LV_1631-100_0_2_node_29 | 0.4 | n |  | TRUE
37 | bus_LV_1631-100_0_2_node_30 | 0.4 | n |  | TRUE
38 | bus_LV_1631-100_0_2_node_31 | 0.4 | n |  | TRUE
39 | bus_LV_1631-100_0_2_node_32 | 0.4 | n |  | TRUE
40 | bus_LV_1631-100_0_2_node_33 | 0.4 | n |  | TRUE
41 | bus_MV_13_0_node_1 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1631-100_0_2_load_0 | 0 | 0.0094071 | 0.0023576 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1631-100_0_2_load_1 | 1 | 0.0077468 | 0.0019415 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1631-100_0_2_load_2 | 2 | 0.0055731 | 0.0013968 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1631-100_0_2_load_12 | 5 | 0.019313 | 0.0048403 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1631-100_0_2_load_8 | 6 | 0.0017429 | 0.00043681 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1631-100_0_2_load_13 | 8 | 0.010581 | 0.0026519 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1631-100_0_2_load_4 | 9 | 0.0073212 | 0.0018349 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1631-100_0_2_load_5 | 10 | 0.0065273 | 0.0016359 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1631-100_0_2_load_7 | 11 | 0.0053689 | 0.0013456 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1631-100_0_2_load_39 | 15 | 0.0027682 | 0.00069379 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1631-100_0_2_load_43 | 16 | 0.015588 | 0.0039068 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1631-100_0_2_load_40 | 17 | 0.0020241 | 0.00050729 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1631-100_0_2_load_25 | 18 | 0.0058206 | 0.0014588 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1631-100_0_2_load_15 | 20 | 0.0060963 | 0.0015279 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1631-100_0_2_load_23 | 22 | 0.002797 | 0.000701 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1631-100_0_2_load_20 | 23 | 0.0022749 | 0.00057015 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1631-100_0_2_load_27 | 24 | 0.0011206 | 0.00028084 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1631-100_0_2_load_18 | 25 | 0.0013229 | 0.00033156 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1631-100_0_2_load_17 | 26 | 0.0035409 | 0.00088742 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1631-100_0_2_load_21 | 28 | 0.004934 | 0.0012366 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1631-100_0_2_load_22 | 29 | 0.004204 | 0.0010536 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1631-100_0_2_load_42 | 30 | 0.0036695 | 0.00091966 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1631-100_0_2_load_24 | 31 | 0.0084724 | 0.0021234 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1631-100_0_2_load_35 | 32 | 0.00255 | 0.00063908 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1631-100_0_2_load_28 | 35 | 0.00326 | 0.00081704 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1631-100_0_2_load_29 | 36 | 0.002156 | 0.00054034 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1631-100_0_2_load_31 | 38 | 0.0010883 | 0.00027276 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1631-100_0_2_load_33 | 40 | 0.0020388 | 0.00051096 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 5 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1631-100_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.015288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1631-100_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0078514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1631-100_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.02291 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1631-100_0_2_line_3 | NAYY 4x150 SE | 3 | 4 | 0.018223 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1631-100_0_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.0357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1631-100_0_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.032382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1631-100_0_2_line_6 | NAYY 4x150 SE | 4 | 7 | 0.030082 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1631-100_0_2_line_7 | NAYY 4x150 SE | 5 | 8 | 0.031595 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1631-100_0_2_line_8 | NAYY 4x150 SE | 6 | 12 | 0.009901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1631-100_0_2_line_9 | NAYY 4x150 SE | 7 | 16 | 0.005432 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1631-100_0_2_line_10 | NAYY 4x150 SE | 7 | 17 | 0.083106 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1631-100_0_2_line_11 | NAYY 4x150 SE | 8 | 19 | 0.014979 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1631-100_0_2_line_12 | NAYY 4x150 SE | 9 | 10 | 0.0069528 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1631-100_0_2_line_13 | NAYY 4x150 SE | 10 | 11 | 0.01811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1631-100_0_2_line_14 | NAYY 4x150 SE | 11 | 14 | 0.020165 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1631-100_0_2_line_15 | NAYY 4x150 SE | 12 | 13 | 0.020592 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1631-100_0_2_line_16 | NAYY 4x150 SE | 13 | 15 | 0.014485 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1631-100_0_2_line_17 | NAYY 4x150 SE | 14 | 18 | 0.029101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1631-100_0_2_line_18 | NAYY 4x150 SE | 18 | 31 | 0.0050805 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1631-100_0_2_line_19 | NAYY 4x150 SE | 19 | 20 | 0.03105 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1631-100_0_2_line_20 | NAYY 4x150 SE | 19 | 21 | 0.008287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1631-100_0_2_line_21 | NAYY 4x150 SE | 21 | 22 | 0.030943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1631-100_0_2_line_22 | NAYY 4x150 SE | 21 | 23 | 0.014543 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1631-100_0_2_line_23 | NAYY 4x150 SE | 22 | 24 | 0.01545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1631-100_0_2_line_24 | NAYY 4x150 SE | 23 | 25 | 0.0051953 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1631-100_0_2_line_25 | NAYY 4x150 SE | 24 | 35 | 0.010303 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1631-100_0_2_line_26 | NAYY 4x150 SE | 25 | 26 | 0.0098867 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1631-100_0_2_line_27 | NAYY 4x150 SE | 26 | 27 | 0.03971 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1631-100_0_2_line_28 | NAYY 4x150 SE | 27 | 28 | 0.026247 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1631-100_0_2_line_29 | NAYY 4x150 SE | 27 | 29 | 0.01013 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1631-100_0_2_line_30 | NAYY 4x150 SE | 28 | 30 | 0.11809 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1631-100_0_2_line_31 | NAYY 4x150 SE | 29 | 31 | 0.018847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1631-100_0_2_line_32 | NAYY 4x150 SE | 30 | 34 | 0.11096 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1631-100_0_2_line_33 | NAYY 4x150 SE | 32 | 33 | 0.11396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1631-100_0_2_line_34 | NAYY 4x150 SE | 33 | 34 | 0.10526 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1631-100_0_2_line_35 | NAYY 4x150 SE | 35 | 36 | 0.0014469 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1631-100_0_2_line_36 | NAYY 4x150 SE | 36 | 37 | 0.0034287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1631-100_0_2_line_37 | NAYY 4x150 SE | 37 | 38 | 0.0090769 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1631-100_0_2_line_38 | NAYY 4x150 SE | 38 | 39 | 0.013071 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1631-100_0_2_line_39 | NAYY 4x150 SE | 39 | 40 | 0.002799 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1631-100_0_2_trafo_12 | 0.25 MVA 20/0.4 kV | 41 | 5 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2719016.4801 | 1197888.4832 | 2719007.3118 | 1197900.7168
1 | 2719015.3015 | 1197880.7207 | 2719016.4801 | 1197888.4832
2 | 2718993.5725 | 1197919.0495 | 2719007.3118 | 1197900.7168
3 | 2718993.5725 | 1197919.0495 | 2718987.247 | 1197901.9556
4 | 2718993.5725 | 1197919.0495 | 2719005.9538 | 1197952.5334
5 | 2718987.247 | 1197901.9556 | 2718982.5913 | 1197889.376 | 2718975.7907 | 1197871.668
6 | 2718987.247 | 1197901.9556 | 2718962.5203 | 1197904.521 | 2718957.439 | 1197902.9854
7 | 2719005.9538 | 1197952.5334 | 2719014.0301 | 1197974.3748 | 2719017.0588 | 1197982.1116
8 | 2718972.2338 | 1197862.428 | 2718974.2259 | 1197867.5936 | 2718975.7907 | 1197871.668
9 | 2718957.439 | 1197902.9854 | 2718958.7704 | 1197897.7192
10 | 2718957.439 | 1197902.9854 | 2718915.5707 | 1197974.7741
11 | 2719022.5191 | 1197996.0596 | 2719017.0588 | 1197982.1116
12 | 2719057.6468 | 1197856.5925 | 2719058.9851 | 1197863.4154
13 | 2719062.4708 | 1197881.1867 | 2719058.9851 | 1197863.4154
14 | 2719066.3521 | 1197900.9741 | 2719062.4708 | 1197881.1867
15 | 2718972.2338 | 1197862.428 | 2718968.6266 | 1197854.9619 | 2718962.6469 | 1197844.2129
16 | 2718962.6469 | 1197844.2129 | 2718975.008 | 1197836.6625
17 | 2719066.3521 | 1197900.9741 | 2719071.9493 | 1197929.5315
18 | 2719071.9493 | 1197929.5315 | 2719072.9265 | 1197934.5172
19 | 2719014.6807 | 1198019.732 | 2719010.9033 | 1198006.6695 | 2719011.0668 | 1198003.8151 | 2719011.8215 | 1198001.4951 | 2719014.3747 | 1197999.1442 | 2719022.5191 | 1197996.0596
20 | 2719025.5344 | 1198003.7809 | 2719022.5191 | 1197996.0596
21 | 2719025.5344 | 1198003.7809 | 2719036.8534 | 1198032.5793
22 | 2719025.5344 | 1198003.7809 | 2719038.9686 | 1197998.2107
23 | 2719036.8534 | 1198032.5793 | 2719042.5048 | 1198046.958
24 | 2719043.093 | 1197995.1647 | 2719040.4521 | 1197997.5956 | 2719038.9686 | 1197998.2107
25 | 2719046.0982 | 1198056.6138 | 2719043.0083 | 1198048.239 | 2719042.5048 | 1198046.958
26 | 2719043.093 | 1197995.1647 | 2719045.7137 | 1197992.7523 | 2719047.3291 | 1197986.6374
27 | 2719075.6236 | 1197962.8928 | 2719070.1763 | 1197967.1097 | 2719053.9591 | 1197972.7464 | 2719049.2815 | 1197979.2469 | 2719047.3291 | 1197986.6374
28 | 2719075.6236 | 1197962.8928 | 2719085.9844 | 1197963.6553 | 2719090.303 | 1197978.9141
29 | 2719075.6236 | 1197962.8928 | 2719077.2019 | 1197956.3306 | 2719076.5515 | 1197953.0126
30 | 2719090.303 | 1197978.9141 | 2719194.2822 | 1197922.9392
31 | 2719072.9265 | 1197934.5172 | 2719076.5515 | 1197953.0126
32 | 2719281.6412 | 1197986.6501 | 2719273.487 | 1197980.6831 | 2719234.3077 | 1197957.3401 | 2719219.1097 | 1197950.8323 | 2719206.495 | 1197943.1419 | 2719200.6912 | 1197936.9661 | 2719195.3956 | 1197928.61 | 2719194.2822 | 1197922.9392
33 | 2719366.6467 | 1198045.2895 | 2719368.1672 | 1198035.535 | 2719367.7816 | 1198024.3302 | 2719366.2827 | 1198017.3729 | 2719347.4018 | 1197980.5358 | 2719331.8909 | 1197938.9736
34 | 2719366.6467 | 1198045.2895 | 2719359.6976 | 1198035.0655 | 2719351.6314 | 1198029.6561 | 2719326.774 | 1198018.5629 | 2719304.766 | 1198007.8381 | 2719296.7366 | 1198003.2523 | 2719281.6412 | 1197986.6501
35 | 2719046.0982 | 1198056.6138 | 2719046.599 | 1198057.9712
36 | 2719047.7859 | 1198061.188 | 2719046.599 | 1198057.9712
37 | 2719047.7859 | 1198061.188 | 2719050.9259 | 1198069.7044
38 | 2719055.0557 | 1198082.1036 | 2719052.0356 | 1198072.7144 | 2719050.9259 | 1198069.7044
39 | 2719055.0557 | 1198082.1036 | 2719055.9127 | 1198084.7681

## bus_geodata
| x | y | coords
0 | 2719016.4801 | 1197888.4832
1 | 2719007.3118 | 1197900.7168
2 | 2719015.3015 | 1197880.7207
3 | 2718993.5725 | 1197919.0495
4 | 2718987.247 | 1197901.9556
5 | 2719005.9538 | 1197952.5334
6 | 2718975.7907 | 1197871.668
7 | 2718957.439 | 1197902.9854
8 | 2719017.0588 | 1197982.1116
9 | 2719057.6468 | 1197856.5925
10 | 2719058.9851 | 1197863.4154
11 | 2719062.4708 | 1197881.1867
12 | 2718972.2338 | 1197862.428
13 | 2718962.6469 | 1197844.2129
14 | 2719066.3521 | 1197900.9741
15 | 2718975.008 | 1197836.6625
16 | 2718958.7704 | 1197897.7192
17 | 2718915.5707 | 1197974.7741
18 | 2719071.9493 | 1197929.5315
19 | 2719022.5191 | 1197996.0596
20 | 2719014.6807 | 1198019.732
21 | 2719025.5344 | 1198003.7809
22 | 2719036.8534 | 1198032.5793
23 | 2719038.9686 | 1197998.2107
24 | 2719042.5048 | 1198046.958
25 | 2719043.093 | 1197995.1647
26 | 2719047.3291 | 1197986.6374
27 | 2719075.6236 | 1197962.8928
28 | 2719090.303 | 1197978.9141
29 | 2719076.5515 | 1197953.0126
30 | 2719194.2822 | 1197922.9392
31 | 2719072.9264 | 1197934.5172
32 | 2719331.8909 | 1197938.9736
33 | 2719366.6467 | 1198045.2895
34 | 2719281.6412 | 1197986.6501
35 | 2719046.0982 | 1198056.6138
36 | 2719046.599 | 1198057.9712
37 | 2719047.7859 | 1198061.188
38 | 2719050.9259 | 1198069.7044
39 | 2719055.0557 | 1198082.1036
40 | 2719055.9127 | 1198084.7681
41 | 2718993.5725 | 1197919.0495

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99664 | -0.023552 | 0.0094071 | 0.0023576
1 | 0.99697 | -0.021251 | 0.0077468 | 0.0019415
2 | 0.99658 | -0.023992 | 0.0055731 | 0.0013968
3 | 0.99771 | -0.016026 | 0 | 0
4 | 0.99713 | -0.020075 | 0 | 0
5 | 1 | 0 | -0.13181 | -0.032957
6 | 0.99692 | -0.021543 | 0.0017429 | 0.00043681
7 | 0.99638 | -0.0254 | 0 | 0
8 | 0.99613 | -0.026978 | 0.010581 | 0.0026519
9 | 0.98511 | -0.1046 | 0.0073212 | 0.0018349
10 | 0.98518 | -0.10408 | 0.0065273 | 0.0016359
11 | 0.98555 | -0.1015 | 0.0053689 | 0.0013456
12 | 0.99689 | -0.021819 | 0 | 0
13 | 0.9968 | -0.022392 | 0 | 0
14 | 0.98611 | -0.09752 | 0 | 0
15 | 0.99675 | -0.022795 | 0.0027682 | 0.00069379
16 | 0.99625 | -0.026251 | 0.015588 | 0.0039068
17 | 0.99613 | -0.027095 | 0.0020241 | 0.00050729
18 | 0.98692 | -0.091783 | 0.0058206 | 0.0014588
19 | 0.99451 | -0.038241 | 0 | 0
20 | 0.99424 | -0.040152 | 0.0060963 | 0.0015279
21 | 0.9937 | -0.043977 | 0 | 0
22 | 0.99314 | -0.047878 | 0.002797 | 0.000701
23 | 0.99252 | -0.052228 | 0.0022749 | 0.00057015
24 | 0.99293 | -0.04939 | 0.0011206 | 0.00028084
25 | 0.99212 | -0.055061 | 0.0013229 | 0.00033156
26 | 0.99137 | -0.060324 | 0.0035409 | 0.00088742
27 | 0.98856 | -0.08011 | 0 | 0
28 | 0.98814 | -0.083112 | 0.004934 | 0.0012366
29 | 0.98801 | -0.084015 | 0.004204 | 0.0010536
30 | 0.98708 | -0.090672 | 0.0036695 | 0.00091966
31 | 0.9871 | -0.09048 | 0.0084724 | 0.0021234
32 | 0.98586 | -0.09936 | 0.00255 | 0.00063908
33 | 0.98628 | -0.096371 | 0 | 0
34 | 0.98667 | -0.093601 | 0 | 0
35 | 0.9928 | -0.050281 | 0.00326 | 0.00081704
36 | 0.99279 | -0.050359 | 0.002156 | 0.00054034
37 | 0.99278 | -0.050468 | 0 | 0
38 | 0.99274 | -0.050755 | 0.0010883 | 0.00027276
39 | 0.9927 | -0.051025 | 0 | 0
40 | 0.99269 | -0.051083 | 0.0020388 | 0.00051096
41 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.014981 | -0.0037544 | 0.014985 | 0.0037561 | 4.7723e-06 | 1.6362e-06 | 0.022367 | 0.022366 | 0.022367 | 0.99664 | -0.023552 | 0.99697 | -0.021251 | 8.2839
1 | 0.0055735 | 0.0013968 | -0.0055731 | -0.0013968 | 3.3925e-07 | 2.8175e-08 | 0.0083214 | 0.0083214 | 0.0083214 | 0.99664 | -0.023552 | 0.99658 | -0.023992 | 3.082
2 | -0.022732 | -0.0056976 | 0.022749 | 0.0057036 | 1.6457e-05 | 6.0305e-06 | 0.033929 | 0.033929 | 0.033929 | 0.99697 | -0.021251 | 0.99771 | -0.016026 | 12.5663
3 | 0.022153 | 0.0055531 | -0.02214 | -0.0055486 | 1.2413e-05 | 4.5364e-06 | 0.03304 | 0.03304 | 0.03304 | 0.99771 | -0.016026 | 0.99713 | -0.020075 | 12.237
4 | -0.044901 | -0.011257 | 0.045001 | 0.011295 | 9.9906e-05 | 3.7958e-05 | 0.066969 | 0.066968 | 0.066969 | 0.99771 | -0.016026 | 1 | 0 | 24.8032
5 | 0.0045125 | 0.0011301 | -0.0045116 | -0.0011302 | 9.1625e-07 | -6.991e-08 | 0.0067337 | 0.0067339 | 0.0067339 | 0.99713 | -0.020075 | 0.99692 | -0.021543 | 2.494
6 | 0.017628 | 0.0044185 | -0.017615 | -0.0044139 | 1.299e-05 | 4.6041e-06 | 0.026306 | 0.026306 | 0.026306 | 0.99713 | -0.020075 | 0.99638 | -0.0254 | 9.7431
7 | 0.086012 | 0.021662 | -0.085689 | -0.021538 | 0.00032314 | 0.00012387 | 0.12802 | 0.12802 | 0.12802 | 1 | 0 | 0.99613 | -0.026978 | 47.4164
8 | 0.0027687 | 0.00069338 | -0.0027686 | -0.00069347 | 1.0551e-07 | -8.8512e-08 | 0.0041324 | 0.0041325 | 0.0041325 | 0.99692 | -0.021543 | 0.99689 | -0.021819 | 1.5305
9 | 0.01559 | 0.0039075 | -0.015588 | -0.0039068 | 1.8375e-06 | 6.3599e-07 | 0.023283 | 0.023283 | 0.023283 | 0.99638 | -0.0254 | 0.99625 | -0.026251 | 8.6234
10 | 0.0020246 | 0.00050639 | -0.0020241 | -0.00050729 | 4.7403e-07 | -8.9982e-07 | 0.0030232 | 0.0030236 | 0.0030236 | 0.99638 | -0.0254 | 0.99613 | -0.027095 | 1.1198
11 | 0.075108 | 0.018887 | -0.07499 | -0.018841 | 0.0001177 | 4.5076e-05 | 0.11222 | 0.11222 | 0.11222 | 0.99613 | -0.026978 | 0.99451 | -0.038241 | 41.5624
12 | -0.0073212 | -0.0018349 | 0.0073218 | 0.001835 | 5.3059e-07 | 1.1555e-07 | 0.011059 | 0.011059 | 0.011059 | 0.98511 | -0.1046 | 0.98518 | -0.10408 | 4.0958
13 | -0.013849 | -0.0034709 | 0.013854 | 0.0034726 | 4.9445e-06 | 1.671e-06 | 0.020918 | 0.020917 | 0.020918 | 0.98518 | -0.10408 | 0.98555 | -0.1015 | 7.7472
14 | -0.019223 | -0.0048181 | 0.019234 | 0.0048219 | 1.0599e-05 | 3.8195e-06 | 0.029024 | 0.029024 | 0.029024 | 0.98555 | -0.1015 | 0.98611 | -0.09752 | 10.7495
15 | 0.0027686 | 0.00069347 | -0.0027684 | -0.00069366 | 2.1944e-07 | -1.8405e-07 | 0.0041325 | 0.0041326 | 0.0041326 | 0.99689 | -0.021819 | 0.9968 | -0.022392 | 1.5306
16 | 0.0027684 | 0.00069366 | -0.0027682 | -0.00069379 | 1.5436e-07 | -1.2943e-07 | 0.0041326 | 0.0041326 | 0.0041326 | 0.9968 | -0.022392 | 0.99675 | -0.022795 | 1.5306
17 | -0.019234 | -0.0048219 | 0.019249 | 0.0048275 | 1.5296e-05 | 5.5117e-06 | 0.029024 | 0.029023 | 0.029024 | 0.98611 | -0.09752 | 0.98692 | -0.091783 | 10.7495
18 | -0.025069 | -0.0062862 | 0.025074 | 0.0062879 | 4.5296e-06 | 1.6772e-06 | 0.037799 | 0.037799 | 0.037799 | 0.98692 | -0.091783 | 0.9871 | -0.09048 | 13.9998
19 | 0.0060979 | 0.0015281 | -0.0060963 | -0.0015279 | 1.6129e-06 | 2.1754e-07 | 0.0091237 | 0.0091239 | 0.0091239 | 0.99451 | -0.038241 | 0.99424 | -0.040152 | 3.3792
20 | 0.068892 | 0.017313 | -0.068837 | -0.017292 | 5.4961e-05 | 2.1031e-05 | 0.10309 | 0.10309 | 0.10309 | 0.99451 | -0.038241 | 0.9937 | -0.043977 | 38.1833
21 | 0.012471 | 0.0031257 | -0.012464 | -0.0031235 | 6.7337e-06 | 2.1893e-06 | 0.018675 | 0.018675 | 0.018675 | 0.9937 | -0.043977 | 0.99314 | -0.047878 | 6.9166
22 | 0.056366 | 0.014167 | -0.056302 | -0.014142 | 6.4675e-05 | 2.4687e-05 | 0.08442 | 0.08442 | 0.08442 | 0.9937 | -0.043977 | 0.99252 | -0.052228 | 31.2668
23 | 0.0096671 | 0.0024225 | -0.009665 | -0.002422 | 2.0224e-06 | 5.7799e-07 | 0.014484 | 0.014484 | 0.014484 | 0.99314 | -0.047878 | 0.99293 | -0.04939 | 5.3645
24 | 0.054027 | 0.013572 | -0.054005 | -0.013564 | 2.1275e-05 | 8.1156e-06 | 0.08101 | 0.08101 | 0.08101 | 0.99252 | -0.052228 | 0.99212 | -0.055061 | 30.0036
25 | 0.0085445 | 0.0021411 | -0.0085434 | -0.0021408 | 1.0541e-06 | 2.7219e-07 | 0.012805 | 0.012805 | 0.012805 | 0.99293 | -0.04939 | 0.9928 | -0.050281 | 4.7425
26 | 0.052683 | 0.013232 | -0.052644 | -0.013217 | 3.8528e-05 | 1.4691e-05 | 0.079025 | 0.079025 | 0.079025 | 0.99212 | -0.055061 | 0.99137 | -0.060324 | 29.2687
27 | 0.049103 | 0.01233 | -0.048969 | -0.012279 | 0.00013463 | 5.1271e-05 | 0.073711 | 0.073711 | 0.073711 | 0.99137 | -0.060324 | 0.98856 | -0.08011 | 27.3004
28 | 0.011168 | 0.0027947 | -0.011163 | -0.0027933 | 4.6272e-06 | 1.4433e-06 | 0.016808 | 0.016808 | 0.016808 | 0.98856 | -0.08011 | 0.98814 | -0.083112 | 6.2253
29 | 0.037801 | 0.009484 | -0.03778 | -0.0094763 | 2.0468e-05 | 7.7426e-06 | 0.056903 | 0.056903 | 0.056903 | 0.98856 | -0.08011 | 0.98801 | -0.084015 | 21.0751
30 | 0.006229 | 0.0015567 | -0.0062225 | -0.0015557 | 6.4816e-06 | 9.8185e-07 | 0.0093785 | 0.009379 | 0.009379 | 0.98814 | -0.083112 | 0.98708 | -0.090672 | 3.4737
31 | 0.033576 | 0.0084226 | -0.033546 | -0.0084113 | 3.0077e-05 | 1.1327e-05 | 0.050571 | 0.050571 | 0.050571 | 0.98801 | -0.084015 | 0.9871 | -0.09048 | 18.7301
32 | 0.002553 | 0.00063604 | -0.002552 | -0.00063706 | 1.025e-06 | -1.0235e-06 | 0.0038473 | 0.0038478 | 0.0038478 | 0.98708 | -0.090672 | 0.98667 | -0.093601 | 1.4251
33 | -0.00255 | -0.00063908 | 0.002551 | 0.00063803 | 1.0532e-06 | -1.0486e-06 | 0.0038488 | 0.0038483 | 0.0038488 | 0.98586 | -0.09936 | 0.98628 | -0.096371 | 1.4255
34 | -0.002551 | -0.00063803 | 0.002552 | 0.00063706 | 9.7259e-07 | -9.6977e-07 | 0.0038483 | 0.0038478 | 0.0038483 | 0.98628 | -0.096371 | 0.98667 | -0.093601 | 1.4253
35 | 0.0052834 | 0.0013238 | -0.0052833 | -0.0013238 | 5.6613e-08 | 3.0648e-09 | 0.0079186 | 0.0079187 | 0.0079187 | 0.9928 | -0.050281 | 0.99279 | -0.050359 | 2.9328
36 | 0.0031274 | 0.00078346 | -0.0031273 | -0.00078348 | 4.7005e-08 | -2.6256e-08 | 0.0046872 | 0.0046872 | 0.0046872 | 0.99279 | -0.050359 | 0.99278 | -0.050468 | 1.736
37 | 0.0031273 | 0.00078348 | -0.0031272 | -0.00078355 | 1.2444e-07 | -6.9501e-08 | 0.0046872 | 0.0046873 | 0.0046873 | 0.99278 | -0.050468 | 0.99274 | -0.050755 | 1.736
38 | 0.0020388 | 0.00051079 | -0.0020388 | -0.00051093 | 7.6172e-08 | -1.397e-07 | 0.003056 | 0.003056 | 0.003056 | 0.99274 | -0.050755 | 0.9927 | -0.051025 | 1.1319
39 | 0.0020388 | 0.00051093 | -0.0020388 | -0.00051096 | 1.6312e-08 | -2.9912e-08 | 0.003056 | 0.003056 | 0.003056 | 0.9927 | -0.051025 | 0.99269 | -0.051083 | 1.1319

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.15113 | 0.037797

## res_load
| p_mw | q_mvar
0 | 0.0094071 | 0.0023576
1 | 0.0077468 | 0.0019415
2 | 0.0055731 | 0.0013968
3 | 0.019313 | 0.0048403
4 | 0.0017429 | 0.00043681
5 | 0.010581 | 0.0026519
6 | 0.0073212 | 0.0018349
7 | 0.0065273 | 0.0016359
8 | 0.0053689 | 0.0013456
9 | 0.0027682 | 0.00069379
10 | 0.015588 | 0.0039068
11 | 0.0020241 | 0.00050729
12 | 0.0058206 | 0.0014588
13 | 0.0060963 | 0.0015279
14 | 0.002797 | 0.000701
15 | 0.0022749 | 0.00057015
16 | 0.0011206 | 0.00028084
17 | 0.0013229 | 0.00033156
18 | 0.0035409 | 0.00088742
19 | 0.004934 | 0.0012366
20 | 0.004204 | 0.0010536
21 | 0.0036695 | 0.00091966
22 | 0.0084724 | 0.0021234
23 | 0.00255 | 0.00063908
24 | 0.00326 | 0.00081704
25 | 0.002156 | 0.00054034
26 | 0.0010883 | 0.00027276
27 | 0.0020388 | 0.00051096

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1