## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1631-102_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1631-102_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1631-102_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1631-102_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1631-102_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1631-102_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1631-102_0_4_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_1631-102_0_4_node_17 | 0.4 | n |  | TRUE
8 | bus_LV_1631-102_0_4_node_15 | 0.4 | n |  | TRUE
9 | bus_LV_1631-102_0_4_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_1631-102_0_4_node_18 | 0.4 | n |  | TRUE
11 | bus_LV_1631-102_0_4_node_16 | 0.4 | n |  | TRUE
12 | bus_LV_1631-102_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1631-102_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1631-102_0_4_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_1631-102_0_4_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_1631-102_0_4_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_1631-102_0_4_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_1631-102_0_4_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_1631-102_0_4_node_19 | 0.4 | n |  | TRUE
20 | bus_LV_1631-102_0_4_node_22 | 0.4 | n |  | TRUE
21 | bus_LV_1631-102_0_4_node_35 | 0.4 | n |  | TRUE
22 | bus_LV_1631-102_0_4_node_34 | 0.4 | n |  | TRUE
23 | bus_LV_1631-102_0_4_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_1631-102_0_4_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_1631-102_0_4_node_26 | 0.4 | n |  | TRUE
26 | bus_LV_1631-102_0_4_node_24 | 0.4 | n |  | TRUE
27 | bus_LV_1631-102_0_4_node_36 | 0.4 | n |  | TRUE
28 | bus_LV_1631-102_0_4_node_28 | 0.4 | n |  | TRUE
29 | bus_LV_1631-102_0_4_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_1631-102_0_4_node_25 | 0.4 | n |  | TRUE
31 | bus_LV_1631-102_0_4_node_27 | 0.4 | n |  | TRUE
32 | bus_LV_1631-102_0_4_node_33 | 0.4 | n |  | TRUE
33 | bus_LV_1631-102_0_4_node_32 | 0.4 | n |  | TRUE
34 | bus_LV_1631-102_0_4_node_29 | 0.4 | n |  | TRUE
35 | bus_LV_1631-102_0_4_node_30 | 0.4 | n |  | TRUE
36 | bus_MV_13_0_node_135 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1631-102_0_4_load_0 | 0 | 0.007826 | 0.0019614 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1631-102_0_4_load_5 | 5 | 0.0036965 | 0.00092644 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1631-102_0_4_load_7 | 6 | 0.0034152 | 0.00085592 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1631-102_0_4_load_17 | 7 | 0.0048997 | 0.001228 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1631-102_0_4_load_6 | 9 | 0.0070951 | 0.0017782 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1631-102_0_4_load_18 | 10 | 0.0045896 | 0.0011503 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1631-102_0_4_load_9 | 13 | 0.0024806 | 0.00062171 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1631-102_0_4_load_11 | 15 | 0.015783 | 0.0039555 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1631-102_0_4_load_12 | 16 | 0.0033645 | 0.00084323 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1631-102_0_4_load_13 | 17 | 0.0016527 | 0.0004142 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1631-102_0_4_load_14 | 18 | 0.0031894 | 0.00079933 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1631-102_0_4_load_19 | 19 | 0.0027787 | 0.00069641 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1631-102_0_4_load_35 | 21 | 0.0082261 | 0.0020617 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1631-102_0_4_load_34 | 22 | 0.012666 | 0.0031743 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1631-102_0_4_load_20 | 23 | 0.0033081 | 0.00082909 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1631-102_0_4_load_24 | 26 | 0.032709 | 0.0081978 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1631-102_0_4_load_36 | 27 | 0.0027903 | 0.00069932 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1631-102_0_4_load_23 | 29 | 0.022883 | 0.005735 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1631-102_0_4_load_27 | 31 | 0.011776 | 0.0029513 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1631-102_0_4_load_33 | 32 | 0.012486 | 0.0031292 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1631-102_0_4_load_32 | 33 | 0.012585 | 0.003154 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1631-102_0_4_load_29 | 34 | 0.010148 | 0.0025433 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 30 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1631-102_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.017789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1631-102_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.015435 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1631-102_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.005004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1631-102_0_4_line_3 | NAYY 4x150 SE | 1 | 4 | 0.072964 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1631-102_0_4_line_4 | NAYY 4x150 SE | 2 | 5 | 0.02401 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1631-102_0_4_line_5 | NAYY 4x150 SE | 3 | 6 | 0.018758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1631-102_0_4_line_6 | NAYY 4x150 SE | 4 | 7 | 0.036181 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1631-102_0_4_line_7 | NAYY 4x150 SE | 5 | 8 | 0.015629 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1631-102_0_4_line_8 | NAYY 4x150 SE | 6 | 9 | 0.0011981 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1631-102_0_4_line_9 | NAYY 4x150 SE | 7 | 10 | 0.0073066 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1631-102_0_4_line_10 | NAYY 4x150 SE | 8 | 11 | 0.003688 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1631-102_0_4_line_11 | NAYY 4x150 SE | 9 | 12 | 0.02334 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1631-102_0_4_line_12 | NAYY 4x150 SE | 11 | 19 | 0.043939 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1631-102_0_4_line_13 | NAYY 4x150 SE | 12 | 13 | 0.016389 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1631-102_0_4_line_14 | NAYY 4x150 SE | 12 | 14 | 0.022144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1631-102_0_4_line_15 | NAYY 4x150 SE | 13 | 15 | 0.0077338 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1631-102_0_4_line_16 | NAYY 4x150 SE | 14 | 16 | 0.0096975 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1631-102_0_4_line_17 | NAYY 4x150 SE | 16 | 17 | 0.0093652 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1631-102_0_4_line_18 | NAYY 4x150 SE | 17 | 18 | 0.0095947 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1631-102_0_4_line_19 | NAYY 4x150 SE | 19 | 23 | 0.0048243 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1631-102_0_4_line_20 | NAYY 4x150 SE | 20 | 21 | 0.011611 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1631-102_0_4_line_21 | NAYY 4x150 SE | 20 | 22 | 0.012157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1631-102_0_4_line_22 | NAYY 4x150 SE | 21 | 27 | 0.015981 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1631-102_0_4_line_23 | NAYY 4x150 SE | 22 | 28 | 0.0047015 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1631-102_0_4_line_24 | NAYY 4x150 SE | 23 | 24 | 0.015384 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1631-102_0_4_line_25 | NAYY 4x150 SE | 24 | 25 | 0.040631 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1631-102_0_4_line_26 | NAYY 4x150 SE | 25 | 26 | 0.030279 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1631-102_0_4_line_27 | NAYY 4x150 SE | 26 | 29 | 0.04837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
28 | LV_1631-102_0_4_line_28 | NAYY 4x150 SE | 28 | 32 | 0.019847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1631-102_0_4_line_29 | NAYY 4x150 SE | 28 | 30 | 0.01484 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1631-102_0_4_line_30 | NAYY 4x150 SE | 29 | 30 | 0.028216 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
31 | LV_1631-102_0_4_line_31 | NAYY 4x150 SE | 30 | 31 | 0.02567 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1631-102_0_4_line_32 | NAYY 4x150 SE | 32 | 33 | 0.02457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1631-102_0_4_line_33 | NAYY 4x150 SE | 33 | 35 | 0.018125 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1631-102_0_4_line_34 | NAYY 4x150 SE | 34 | 35 | 0.028396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1631-102_0_4_trafo_25 | 0.25 MVA 20/0.4 kV | 36 | 30 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2719069.9321 | 1198128.0556 | 2719056.5929 | 1198137.6191 | 2719055.4568 | 1198138.3943
1 | 2719042.7069 | 1198147.094 | 2719055.4568 | 1198138.3943
2 | 2719069.9321 | 1198128.0556 | 2719068.3125 | 1198123.3199
3 | 2719073.7225 | 1198186.7072 | 2719090.0834 | 1198179.1832 | 2719084.9465 | 1198165.9267 | 2719069.9321 | 1198128.0556
4 | 2719042.7069 | 1198147.094 | 2719025.1062 | 1198159.1079 | 2719023.0561 | 1198160.8649
5 | 2719068.3125 | 1198123.3199 | 2719062.5689 | 1198105.4628
6 | 2719073.7225 | 1198186.7072 | 2719045.4871 | 1198196.4298 | 2719039.3886 | 1198198.0821
7 | 2719011.61 | 1198171.2036 | 2719012.6966 | 1198170.9584 | 2719015.1065 | 1198168.916 | 2719018.627 | 1198164.6607 | 2719023.0561 | 1198160.8649
8 | 2719062.2021 | 1198104.3222 | 2719062.5689 | 1198105.4628
9 | 2719032.3362 | 1198199.9928 | 2719039.3886 | 1198198.0821
10 | 2719008.0687 | 1198170.7661 | 2719010.2936 | 1198171.511 | 2719011.61 | 1198171.2036
11 | 2719055.0557 | 1198082.1036 | 2719062.2021 | 1198104.3222
12 | 2719008.0687 | 1198170.7661 | 2719006.9774 | 1198173.1573 | 2719003.6094 | 1198185.8217 | 2719002.3248 | 1198188.7427 | 2718990.3363 | 1198210.6973
13 | 2719055.0557 | 1198082.1036 | 2719038.8441 | 1198084.5077
14 | 2719055.0557 | 1198082.1036 | 2719052.0356 | 1198072.7144 | 2719047.7859 | 1198061.188
15 | 2719031.194 | 1198085.6421 | 2719038.8441 | 1198084.5077
16 | 2719047.7859 | 1198061.188 | 2719038.1068 | 1198061.7853
17 | 2719028.7594 | 1198062.3622 | 2719038.1068 | 1198061.7853
18 | 2719019.1829 | 1198062.9531 | 2719028.7594 | 1198062.3622
19 | 2718988.0242 | 1198214.9315 | 2718990.3363 | 1198210.6973
20 | 2718976.7569 | 1198123.8198 | 2718971.2153 | 1198113.6166
21 | 2718976.7569 | 1198123.8198 | 2718966.2417 | 1198129.9208
22 | 2718963.5882 | 1198099.5734 | 2718971.2153 | 1198113.6166
23 | 2718962.1751 | 1198132.2802 | 2718966.2417 | 1198129.9208
24 | 2718985.8136 | 1198229.4438 | 2718984.8281 | 1198220.7845 | 2718988.0242 | 1198214.9315
25 | 2718985.8136 | 1198229.4438 | 2718975.7873 | 1198238.6843 | 2718971.5064 | 1198240.5783 | 2718969.0575 | 1198245.7333 | 2718963.45 | 1198246.5334 | 2718957.9196 | 1198247.2906 | 2718956.7287 | 1198242.0631
26 | 2718956.7287 | 1198242.0631 | 2718964.524 | 1198240.0389 | 2718967.053 | 1198236.2198 | 2718968.4047 | 1198229.931 | 2718971.2715 | 1198219.0913
27 | 2718971.2184 | 1198173.8411 | 2718979.2099 | 1198205.2947 | 2718971.2715 | 1198219.0913 | 2718971.2715 | 1198219.0913
28 | 2718962.1751 | 1198132.2802 | 2718945.0136 | 1198142.2488
29 | 2718966.2178 | 1198146.56 | 2718962.1751 | 1198132.2802
30 | 2718966.2178 | 1198146.56 | 2718968.941 | 1198156.7105 | 2718967.8435 | 1198160.5581 | 2718971.2184 | 1198173.8411
31 | 2718966.2178 | 1198146.56 | 2718963.6296 | 1198172.0938
32 | 2718923.7675 | 1198154.59 | 2718945.0136 | 1198142.2488
33 | 2718908.0944 | 1198163.694 | 2718923.7675 | 1198154.59
34 | 2718908.0944 | 1198163.694 | 2718914.0042 | 1198191.4683

## bus_geodata
| x | y | coords
0 | 2719055.4568 | 1198138.3943
1 | 2719069.9321 | 1198128.0556
2 | 2719042.7069 | 1198147.094
3 | 2719068.3125 | 1198123.3199
4 | 2719073.7225 | 1198186.7072
5 | 2719023.0561 | 1198160.8649
6 | 2719062.5689 | 1198105.4628
7 | 2719039.3886 | 1198198.0821
8 | 2719011.61 | 1198171.2036
9 | 2719062.2021 | 1198104.3222
10 | 2719032.3362 | 1198199.9928
11 | 2719008.0687 | 1198170.7661
12 | 2719055.0557 | 1198082.1036
13 | 2719038.8441 | 1198084.5077
14 | 2719047.7859 | 1198061.188
15 | 2719031.194 | 1198085.6421
16 | 2719038.1068 | 1198061.7853
17 | 2719028.7594 | 1198062.3622
18 | 2719019.1829 | 1198062.9531
19 | 2718990.3363 | 1198210.6973
20 | 2718976.7569 | 1198123.8198
21 | 2718971.2153 | 1198113.6166
22 | 2718966.2417 | 1198129.9208
23 | 2718988.0242 | 1198214.9315
24 | 2718985.8136 | 1198229.4438
25 | 2718956.7287 | 1198242.0631
26 | 2718971.2715 | 1198219.0913
27 | 2718963.5882 | 1198099.5734
28 | 2718962.1751 | 1198132.2802
29 | 2718971.2184 | 1198173.8411
30 | 2718966.2178 | 1198146.56
31 | 2718963.6296 | 1198172.0938
32 | 2718945.0136 | 1198142.2488
33 | 2718923.7675 | 1198154.59
34 | 2718914.0042 | 1198191.4683
35 | 2718908.0944 | 1198163.694
36 | 2718962.1751 | 1198132.2802

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97715 | -0.16004 | 0.007826 | 0.0019614
1 | 0.97594 | -0.1687 | 0 | 0
2 | 0.97838 | -0.15129 | 0 | 0
3 | 0.97567 | -0.17064 | 0 | 0
4 | 0.97493 | -0.17597 | 0 | 0
5 | 0.98028 | -0.13772 | 0.0036965 | 0.00092644
6 | 0.97465 | -0.17792 | 0.0034152 | 0.00085592
7 | 0.97443 | -0.17958 | 0.0048997 | 0.001228
8 | 0.98161 | -0.12831 | 0 | 0
9 | 0.9746 | -0.17834 | 0.0070951 | 0.0017782
10 | 0.97438 | -0.17993 | 0.0045896 | 0.0011503
11 | 0.98192 | -0.1261 | 0 | 0
12 | 0.97369 | -0.18484 | 0 | 0
13 | 0.97325 | -0.188 | 0.0024806 | 0.00062171
14 | 0.97342 | -0.18676 | 0 | 0
15 | 0.97307 | -0.18928 | 0.015783 | 0.0039555
16 | 0.97331 | -0.1876 | 0.0033645 | 0.00084323
17 | 0.97324 | -0.18808 | 0.0016527 | 0.0004142
18 | 0.9732 | -0.1884 | 0.0031894 | 0.00079933
19 | 0.98565 | -0.099808 | 0.0027787 | 0.00069641
20 | 0.9984 | -0.011192 | 0 | 0
21 | 0.99822 | -0.012473 | 0.0082261 | 0.0020617
22 | 0.99859 | -0.0098509 | 0.012666 | 0.0031743
23 | 0.98608 | -0.096796 | 0.0033081 | 0.00082909
24 | 0.98752 | -0.086687 | 0 | 0
25 | 0.99132 | -0.060128 | 0 | 0
26 | 0.99416 | -0.040467 | 0.032709 | 0.0081978
27 | 0.99815 | -0.01292 | 0.0027903 | 0.00069932
28 | 0.99875 | -0.0087365 | 0 | 0
29 | 0.99756 | -0.016899 | 0.022883 | 0.005735
30 | 1 | 0 | -0.19308 | -0.048439
31 | 0.99957 | -0.0030185 | 0.011776 | 0.0029513
32 | 0.99775 | -0.015738 | 0.012486 | 0.0031292
33 | 0.99695 | -0.021344 | 0.012585 | 0.003154
34 | 0.99628 | -0.026089 | 0.010148 | 0.0025433
35 | 0.99669 | -0.023192 | 0 | 0
36 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.046627 | 0.011704 | -0.046571 | -0.011683 | 5.5974e-05 | 2.1306e-05 | 0.071011 | 0.071011 | 0.071011 | 0.97715 | -0.16004 | 0.97594 | -0.1687 | 26.3005
1 | -0.054453 | -0.013665 | 0.05452 | 0.013691 | 6.6238e-05 | 2.5282e-05 | 0.082929 | 0.082929 | 0.082929 | 0.97715 | -0.16004 | 0.97838 | -0.15129 | 30.7144
2 | 0.037068 | 0.0093002 | -0.037058 | -0.0092964 | 9.9751e-06 | 3.7741e-06 | 0.056521 | 0.056521 | 0.056521 | 0.97594 | -0.1687 | 0.97567 | -0.17064 | 20.9336
3 | 0.0095039 | 0.0023824 | -0.0094943 | -0.0023796 | 9.5605e-06 | 2.7663e-06 | 0.014491 | 0.014491 | 0.014491 | 0.97594 | -0.1687 | 0.97493 | -0.17597 | 5.3671
4 | -0.05452 | -0.013691 | 0.054623 | 0.01373 | 0.00010304 | 3.9327e-05 | 0.082929 | 0.082929 | 0.082929 | 0.97838 | -0.15129 | 0.98028 | -0.13772 | 30.7143
5 | 0.037058 | 0.0092964 | -0.03702 | -0.0092823 | 3.7393e-05 | 1.4148e-05 | 0.056521 | 0.056521 | 0.056521 | 0.97567 | -0.17064 | 0.97465 | -0.17792 | 20.9336
6 | 0.0094943 | 0.0023796 | -0.0094896 | -0.0023782 | 4.741e-06 | 1.3725e-06 | 0.014491 | 0.014491 | 0.014491 | 0.97493 | -0.17597 | 0.97443 | -0.17958 | 5.3671
7 | -0.058319 | -0.014656 | 0.058396 | 0.014686 | 7.6452e-05 | 2.9207e-05 | 0.08854 | 0.08854 | 0.08854 | 0.98028 | -0.13772 | 0.98161 | -0.12831 | 32.7925
8 | 0.033605 | 0.0084264 | -0.033603 | -0.0084256 | 1.968e-06 | 7.4198e-07 | 0.051307 | 0.051307 | 0.051307 | 0.97465 | -0.17792 | 0.9746 | -0.17834 | 19.0025
9 | 0.0045899 | 0.0011503 | -0.0045896 | -0.0011503 | 2.2399e-07 | -4.8645e-09 | 0.007009 | 0.0070091 | 0.0070091 | 0.97443 | -0.17958 | 0.97438 | -0.17993 | 2.596
10 | -0.058396 | -0.014686 | 0.058414 | 0.014692 | 1.8041e-05 | 6.8921e-06 | 0.08854 | 0.08854 | 0.08854 | 0.98161 | -0.12831 | 0.98192 | -0.1261 | 32.7925
11 | 0.026508 | 0.0066474 | -0.026484 | -0.0066386 | 2.3858e-05 | 8.8855e-06 | 0.040474 | 0.040474 | 0.040474 | 0.9746 | -0.17834 | 0.97369 | -0.18484 | 14.9904
12 | -0.058414 | -0.014692 | 0.058629 | 0.014775 | 0.00021493 | 8.2109e-05 | 0.08854 | 0.088539 | 0.08854 | 0.98192 | -0.1261 | 0.98565 | -0.099808 | 32.7925
13 | 0.018274 | 0.004581 | -0.018266 | -0.0045782 | 7.976e-06 | 2.864e-06 | 0.027927 | 0.027927 | 0.027927 | 0.97369 | -0.18484 | 0.97325 | -0.188 | 10.3434
14 | 0.0082102 | 0.0020575 | -0.008208 | -0.002057 | 2.1753e-06 | 5.613e-07 | 0.012547 | 0.012547 | 0.012547 | 0.97369 | -0.18484 | 0.97342 | -0.18676 | 4.6471
15 | 0.015785 | 0.0039565 | -0.015783 | -0.0039555 | 2.811e-06 | 9.8505e-07 | 0.024135 | 0.024135 | 0.024135 | 0.97325 | -0.188 | 0.97307 | -0.18928 | 8.9387
16 | 0.008208 | 0.002057 | -0.0082071 | -0.0020567 | 9.5264e-07 | 2.4586e-07 | 0.012547 | 0.012547 | 0.012547 | 0.97342 | -0.18676 | 0.97331 | -0.1876 | 4.6471
17 | 0.0048425 | 0.0012135 | -0.0048422 | -0.0012135 | 3.203e-07 | 6.8065e-09 | 0.0074033 | 0.0074033 | 0.0074033 | 0.97331 | -0.1876 | 0.97324 | -0.18808 | 2.742
18 | 0.0031895 | 0.00079926 | -0.0031894 | -0.00079933 | 1.4238e-07 | -6.4464e-08 | 0.0048765 | 0.0048765 | 0.0048765 | 0.97324 | -0.18808 | 0.9732 | -0.1884 | 1.8061
19 | -0.061407 | -0.015471 | 0.061433 | 0.015481 | 2.5888e-05 | 9.8955e-06 | 0.092734 | 0.092734 | 0.092734 | 0.98565 | -0.099808 | 0.98608 | -0.096796 | 34.3461
20 | 0.011019 | 0.0027614 | -0.011017 | -0.0027608 | 1.9539e-06 | 5.997e-07 | 0.016422 | 0.016422 | 0.016422 | 0.9984 | -0.011192 | 0.99822 | -0.012473 | 6.0823
21 | -0.011019 | -0.0027614 | 0.011021 | 0.0027621 | 2.0458e-06 | 6.2783e-07 | 0.016422 | 0.016422 | 0.016422 | 0.9984 | -0.011192 | 0.99859 | -0.0098509 | 6.0822
22 | 0.0027905 | 0.00069917 | -0.0027903 | -0.00069932 | 1.7254e-07 | -1.4253e-07 | 0.0041596 | 0.0041597 | 0.0041597 | 0.99822 | -0.012473 | 0.99815 | -0.01292 | 1.5406
23 | -0.023686 | -0.0059364 | 0.02369 | 0.0059377 | 3.6547e-06 | 1.3441e-06 | 0.035295 | 0.035295 | 0.035295 | 0.99859 | -0.0098509 | 0.99875 | -0.0087365 | 13.0723
24 | -0.064741 | -0.01631 | 0.064833 | 0.016345 | 9.168e-05 | 3.5065e-05 | 0.097726 | 0.097726 | 0.097726 | 0.98608 | -0.096796 | 0.98752 | -0.086687 | 36.195
25 | -0.064833 | -0.016345 | 0.065075 | 0.016438 | 0.00024214 | 9.2609e-05 | 0.097726 | 0.097726 | 0.097726 | 0.98752 | -0.086687 | 0.99132 | -0.060128 | 36.1949
26 | -0.065075 | -0.016438 | 0.065256 | 0.016507 | 0.00018045 | 6.9011e-05 | 0.097726 | 0.097726 | 0.097726 | 0.99132 | -0.060128 | 0.99416 | -0.040467 | 36.1949
27 | -0.097965 | -0.024704 | 0.09829 | 0.024828 | 0.00032471 | 0.00012363 | 0.14668 | 0.14668 | 0.14668 | 0.99416 | -0.040467 | 0.99756 | -0.016899 | 27.1637
28 | 0.035277 | 0.0088478 | -0.035242 | -0.0088349 | 3.4213e-05 | 1.2899e-05 | 0.05256 | 0.05256 | 0.05256 | 0.99875 | -0.0087365 | 0.99775 | -0.015738 | 19.4668
29 | -0.058967 | -0.014786 | 0.059038 | 0.014813 | 7.1475e-05 | 2.7296e-05 | 0.087855 | 0.087855 | 0.087855 | 0.99875 | -0.0087365 | 1 | 0 | 32.539
30 | -0.12117 | -0.030563 | 0.12146 | 0.030673 | 0.00028782 | 0.00010996 | 0.18082 | 0.18082 | 0.18082 | 0.99756 | -0.016899 | 1 | 0 | 33.4847
31 | 0.011781 | 0.0029528 | -0.011776 | -0.0029513 | 4.9223e-06 | 1.5566e-06 | 0.01753 | 0.01753 | 0.01753 | 1 | 0 | 0.99957 | -0.0030185 | 6.4926
32 | 0.022757 | 0.0057057 | -0.022739 | -0.0056993 | 1.7661e-05 | 6.472e-06 | 0.03394 | 0.03394 | 0.03394 | 0.99775 | -0.015738 | 0.99695 | -0.021344 | 12.5703
33 | 0.010155 | 0.0025453 | -0.010152 | -0.0025445 | 2.5982e-06 | 7.6303e-07 | 0.015157 | 0.015157 | 0.015157 | 0.99695 | -0.021344 | 0.99669 | -0.023192 | 5.6136
34 | -0.010148 | -0.0025433 | 0.010152 | 0.0025445 | 4.0706e-06 | 1.1957e-06 | 0.015157 | 0.015157 | 0.015157 | 0.99628 | -0.026089 | 0.99669 | -0.023192 | 5.6136

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.19308 | 0.048439

## res_load
| p_mw | q_mvar
0 | 0.007826 | 0.0019614
1 | 0.0036965 | 0.00092644
2 | 0.0034152 | 0.00085592
3 | 0.0048997 | 0.001228
4 | 0.0070951 | 0.0017782
5 | 0.0045896 | 0.0011503
6 | 0.0024806 | 0.00062171
7 | 0.015783 | 0.0039555
8 | 0.0033645 | 0.00084323
9 | 0.0016527 | 0.0004142
10 | 0.0031894 | 0.00079933
11 | 0.0027787 | 0.00069641
12 | 0.0082261 | 0.0020617
13 | 0.012666 | 0.0031743
14 | 0.0033081 | 0.00082909
15 | 0.032709 | 0.0081978
16 | 0.0027903 | 0.00069932
17 | 0.022883 | 0.005735
18 | 0.011776 | 0.0029513
19 | 0.012486 | 0.0031292
20 | 0.012585 | 0.003154
21 | 0.010148 | 0.0025433

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1