## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1631-109_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1631-109_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1631-109_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1631-109_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1631-109_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1631-109_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1631-109_0_3_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_1631-109_0_3_node_31 | 0.4 | n |  | TRUE
8 | bus_LV_1631-109_0_3_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_1631-109_0_3_node_11 | 0.4 | n |  | TRUE
10 | bus_LV_1631-109_0_3_node_12 | 0.4 | n |  | TRUE
11 | bus_LV_1631-109_0_3_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_1631-109_0_3_node_15 | 0.4 | n |  | TRUE
13 | bus_LV_1631-109_0_3_node_19 | 0.4 | n |  | TRUE
14 | bus_LV_1631-109_0_3_node_17 | 0.4 | n |  | TRUE
15 | bus_LV_1631-109_0_3_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_1631-109_0_3_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_1631-109_0_3_node_23 | 0.4 | n |  | TRUE
18 | bus_LV_1631-109_0_3_node_25 | 0.4 | n |  | TRUE
19 | bus_LV_1631-109_0_3_node_28 | 0.4 | n |  | TRUE
20 | bus_LV_1631-109_0_3_node_27 | 0.4 | n |  | TRUE
21 | bus_LV_1631-109_0_3_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_1631-109_0_3_node_24 | 0.4 | n |  | TRUE
23 | bus_LV_1631-109_0_3_node_22 | 0.4 | n |  | TRUE
24 | bus_LV_1631-109_0_3_node_26 | 0.4 | n |  | TRUE
25 | bus_LV_1631-109_0_3_node_30 | 0.4 | n |  | TRUE
26 | bus_LV_1631-109_0_3_node_29 | 0.4 | n |  | TRUE
27 | bus_LV_1631-109_0_3_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_1631-109_0_3_node_21 | 0.4 | n |  | TRUE
29 | bus_MV_13_0_node_83 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1631-109_0_3_load_0 | 0 | 0.002044 | 0.00051228 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1631-109_0_3_load_1 | 1 | 0.004516 | 0.0011318 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1631-109_0_3_load_3 | 3 | 0.010583 | 0.0026522 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1631-109_0_3_load_4 | 4 | 0.0013584 | 0.00034046 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1631-109_0_3_load_7 | 6 | 0.010532 | 0.0026395 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1631-109_0_3_load_31 | 7 | 0.0011833 | 0.00029656 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1631-109_0_3_load_11 | 9 | 0.015304 | 0.0038356 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1631-109_0_3_load_9 | 11 | 0.022853 | 0.0057274 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1631-109_0_3_load_15 | 12 | 0.0046128 | 0.0011561 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1631-109_0_3_load_19 | 13 | 0.016415 | 0.0041141 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1631-109_0_3_load_17 | 14 | 0.01544 | 0.0038697 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1631-109_0_3_load_25 | 18 | 0.0096037 | 0.0024069 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1631-109_0_3_load_27 | 20 | 0.0032341 | 0.00081055 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1631-109_0_3_load_24 | 22 | 0.017688 | 0.004433 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1631-109_0_3_load_22 | 23 | 0.011177 | 0.0028011 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1631-109_0_3_load_26 | 24 | 0.0017166 | 0.00043022 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1631-109_0_3_load_30 | 25 | 0.011101 | 0.0027822 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1631-109_0_3_load_29 | 26 | 0.0041721 | 0.0010456 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1631-109_0_3_load_20 | 27 | 0.014268 | 0.003576 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1631-109_0_3_load_21 | 28 | 0.011641 | 0.0029175 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 10 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1631-109_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.055048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1631-109_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.01298 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1631-109_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.021033 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1631-109_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.022968 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1631-109_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.036621 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1631-109_0_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.0067681 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1631-109_0_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.011455 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1631-109_0_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.01888 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1631-109_0_3_line_8 | NAYY 4x150 SE | 8 | 9 | 0.014453 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1631-109_0_3_line_9 | NAYY 4x150 SE | 8 | 10 | 0.020448 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1631-109_0_3_line_10 | NAYY 4x150 SE | 8 | 11 | 0.011158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1631-109_0_3_line_11 | NAYY 4x150 SE | 9 | 12 | 0.012065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1631-109_0_3_line_12 | NAYY 4x150 SE | 10 | 13 | 0.010237 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1631-109_0_3_line_13 | NAYY 4x150 SE | 10 | 14 | 0.0086924 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1631-109_0_3_line_14 | NAYY 4x150 SE | 14 | 21 | 0.0040563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1631-109_0_3_line_15 | NAYY 4x150 SE | 15 | 16 | 0.14535 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1631-109_0_3_line_16 | NAYY 4x150 SE | 15 | 17 | 0.015849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1631-109_0_3_line_17 | NAYY 4x150 SE | 15 | 18 | 0.011015 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1631-109_0_3_line_18 | NAYY 4x150 SE | 16 | 19 | 0.017825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1631-109_0_3_line_19 | NAYY 4x150 SE | 16 | 20 | 0.045323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1631-109_0_3_line_20 | NAYY 4x150 SE | 17 | 22 | 0.022394 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1631-109_0_3_line_21 | NAYY 4x150 SE | 17 | 23 | 0.0073181 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1631-109_0_3_line_22 | NAYY 4x150 SE | 18 | 24 | 0.0086569 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1631-109_0_3_line_23 | NAYY 4x150 SE | 19 | 25 | 0.063317 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1631-109_0_3_line_24 | NAYY 4x150 SE | 19 | 26 | 0.035359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1631-109_0_3_line_25 | NAYY 4x150 SE | 21 | 27 | 0.0097409 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1631-109_0_3_line_26 | NAYY 4x150 SE | 21 | 28 | 0.016083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1631-109_0_3_line_27 | NAYY 4x150 SE | 23 | 28 | 0.0030184 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1631-109_0_3_trafo_12 | 0.25 MVA 20/0.4 kV | 29 | 10 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2720852.5709 | 1200618.2711 | 2720896.6315 | 1200651.2709
1 | 2720842.1814 | 1200610.4899 | 2720852.5709 | 1200618.2711
2 | 2720896.6315 | 1200651.2709 | 2720913.4665 | 1200663.8796
3 | 2720842.1814 | 1200610.4899 | 2720835.4436 | 1200613.4336 | 2720830.101 | 1200615.1602 | 2720820.4967 | 1200617.9454
4 | 2720842.1814 | 1200610.4899 | 2720833.7425 | 1200604.1701 | 2720830.5169 | 1200601.7587 | 2720846.5034 | 1200586.5707
5 | 2720918.8837 | 1200667.9369 | 2720913.4665 | 1200663.8796
6 | 2720846.5034 | 1200586.5707 | 2720855.8179 | 1200593.2751
7 | 2720933.9879 | 1200679.2645 | 2720930.5602 | 1200676.6821 | 2720918.8837 | 1200667.9369
8 | 2720933.9879 | 1200679.2645 | 2720924.9491 | 1200690.5423
9 | 2720947.7503 | 1200664.1096 | 2720933.9879 | 1200679.2645
10 | 2720933.9879 | 1200679.2645 | 2720942.9494 | 1200685.9116
11 | 2720924.9491 | 1200690.5423 | 2720917.404 | 1200699.9564
12 | 2720947.5768 | 1200653.8763 | 2720947.7503 | 1200664.1096
13 | 2720947.7503 | 1200664.1096 | 2720953.8766 | 1200670.2761
14 | 2720956.7354 | 1200673.1537 | 2720953.8766 | 1200670.2761
15 | 2720991.7847 | 1200670.6168 | 2720994.124 | 1200676.1794 | 2720996.22 | 1200678.7126 | 2720999.2435 | 1200680.5752 | 2721008.255 | 1200683.4265 | 2721011.4065 | 1200686.4814 | 2721017.612 | 1200696.6591 | 2721053.05 | 1200682.0771 | 2721060.3073 | 1200614.0738
16 | 2720991.7847 | 1200670.6168 | 2720989.5333 | 1200667.4801 | 2720986.3122 | 1200664.1012 | 2720982.753 | 1200661.6162 | 2720979.8024 | 1200661.045
17 | 2720991.7847 | 1200670.6168 | 2721001.1717 | 1200664.8527
18 | 2721057.0893 | 1200596.6401 | 2721059.6663 | 1200605.4989 | 2721060.3073 | 1200614.0738
19 | 2721060.3073 | 1200614.0738 | 2721065.4796 | 1200613.6115 | 2721094.9919 | 1200586.4192
20 | 2720976.2385 | 1200640.3797 | 2720981.8088 | 1200651.4674 | 2720982.1974 | 1200653.7102 | 2720979.8024 | 1200661.045
21 | 2720979.8024 | 1200661.045 | 2720974.8697 | 1200661.7123 | 2720972.8903 | 1200662.9611
22 | 2721001.1717 | 1200664.8527 | 2721008.5488 | 1200660.3228
23 | 2721007.8842 | 1200635.9616 | 2721014.4783 | 1200633.3487 | 2721022.4452 | 1200628.0061 | 2721057.0893 | 1200596.6401
24 | 2721057.0893 | 1200596.6401 | 2721046.9244 | 1200581.9344 | 2721037.177 | 1200567.4223
25 | 2720956.7354 | 1200673.1537 | 2720963.1275 | 1200680.5039
26 | 2720956.7354 | 1200673.1537 | 2720970.3376 | 1200664.5717
27 | 2720972.8903 | 1200662.9611 | 2720970.3376 | 1200664.5717

## bus_geodata
| x | y | coords
0 | 2720852.5709 | 1200618.2711
1 | 2720896.6315 | 1200651.2709
2 | 2720842.1814 | 1200610.4899
3 | 2720913.4665 | 1200663.8796
4 | 2720820.4967 | 1200617.9454
5 | 2720846.5034 | 1200586.5707
6 | 2720918.8837 | 1200667.9369
7 | 2720855.8179 | 1200593.2751
8 | 2720933.9879 | 1200679.2645
9 | 2720924.9491 | 1200690.5423
10 | 2720947.7503 | 1200664.1096
11 | 2720942.9494 | 1200685.9116
12 | 2720917.404 | 1200699.9564
13 | 2720947.5768 | 1200653.8763
14 | 2720953.8766 | 1200670.2761
15 | 2720991.7847 | 1200670.6168
16 | 2721060.3073 | 1200614.0738
17 | 2720979.8024 | 1200661.045
18 | 2721001.1717 | 1200664.8527
19 | 2721057.0893 | 1200596.6401
20 | 2721094.9919 | 1200586.4192
21 | 2720956.7354 | 1200673.1537
22 | 2720976.2385 | 1200640.3797
23 | 2720972.8903 | 1200662.9611
24 | 2721008.5488 | 1200660.3228
25 | 2721007.8842 | 1200635.9616
26 | 2721037.177 | 1200567.4223
27 | 2720963.1275 | 1200680.5039
28 | 2720970.3376 | 1200664.5717
29 | 2720947.5768 | 1200653.8763

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99623 | -0.026466 | 0.002044 | 0.00051228
1 | 0.99659 | -0.023922 | 0.004516 | 0.0011318
2 | 0.99618 | -0.026799 | 0 | 0
3 | 0.99686 | -0.021996 | 0.010583 | 0.0026522
4 | 0.99613 | -0.027113 | 0.0013584 | 0.00034046
5 | 0.99612 | -0.027236 | 0 | 0
6 | 0.99705 | -0.020657 | 0.010532 | 0.0026395
7 | 0.9961 | -0.027372 | 0.0011833 | 0.00029656
8 | 0.99787 | -0.014931 | 0 | 0
9 | 0.99746 | -0.017818 | 0.015304 | 0.0038356
10 | 1 | 0 | -0.19088 | -0.047715
11 | 0.9975 | -0.017488 | 0.022853 | 0.0057274
12 | 0.99738 | -0.018376 | 0.0046128 | 0.0011561
13 | 0.99976 | -0.0016776 | 0.016415 | 0.0041141
14 | 0.99875 | -0.0086931 | 0.01544 | 0.0038697
15 | 0.99521 | -0.03353 | 0 | 0
16 | 0.99134 | -0.060775 | 0 | 0
17 | 0.99589 | -0.028765 | 0 | 0
18 | 0.99503 | -0.034787 | 0.0096037 | 0.0024069
19 | 0.99095 | -0.063542 | 0 | 0
20 | 0.99113 | -0.062265 | 0.0032341 | 0.00081055
21 | 0.99826 | -0.01213 | 0 | 0
22 | 0.99532 | -0.032753 | 0.017688 | 0.004433
23 | 0.99639 | -0.025265 | 0.011177 | 0.0028011
24 | 0.99501 | -0.034937 | 0.0017166 | 0.00043022
25 | 0.98993 | -0.070695 | 0.011101 | 0.0027822
26 | 0.99073 | -0.065043 | 0.0041721 | 0.0010456
27 | 0.99806 | -0.013522 | 0.014268 | 0.003576
28 | 0.99664 | -0.023483 | 0.011641 | 0.0029175
29 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.004586 | -0.0011483 | 0.0045876 | 0.0011482 | 1.6115e-06 | -9.7197e-08 | 0.0068495 | 0.0068493 | 0.0068495 | 0.99623 | -0.026466 | 0.99659 | -0.023922 | 2.5369
1 | 0.002542 | 0.00063603 | -0.0025419 | -0.00063615 | 1.1675e-07 | -1.241e-07 | 0.0037965 | 0.0037966 | 0.0037966 | 0.99623 | -0.026466 | 0.99618 | -0.026799 | 1.4061
2 | -0.0091036 | -0.00228 | 0.009106 | 0.0022807 | 2.4247e-06 | 6.5846e-07 | 0.013592 | 0.013592 | 0.013592 | 0.99659 | -0.023922 | 0.99686 | -0.021996 | 5.0341
3 | 0.0013585 | 0.00034018 | -0.0013584 | -0.00034046 | 5.9012e-08 | -2.7631e-07 | 0.0020291 | 0.0020292 | 0.0020292 | 0.99618 | -0.026799 | 0.99613 | -0.027113 | 0.75157
4 | 0.0011834 | 0.00029597 | -0.0011833 | -0.00029642 | 7.1391e-08 | -4.4929e-07 | 0.0017674 | 0.0017676 | 0.0017676 | 0.99618 | -0.026799 | 0.99612 | -0.027236 | 0.65467
5 | -0.019689 | -0.0049329 | 0.019692 | 0.0049342 | 3.6476e-06 | 1.3147e-06 | 0.029389 | 0.029389 | 0.029389 | 0.99686 | -0.021996 | 0.99705 | -0.020657 | 10.8847
6 | 0.0011833 | 0.00029642 | -0.0011833 | -0.00029656 | 2.2334e-08 | -1.4052e-07 | 0.0017676 | 0.0017677 | 0.0017677 | 0.99612 | -0.027236 | 0.9961 | -0.027372 | 0.65469
7 | -0.030224 | -0.0075738 | 0.030248 | 0.0075827 | 2.397e-05 | 8.9727e-06 | 0.045106 | 0.045106 | 0.045106 | 0.99705 | -0.020657 | 0.99787 | -0.014931 | 16.7061
8 | 0.019925 | 0.0049946 | -0.019917 | -0.0049917 | 7.9623e-06 | 2.8737e-06 | 0.029713 | 0.029713 | 0.029713 | 0.99787 | -0.014931 | 0.99746 | -0.017818 | 11.0049
9 | -0.073034 | -0.018308 | 0.073186 | 0.018366 | 0.00015134 | 5.7942e-05 | 0.10891 | 0.10891 | 0.10891 | 0.99787 | -0.014931 | 1 | 0 | 40.3369
10 | 0.022861 | 0.0057304 | -0.022853 | -0.0057274 | 8.0912e-06 | 2.9663e-06 | 0.03409 | 0.03409 | 0.03409 | 0.99787 | -0.014931 | 0.9975 | -0.017488 | 12.626
11 | 0.0046131 | 0.0011561 | -0.0046128 | -0.0011561 | 3.5655e-07 | -2.0328e-08 | 0.0068819 | 0.006882 | 0.006882 | 0.99746 | -0.017818 | 0.99738 | -0.018376 | 2.5489
12 | 0.016419 | 0.0041154 | -0.016415 | -0.0041141 | 3.8131e-06 | 1.3323e-06 | 0.024432 | 0.024432 | 0.024432 | 1 | 0 | 0.99976 | -0.0016776 | 9.0489
13 | 0.10048 | 0.025234 | -0.10035 | -0.025188 | 0.00012127 | 4.653e-05 | 0.14953 | 0.14953 | 0.14953 | 1 | 0 | 0.99875 | -0.0086931 | 55.3805
14 | 0.084914 | 0.021318 | -0.084873 | -0.021302 | 4.0518e-05 | 1.5531e-05 | 0.12652 | 0.12652 | 0.12652 | 0.99875 | -0.0086931 | 0.99826 | -0.01213 | 46.8604
15 | 0.018596 | 0.0046684 | -0.018526 | -0.0046434 | 7.0129e-05 | 2.5091e-05 | 0.027807 | 0.027807 | 0.027807 | 0.99521 | -0.03353 | 0.99134 | -0.060775 | 10.2991
16 | -0.029918 | -0.0075061 | 0.029938 | 0.0075135 | 1.9792e-05 | 7.4063e-06 | 0.044736 | 0.044736 | 0.044736 | 0.99521 | -0.03353 | 0.99589 | -0.028765 | 16.5688
17 | 0.011322 | 0.0028377 | -0.01132 | -0.002837 | 1.9699e-06 | 6.1455e-07 | 0.016929 | 0.016929 | 0.016929 | 0.99521 | -0.03353 | 0.99503 | -0.034787 | 6.27
18 | 0.015291 | 0.0038331 | -0.015285 | -0.0038311 | 5.8596e-06 | 2.0239e-06 | 0.022952 | 0.022952 | 0.022952 | 0.99134 | -0.060775 | 0.99095 | -0.063542 | 8.5008
19 | 0.0032348 | 0.00081022 | -0.0032341 | -0.00081055 | 6.6673e-07 | -3.2779e-07 | 0.0048553 | 0.0048555 | 0.0048555 | 0.99134 | -0.060775 | 0.99113 | -0.062265 | 1.7983
20 | 0.017698 | 0.0044364 | -0.017688 | -0.004433 | 9.7712e-06 | 3.4669e-06 | 0.026443 | 0.026443 | 0.026443 | 0.99589 | -0.028765 | 0.99532 | -0.032753 | 9.7938
21 | -0.047635 | -0.01195 | 0.047659 | 0.011959 | 2.3136e-05 | 8.8032e-06 | 0.071179 | 0.071179 | 0.071179 | 0.99589 | -0.028765 | 0.99639 | -0.025265 | 26.3626
22 | 0.0017166 | 0.00043012 | -0.0017166 | -0.00043022 | 3.5599e-08 | -9.8752e-08 | 0.0025671 | 0.0025671 | 0.0025671 | 0.99503 | -0.034787 | 0.99501 | -0.034937 | 0.95079
23 | 0.011112 | 0.0027856 | -0.011101 | -0.0027822 | 1.1001e-05 | 3.4162e-06 | 0.016686 | 0.016686 | 0.016686 | 0.99095 | -0.063542 | 0.98993 | -0.070695 | 6.1802
24 | 0.004173 | 0.0010455 | -0.0041721 | -0.0010456 | 8.6633e-07 | -1.2222e-07 | 0.0062661 | 0.0062662 | 0.0062662 | 0.99095 | -0.063542 | 0.99073 | -0.065043 | 2.3208
25 | 0.014271 | 0.0035769 | -0.014268 | -0.003576 | 2.7506e-06 | 9.306e-07 | 0.021273 | 0.021273 | 0.021273 | 0.99826 | -0.01213 | 0.99806 | -0.013522 | 7.8788
26 | 0.070602 | 0.017725 | -0.070491 | -0.017683 | 0.00011117 | 4.255e-05 | 0.10525 | 0.10525 | 0.10525 | 0.99826 | -0.01213 | 0.99664 | -0.023483 | 38.9817
27 | -0.058835 | -0.01476 | 0.05885 | 0.014765 | 1.4543e-05 | 5.554e-06 | 0.08787 | 0.08787 | 0.08787 | 0.99639 | -0.025265 | 0.99664 | -0.023483 | 32.5445

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.19088 | 0.047715

## res_load
| p_mw | q_mvar
0 | 0.002044 | 0.00051228
1 | 0.004516 | 0.0011318
2 | 0.010583 | 0.0026522
3 | 0.0013584 | 0.00034046
4 | 0.010532 | 0.0026395
5 | 0.0011833 | 0.00029656
6 | 0.015304 | 0.0038356
7 | 0.022853 | 0.0057274
8 | 0.0046128 | 0.0011561
9 | 0.016415 | 0.0041141
10 | 0.01544 | 0.0038697
11 | 0.0096037 | 0.0024069
12 | 0.0032341 | 0.00081055
13 | 0.017688 | 0.004433
14 | 0.011177 | 0.0028011
15 | 0.0017166 | 0.00043022
16 | 0.011101 | 0.0027822
17 | 0.0041721 | 0.0010456
18 | 0.014268 | 0.003576
19 | 0.011641 | 0.0029175

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1