## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1631-110_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1631-110_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1631-110_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1631-110_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1631-110_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1631-110_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1631-110_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1631-110_0_3_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_1631-110_0_3_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_1631-110_0_3_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_1631-110_0_3_node_12 | 0.4 | n |  | TRUE
11 | bus_LV_1631-110_0_3_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_1631-110_0_3_node_13 | 0.4 | n |  | TRUE
13 | bus_LV_1631-110_0_3_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_1631-110_0_3_node_34 | 0.4 | n |  | TRUE
15 | bus_LV_1631-110_0_3_node_35 | 0.4 | n |  | TRUE
16 | bus_LV_1631-110_0_3_node_32 | 0.4 | n |  | TRUE
17 | bus_LV_1631-110_0_3_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_1631-110_0_3_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_1631-110_0_3_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_1631-110_0_3_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_1631-110_0_3_node_21 | 0.4 | n |  | TRUE
22 | bus_LV_1631-110_0_3_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_1631-110_0_3_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_1631-110_0_3_node_52 | 0.4 | n |  | TRUE
25 | bus_LV_1631-110_0_3_node_44 | 0.4 | n |  | TRUE
26 | bus_LV_1631-110_0_3_node_45 | 0.4 | n |  | TRUE
27 | bus_LV_1631-110_0_3_node_43 | 0.4 | n |  | TRUE
28 | bus_LV_1631-110_0_3_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_1631-110_0_3_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_1631-110_0_3_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_1631-110_0_3_node_25 | 0.4 | n |  | TRUE
32 | bus_LV_1631-110_0_3_node_26 | 0.4 | n |  | TRUE
33 | bus_LV_1631-110_0_3_node_27 | 0.4 | n |  | TRUE
34 | bus_LV_1631-110_0_3_node_28 | 0.4 | n |  | TRUE
35 | bus_LV_1631-110_0_3_node_30 | 0.4 | n |  | TRUE
36 | bus_LV_1631-110_0_3_node_36 | 0.4 | n |  | TRUE
37 | bus_LV_1631-110_0_3_node_33 | 0.4 | n |  | TRUE
38 | bus_LV_1631-110_0_3_node_29 | 0.4 | n |  | TRUE
39 | bus_LV_1631-110_0_3_node_37 | 0.4 | n |  | TRUE
40 | bus_LV_1631-110_0_3_node_38 | 0.4 | n |  | TRUE
41 | bus_LV_1631-110_0_3_node_31 | 0.4 | n |  | TRUE
42 | bus_LV_1631-110_0_3_node_41 | 0.4 | n |  | TRUE
43 | bus_LV_1631-110_0_3_node_39 | 0.4 | n |  | TRUE
44 | bus_LV_1631-110_0_3_node_51 | 0.4 | n |  | TRUE
45 | bus_LV_1631-110_0_3_node_42 | 0.4 | n |  | TRUE
46 | bus_LV_1631-110_0_3_node_40 | 0.4 | n |  | TRUE
47 | bus_LV_1631-110_0_3_node_50 | 0.4 | n |  | TRUE
48 | bus_LV_1631-110_0_3_node_48 | 0.4 | n |  | TRUE
49 | bus_LV_1631-110_0_3_node_46 | 0.4 | n |  | TRUE
50 | bus_LV_1631-110_0_3_node_47 | 0.4 | n |  | TRUE
51 | bus_LV_1631-110_0_3_node_49 | 0.4 | n |  | TRUE
52 | bus_LV_1631-110_0_3_node_53 | 0.4 | n |  | TRUE
53 | bus_MV_13_0_node_32 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1631-110_0_3_load_0 | 0 | 0.014452 | 0.003622 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1631-110_0_3_load_1 | 1 | 0.019505 | 0.0048884 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1631-110_0_3_load_3 | 3 | 0.0034063 | 0.0008537 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1631-110_0_3_load_5 | 5 | 0.00086912 | 0.00021782 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1631-110_0_3_load_7 | 7 | 0.017547 | 0.0043978 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1631-110_0_3_load_11 | 8 | 0.0080675 | 0.0020219 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1631-110_0_3_load_8 | 9 | 0.0014938 | 0.00037438 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1631-110_0_3_load_12 | 10 | 0.0036623 | 0.00091785 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1631-110_0_3_load_9 | 11 | 0.0029386 | 0.00073649 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1631-110_0_3_load_13 | 12 | 0.002096 | 0.00052531 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1631-110_0_3_load_14 | 13 | 0.0017715 | 0.00044397 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1631-110_0_3_load_32 | 16 | 0.0036321 | 0.00091028 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1631-110_0_3_load_15 | 17 | 0.0053332 | 0.0013366 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1631-110_0_3_load_17 | 19 | 0.0027457 | 0.00068814 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1631-110_0_3_load_21 | 21 | 0.0034894 | 0.00087453 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1631-110_0_3_load_18 | 22 | 0.0052113 | 0.0013061 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1631-110_0_3_load_20 | 23 | 0.0088519 | 0.0022185 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1631-110_0_3_load_52 | 24 | 0.0063347 | 0.0015876 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1631-110_0_3_load_45 | 26 | 0.0019129 | 0.00047942 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1631-110_0_3_load_43 | 27 | 0.0044982 | 0.0011274 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1631-110_0_3_load_22 | 28 | 0.0076917 | 0.0019277 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1631-110_0_3_load_24 | 30 | 0.017966 | 0.0045026 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1631-110_0_3_load_25 | 31 | 0.0065575 | 0.0016435 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1631-110_0_3_load_26 | 32 | 0.0017632 | 0.0004419 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1631-110_0_3_load_30 | 35 | 0.007445 | 0.0018659 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1631-110_0_3_load_36 | 36 | 0.0022971 | 0.00057571 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1631-110_0_3_load_33 | 37 | 0.0044903 | 0.0011254 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1631-110_0_3_load_37 | 39 | 0.0023083 | 0.00057851 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1631-110_0_3_load_38 | 40 | 0.009286 | 0.0023273 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1631-110_0_3_load_31 | 41 | 0.0051519 | 0.0012912 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1631-110_0_3_load_39 | 43 | 0.0029012 | 0.00072711 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1631-110_0_3_load_51 | 44 | 0.0047629 | 0.0011937 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1631-110_0_3_load_42 | 45 | 0.010558 | 0.002646 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1631-110_0_3_load_40 | 46 | 0.0059605 | 0.0014938 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1631-110_0_3_load_46 | 49 | 0.0062231 | 0.0015597 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1631-110_0_3_load_47 | 50 | 0.0096715 | 0.0024239 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1631-110_0_3_load_53 | 52 | 0.018126 | 0.0045427 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 37 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1631-110_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.039705 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1631-110_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.022188 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1631-110_0_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.011825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1631-110_0_3_line_3 | NAYY 4x150 SE | 3 | 4 | 0.018202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1631-110_0_3_line_4 | NAYY 4x150 SE | 4 | 5 | 0.048715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1631-110_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.043901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1631-110_0_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.014827 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1631-110_0_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.018821 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1631-110_0_3_line_8 | NAYY 4x150 SE | 7 | 9 | 0.00010452 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1631-110_0_3_line_9 | NAYY 4x150 SE | 8 | 10 | 0.035586 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1631-110_0_3_line_10 | NAYY 4x150 SE | 9 | 11 | 0.053678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1631-110_0_3_line_11 | NAYY 4x150 SE | 10 | 12 | 0.033651 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1631-110_0_3_line_12 | NAYY 4x150 SE | 12 | 13 | 0.0019042 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1631-110_0_3_line_13 | NAYY 4x150 SE | 13 | 14 | 0.01123 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1631-110_0_3_line_14 | NAYY 4x150 SE | 14 | 15 | 0.018444 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1631-110_0_3_line_15 | NAYY 4x150 SE | 14 | 16 | 0.017602 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1631-110_0_3_line_16 | NAYY 4x150 SE | 15 | 44 | 0.025329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1631-110_0_3_line_17 | NAYY 4x150 SE | 16 | 41 | 0.0094271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1631-110_0_3_line_18 | NAYY 4x150 SE | 17 | 18 | 0.022268 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1631-110_0_3_line_19 | NAYY 4x150 SE | 17 | 19 | 0.095754 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1631-110_0_3_line_20 | NAYY 4x150 SE | 18 | 20 | 0.11951 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1631-110_0_3_line_21 | NAYY 4x150 SE | 20 | 21 | 0.011314 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1631-110_0_3_line_22 | NAYY 4x150 SE | 20 | 22 | 0.034938 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1631-110_0_3_line_23 | NAYY 4x150 SE | 21 | 24 | 0.031152 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1631-110_0_3_line_24 | NAYY 4x150 SE | 21 | 25 | 0.013065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1631-110_0_3_line_25 | NAYY 4x150 SE | 22 | 23 | 0.015188 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1631-110_0_3_line_26 | NAYY 4x150 SE | 25 | 26 | 0.018112 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1631-110_0_3_line_27 | NAYY 4x150 SE | 25 | 27 | 0.012275 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1631-110_0_3_line_28 | NAYY 4x150 SE | 26 | 49 | 0.0020738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1631-110_0_3_line_29 | NAYY 4x150 SE | 27 | 43 | 0.0092378 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1631-110_0_3_line_30 | NAYY 4x150 SE | 28 | 29 | 0.0066173 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1631-110_0_3_line_31 | NAYY 4x150 SE | 28 | 30 | 0.032417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1631-110_0_3_line_32 | NAYY 4x150 SE | 29 | 31 | 0.033222 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1631-110_0_3_line_33 | NAYY 4x150 SE | 29 | 32 | 0.014536 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1631-110_0_3_line_34 | NAYY 4x150 SE | 32 | 33 | 0.019574 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1631-110_0_3_line_35 | NAYY 4x150 SE | 33 | 34 | 0.033764 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1631-110_0_3_line_36 | NAYY 4x150 SE | 33 | 35 | 0.017413 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1631-110_0_3_line_37 | NAYY 4x150 SE | 34 | 36 | 0.015888 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1631-110_0_3_line_38 | NAYY 4x150 SE | 34 | 37 | 0.007082 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
39 | LV_1631-110_0_3_line_39 | NAYY 4x150 SE | 35 | 40 | 0.0016412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1631-110_0_3_line_40 | NAYY 4x150 SE | 36 | 38 | 0.0033305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1631-110_0_3_line_41 | NAYY 4x150 SE | 37 | 41 | 0.009572 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1631-110_0_3_line_42 | NAYY 4x150 SE | 38 | 39 | 0.0052843 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1631-110_0_3_line_43 | NAYY 4x150 SE | 39 | 42 | 0.018329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1631-110_0_3_line_44 | NAYY 4x150 SE | 40 | 43 | 0.01868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1631-110_0_3_line_45 | NAYY 4x150 SE | 42 | 45 | 0.074185 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1631-110_0_3_line_46 | NAYY 4x150 SE | 42 | 46 | 0.062305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1631-110_0_3_line_47 | NAYY 4x150 SE | 45 | 47 | 0.0018495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1631-110_0_3_line_48 | NAYY 4x150 SE | 47 | 48 | 0.039774 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1631-110_0_3_line_49 | NAYY 4x150 SE | 48 | 51 | 0.023107 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1631-110_0_3_line_50 | NAYY 4x150 SE | 48 | 50 | 0.026242 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1631-110_0_3_line_51 | NAYY 4x150 SE | 51 | 52 | 0.03445 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1631-110_0_3_trafo_33 | 0.25 MVA 20/0.4 kV | 53 | 37 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2721030.0681 | 1201255.2336 | 2720996.0993 | 1201275.7915
1 | 2721049.0502 | 1201243.7457 | 2721030.0681 | 1201255.2336
2 | 2721049.0502 | 1201243.7457 | 2721043.2773 | 1201233.4259
3 | 2721034.3912 | 1201217.5405 | 2721043.2773 | 1201233.4259
4 | 2721034.3912 | 1201217.5405 | 2721008.6203 | 1201233.5415 | 2721005.7009 | 1201234.4497 | 2721002.5034 | 1201234.4294 | 2720999.0336 | 1201233.1916 | 2720996.7776 | 1201231.4223 | 2720993.8829 | 1201226.6577
5 | 2721070.4439 | 1201192.3966 | 2721049.0855 | 1201208.1978 | 2721034.3912 | 1201217.5405
6 | 2720986.1843 | 1201213.9863 | 2720993.8829 | 1201226.6577
7 | 2721070.4439 | 1201192.3966 | 2721077.5842 | 1201187.6044 | 2721085.1257 | 1201180.7049
8 | 2720986.1843 | 1201213.9863 | 2720986.13 | 1201213.8969
9 | 2721085.1257 | 1201180.7049 | 2721098.7019 | 1201168.2846 | 2721111.4188 | 1201156.7258
10 | 2720954.7046 | 1201170.5621 | 2720968.7438 | 1201191.881 | 2720971.9342 | 1201195.6373 | 2720981.5249 | 1201206.3171 | 2720986.13 | 1201213.8969
11 | 2721135.8525 | 1201133.6139 | 2721129.5991 | 1201140.2011 | 2721111.4188 | 1201156.7258
12 | 2721137.1636 | 1201132.233 | 2721135.8525 | 1201133.6139
13 | 2721144.8957 | 1201124.0882 | 2721137.1636 | 1201132.233
14 | 2721144.8957 | 1201124.0882 | 2721141.4366 | 1201121.1937 | 2721130.7144 | 1201112.2475
15 | 2721144.8957 | 1201124.0882 | 2721158.4059 | 1201135.3709
16 | 2721130.7144 | 1201112.2475 | 2721134.6119 | 1201108.5459 | 2721142.6695 | 1201103.2053 | 2721146.3809 | 1201101.546 | 2721152.5762 | 1201100.5598
17 | 2721165.6415 | 1201141.4136 | 2721158.4059 | 1201135.3709
18 | 2721342.3488 | 1200981.7443 | 2721356.206 | 1200973.931 | 2721361.1615 | 1200969.9447
19 | 2721361.1615 | 1200969.9447 | 2721452.7342 | 1200997.932
20 | 2721263.8037 | 1201071.8167 | 2721342.3488 | 1200981.7443
21 | 2721256.7822 | 1201080.4918 | 2721260.002 | 1201077.5438 | 2721262.5106 | 1201074.7482 | 2721263.8037 | 1201071.8167
22 | 2721263.8037 | 1201071.8167 | 2721263.3446 | 1201068.5494 | 2721261.5609 | 1201066.0225 | 2721241.2023 | 1201046.013
23 | 2721256.7822 | 1201080.4918 | 2721278.4227 | 1201102.9587
24 | 2721247.1306 | 1201089.3247 | 2721256.7822 | 1201080.4918
25 | 2721230.3704 | 1201035.3669 | 2721241.2023 | 1201046.013
26 | 2721247.1306 | 1201089.3247 | 2721259.2437 | 1201102.7902
27 | 2721247.1306 | 1201089.3247 | 2721238.0776 | 1201097.614
28 | 2721260.6306 | 1201104.332 | 2721259.2437 | 1201102.7902
29 | 2721231.2644 | 1201103.8524 | 2721238.0776 | 1201097.614
30 | 2721181.1794 | 1201104.4982 | 2721182.2819 | 1201100.4509 | 2721183.0788 | 1201098.1632
31 | 2721185.1433 | 1201067.8848 | 2721188.6661 | 1201072.8932 | 2721189.1956 | 1201076.818 | 2721188.8472 | 1201081.6034 | 2721183.0788 | 1201098.1632
32 | 2721181.1794 | 1201104.4982 | 2721190.0385 | 1201098.3177 | 2721206.8788 | 1201083.4371
33 | 2721181.1794 | 1201104.4982 | 2721181.6673 | 1201108.222 | 2721184.9093 | 1201112.0572 | 2721189.1203 | 1201115.9846
34 | 2721203.4345 | 1201129.3346 | 2721189.1203 | 1201115.9846
35 | 2721178.4242 | 1201152.0887 | 2721203.4345 | 1201129.3346
36 | 2721203.4345 | 1201129.3346 | 2721216.277 | 1201117.5755
37 | 2721178.4242 | 1201152.0887 | 2721190.6633 | 1201162.2189
38 | 2721178.4242 | 1201152.0887 | 2721172.9885 | 1201147.5492
39 | 2721216.277 | 1201117.5755 | 2721217.4875 | 1201116.4672
40 | 2721193.2289 | 1201164.3425 | 2721190.6633 | 1201162.2189
41 | 2721165.6415 | 1201141.4136 | 2721172.9885 | 1201147.5492
42 | 2721193.2289 | 1201164.3425 | 2721197.2994 | 1201167.7122
43 | 2721211.4183 | 1201179.4004 | 2721197.2994 | 1201167.7122
44 | 2721231.2644 | 1201103.8524 | 2721217.4875 | 1201116.4672
45 | 2721211.4183 | 1201179.4004 | 2721242.9152 | 1201205.8034 | 2721268.4035 | 1201226.898
46 | 2721211.4183 | 1201179.4004 | 2721236.1685 | 1201154.8287 | 2721246.7394 | 1201147.2153 | 2721259.1161 | 1201139.8516
47 | 2721269.8283 | 1201228.0772 | 2721268.4035 | 1201226.898
48 | 2721238.6865 | 1201252.8192 | 2721249.1034 | 1201244.5355 | 2721269.8283 | 1201228.0772
49 | 2721238.6865 | 1201252.8192 | 2721220.666 | 1201267.3421
50 | 2721238.6865 | 1201252.8192 | 2721218.8014 | 1201235.6957
51 | 2721220.666 | 1201267.3421 | 2721194.0434 | 1201245.3858

## bus_geodata
| x | y | coords
0 | 2721030.0681 | 1201255.2336
1 | 2720996.0993 | 1201275.7915
2 | 2721049.0502 | 1201243.7457
3 | 2721043.2773 | 1201233.4259
4 | 2721034.3911 | 1201217.5405
5 | 2720993.8828 | 1201226.6577
6 | 2721070.4439 | 1201192.3966
7 | 2720986.1843 | 1201213.9863
8 | 2721085.1257 | 1201180.7049
9 | 2720986.13 | 1201213.8969
10 | 2721111.4188 | 1201156.7258
11 | 2720954.7046 | 1201170.5621
12 | 2721135.8525 | 1201133.6139
13 | 2721137.1636 | 1201132.233
14 | 2721144.8957 | 1201124.0882
15 | 2721130.7144 | 1201112.2475
16 | 2721158.4059 | 1201135.3709
17 | 2721361.1615 | 1200969.9447
18 | 2721342.3488 | 1200981.7443
19 | 2721452.7342 | 1200997.932
20 | 2721263.8037 | 1201071.8167
21 | 2721256.7822 | 1201080.4918
22 | 2721241.2023 | 1201046.013
23 | 2721230.3704 | 1201035.3669
24 | 2721278.4227 | 1201102.9587
25 | 2721247.1306 | 1201089.3247
26 | 2721259.2437 | 1201102.7902
27 | 2721238.0776 | 1201097.614
28 | 2721183.0788 | 1201098.1632
29 | 2721181.1794 | 1201104.4982
30 | 2721185.1433 | 1201067.8848
31 | 2721206.8788 | 1201083.4371
32 | 2721189.1203 | 1201115.9846
33 | 2721203.4345 | 1201129.3346
34 | 2721178.4242 | 1201152.0887
35 | 2721216.277 | 1201117.5755
36 | 2721190.6633 | 1201162.219
37 | 2721172.9885 | 1201147.5492
38 | 2721193.2289 | 1201164.3425
39 | 2721197.2994 | 1201167.7122
40 | 2721217.4875 | 1201116.4672
41 | 2721165.6415 | 1201141.4136
42 | 2721211.4183 | 1201179.4004
43 | 2721231.2644 | 1201103.8524
44 | 2721152.5762 | 1201100.5598
45 | 2721268.4035 | 1201226.898
46 | 2721259.1161 | 1201139.8516
47 | 2721269.8283 | 1201228.0772
48 | 2721238.6865 | 1201252.8192
49 | 2721260.6306 | 1201104.332
50 | 2721218.8014 | 1201235.6957
51 | 2721220.666 | 1201267.3421
52 | 2721194.0434 | 1201245.3858
53 | 2721178.4242 | 1201152.0887

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97888 | -0.14812 | 0.014452 | 0.003622
1 | 0.97775 | -0.15619 | 0.019505 | 0.0048884
2 | 0.97998 | -0.14028 | 0 | 0
3 | 0.98056 | -0.13611 | 0.0034063 | 0.0008537
4 | 0.98155 | -0.12905 | 0 | 0
5 | 0.97993 | -0.14061 | 0.00086912 | 0.00021782
6 | 0.9854 | -0.10177 | 0 | 0
7 | 0.97946 | -0.144 | 0.017547 | 0.0043978
8 | 0.98705 | -0.090133 | 0.0080675 | 0.0020219
9 | 0.97946 | -0.144 | 0.0014938 | 0.00037438
10 | 0.99059 | -0.065322 | 0.0036623 | 0.00091785
11 | 0.97923 | -0.14564 | 0.0029386 | 0.00073649
12 | 0.99411 | -0.040776 | 0.002096 | 0.00052531
13 | 0.99431 | -0.039352 | 0.0017715 | 0.00044397
14 | 0.99555 | -0.030764 | 0 | 0
15 | 0.99542 | -0.03165 | 0 | 0
16 | 0.99761 | -0.016506 | 0.0036321 | 0.00091028
17 | 0.98754 | -0.087531 | 0.0053332 | 0.0013366
18 | 0.9878 | -0.085688 | 0 | 0
19 | 0.98716 | -0.090227 | 0.0027457 | 0.00068814
20 | 0.98919 | -0.075805 | 0 | 0
21 | 0.98955 | -0.073248 | 0.0034894 | 0.00087453
22 | 0.98848 | -0.080822 | 0.0052113 | 0.0013061
23 | 0.98829 | -0.082195 | 0.0088519 | 0.0022185
24 | 0.98927 | -0.07526 | 0.0063347 | 0.0015876
25 | 0.99015 | -0.06899 | 0 | 0
26 | 0.98994 | -0.07049 | 0.0019129 | 0.00047942
27 | 0.99086 | -0.063978 | 0.0044982 | 0.0011274
28 | 0.99261 | -0.051706 | 0.0076917 | 0.0019277
29 | 0.99285 | -0.049986 | 0 | 0
30 | 0.99177 | -0.057611 | 0.017966 | 0.0045026
31 | 0.99254 | -0.052193 | 0.0065575 | 0.0016435
32 | 0.99352 | -0.045247 | 0.0017632 | 0.0004419
33 | 0.99448 | -0.038528 | 0 | 0
34 | 0.99925 | -0.0052065 | 0 | 0
35 | 0.99287 | -0.04984 | 0.007445 | 0.0018659
36 | 0.99813 | -0.012988 | 0.0022971 | 0.00057571
37 | 1 | 0 | -0.24003 | -0.060306
38 | 0.99791 | -0.014545 | 0 | 0
39 | 0.99756 | -0.017017 | 0.0023083 | 0.00057851
40 | 0.99274 | -0.050784 | 0.009286 | 0.0023273
41 | 0.99876 | -0.0085509 | 0.0051519 | 0.0012912
42 | 0.99639 | -0.025177 | 0 | 0
43 | 0.99146 | -0.059789 | 0.0029012 | 0.00072711
44 | 0.99525 | -0.032865 | 0.0047629 | 0.0011937
45 | 0.99229 | -0.053911 | 0.010558 | 0.002646
46 | 0.99586 | -0.028915 | 0.0059605 | 0.0014938
47 | 0.99222 | -0.054432 | 0 | 0
48 | 0.99063 | -0.065662 | 0 | 0
49 | 0.98992 | -0.070622 | 0.0062231 | 0.0015597
50 | 0.99026 | -0.068245 | 0.0096715 | 0.0024239
51 | 0.99002 | -0.069926 | 0 | 0
52 | 0.98912 | -0.07629 | 0.018126 | 0.0045427
53 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.019527 | 0.0048963 | -0.019505 | -0.0048884 | 2.1831e-05 | 7.8981e-06 | 0.029684 | 0.029684 | 0.029684 | 0.97888 | -0.14812 | 0.97775 | -0.15619 | 10.9942
1 | -0.033979 | -0.0085183 | 0.034016 | 0.0085322 | 3.6938e-05 | 1.3928e-05 | 0.051653 | 0.051652 | 0.051653 | 0.97888 | -0.14812 | 0.97998 | -0.14028 | 19.1306
2 | -0.034016 | -0.0085322 | 0.034035 | 0.0085396 | 1.9686e-05 | 7.4225e-06 | 0.051652 | 0.051652 | 0.051652 | 0.97998 | -0.14028 | 0.98056 | -0.13611 | 19.1306
3 | -0.037442 | -0.0093933 | 0.037478 | 0.0094072 | 3.6671e-05 | 1.3875e-05 | 0.056822 | 0.056821 | 0.056822 | 0.98056 | -0.13611 | 0.98155 | -0.12905 | 21.045
4 | 0.022897 | 0.0057433 | -0.02286 | -0.0057298 | 3.6629e-05 | 1.3473e-05 | 0.034713 | 0.034713 | 0.034713 | 0.98155 | -0.12905 | 0.97993 | -0.14061 | 12.8566
5 | -0.060375 | -0.015151 | 0.060604 | 0.015238 | 0.00022952 | 8.772e-05 | 0.091534 | 0.091534 | 0.091534 | 0.98155 | -0.12905 | 0.9854 | -0.10177 | 33.9015
6 | 0.021991 | 0.005512 | -0.02198 | -0.0055082 | 1.0317e-05 | 3.7813e-06 | 0.033393 | 0.033393 | 0.033393 | 0.97993 | -0.14061 | 0.97946 | -0.144 | 12.3678
7 | -0.060604 | -0.015238 | 0.060703 | 0.015276 | 9.8397e-05 | 3.7605e-05 | 0.091534 | 0.091534 | 0.091534 | 0.9854 | -0.10177 | 0.98705 | -0.090133 | 33.9014
8 | 0.0044331 | 0.0011105 | -0.0044331 | -0.0011105 | 2.9583e-09 | -1.7802e-10 | 0.0067346 | 0.0067346 | 0.0067346 | 0.97946 | -0.144 | 0.97946 | -0.144 | 2.4943
9 | -0.06877 | -0.017298 | 0.069009 | 0.017389 | 0.00023877 | 9.1378e-05 | 0.1037 | 0.1037 | 0.1037 | 0.98705 | -0.090133 | 0.99059 | -0.065322 | 38.4058
10 | 0.0029393 | 0.00073607 | -0.0029386 | -0.00073649 | 6.6788e-07 | -4.1855e-07 | 0.0044653 | 0.0044655 | 0.0044655 | 0.97946 | -0.144 | 0.97923 | -0.14564 | 1.6539
11 | -0.072671 | -0.018307 | 0.072922 | 0.018403 | 0.00025038 | 9.5865e-05 | 0.1092 | 0.1092 | 0.1092 | 0.99059 | -0.065322 | 0.99411 | -0.040776 | 40.4433
12 | -0.075018 | -0.018928 | 0.075033 | 0.018934 | 1.4994e-05 | 5.7422e-06 | 0.11233 | 0.11233 | 0.11233 | 0.99411 | -0.040776 | 0.99431 | -0.039352 | 41.6052
13 | -0.076804 | -0.019378 | 0.076897 | 0.019413 | 9.2654e-05 | 3.549e-05 | 0.11499 | 0.11499 | 0.11499 | 0.99431 | -0.039352 | 0.99555 | -0.030764 | 42.5871
14 | 0.0047643 | 0.0011937 | -0.0047637 | -0.0011937 | 5.8361e-07 | -1.5329e-08 | 0.0071209 | 0.007121 | 0.007121 | 0.99555 | -0.030764 | 0.99542 | -0.03165 | 2.6374
15 | -0.081661 | -0.020607 | 0.081825 | 0.02067 | 0.00016376 | 6.2757e-05 | 0.12211 | 0.12211 | 0.12211 | 0.99555 | -0.030764 | 0.99761 | -0.016506 | 45.2244
16 | 0.0047637 | 0.0011937 | -0.0047629 | -0.0011937 | 8.0148e-07 | -2.0943e-08 | 0.007121 | 0.0071211 | 0.0071211 | 0.99542 | -0.03165 | 0.99525 | -0.032865 | 2.6375
17 | -0.085457 | -0.02158 | 0.085553 | 0.021617 | 9.5662e-05 | 3.667e-05 | 0.12752 | 0.12752 | 0.12752 | 0.99761 | -0.016506 | 0.99876 | -0.0085509 | 47.2309
18 | -0.00808 | -0.0020239 | 0.008082 | 0.0020244 | 2.0595e-06 | 5.0714e-07 | 0.012174 | 0.012174 | 0.012174 | 0.98754 | -0.087531 | 0.9878 | -0.085688 | 4.5091
19 | 0.0027467 | 0.00068731 | -0.0027457 | -0.00068814 | 1.0234e-06 | -8.3102e-07 | 0.0041384 | 0.0041388 | 0.0041388 | 0.98754 | -0.087531 | 0.98716 | -0.090227 | 1.5329
20 | -0.008082 | -0.0020244 | 0.0080931 | 0.0020272 | 1.1052e-05 | 2.7189e-06 | 0.012174 | 0.012174 | 0.012174 | 0.9878 | -0.085688 | 0.98919 | -0.075805 | 4.509
21 | -0.022168 | -0.0055555 | 0.022176 | 0.0055584 | 7.8505e-06 | 2.8741e-06 | 0.033346 | 0.033346 | 0.033346 | 0.98919 | -0.075805 | 0.98955 | -0.073248 | 12.3505
22 | 0.014075 | 0.0035283 | -0.014065 | -0.003525 | 9.773e-06 | 3.3107e-06 | 0.021172 | 0.021173 | 0.021173 | 0.98919 | -0.075805 | 0.98848 | -0.080822 | 7.8417
23 | 0.0063364 | 0.0015879 | -0.0063347 | -0.0015876 | 1.7648e-06 | 2.7869e-07 | 0.0095282 | 0.0095283 | 0.0095283 | 0.98955 | -0.073248 | 0.98927 | -0.07526 | 3.529
24 | -0.032001 | -0.0080208 | 0.03202 | 0.0080279 | 1.8879e-05 | 7.0931e-06 | 0.048122 | 0.048121 | 0.048122 | 0.98955 | -0.073248 | 0.99015 | -0.06899 | 17.8228
25 | 0.0088535 | 0.0022189 | -0.0088519 | -0.0022185 | 1.6834e-06 | 4.5282e-07 | 0.013328 | 0.013328 | 0.013328 | 0.98848 | -0.080822 | 0.98829 | -0.082195 | 4.9362
26 | 0.0081379 | 0.0020395 | -0.0081362 | -0.0020391 | 1.6904e-06 | 4.1724e-07 | 0.01223 | 0.01223 | 0.01223 | 0.99015 | -0.06899 | 0.98994 | -0.07049 | 4.5295
27 | -0.040158 | -0.010067 | 0.040186 | 0.010078 | 2.7898e-05 | 1.0572e-05 | 0.060351 | 0.060351 | 0.060351 | 0.99015 | -0.06899 | 0.99086 | -0.063978 | 22.3523
28 | 0.0062233 | 0.0015597 | -0.0062231 | -0.0015597 | 1.1324e-07 | 1.6891e-08 | 0.0093544 | 0.0093544 | 0.0093544 | 0.98994 | -0.07049 | 0.98992 | -0.070622 | 3.4646
29 | -0.044684 | -0.011205 | 0.04471 | 0.011215 | 2.5958e-05 | 9.865e-06 | 0.067106 | 0.067106 | 0.067106 | 0.99086 | -0.063978 | 0.99146 | -0.059789 | 24.8542
30 | -0.025672 | -0.0064356 | 0.025678 | 0.0064379 | 6.1159e-06 | 2.2667e-06 | 0.038486 | 0.038486 | 0.038486 | 0.99261 | -0.051706 | 0.99285 | -0.049986 | 14.2539
31 | 0.01798 | 0.0045079 | -0.017966 | -0.0045026 | 1.4698e-05 | 5.2342e-06 | 0.026955 | 0.026955 | 0.026955 | 0.99261 | -0.051706 | 0.99177 | -0.057611 | 9.9834
32 | 0.0065595 | 0.0016438 | -0.0065575 | -0.0016435 | 2.0036e-06 | 3.4109e-07 | 0.0098309 | 0.009831 | 0.009831 | 0.99285 | -0.049986 | 0.99254 | -0.052193 | 3.6411
33 | -0.032238 | -0.0080817 | 0.032259 | 0.0080896 | 2.1174e-05 | 7.9558e-06 | 0.048316 | 0.048316 | 0.048316 | 0.99285 | -0.049986 | 0.99352 | -0.045247 | 17.895
34 | -0.034022 | -0.0085315 | 0.034054 | 0.0085435 | 3.1715e-05 | 1.1944e-05 | 0.050957 | 0.050957 | 0.050957 | 0.99352 | -0.045247 | 0.99448 | -0.038528 | 18.873
35 | -0.098565 | -0.024743 | 0.099023 | 0.024919 | 0.00045834 | 0.00017584 | 0.14749 | 0.14749 | 0.14749 | 0.99448 | -0.038528 | 0.99925 | -0.0052065 | 54.6274
36 | 0.064511 | 0.0162 | -0.064409 | -0.016161 | 0.00010126 | 3.8721e-05 | 0.096537 | 0.096537 | 0.096537 | 0.99448 | -0.038528 | 0.99287 | -0.04984 | 35.7545
37 | 0.049283 | 0.012396 | -0.04923 | -0.012376 | 5.3419e-05 | 2.0338e-05 | 0.073405 | 0.073405 | 0.073405 | 0.99925 | -0.0052065 | 0.99813 | -0.012988 | 27.1871
38 | -0.14831 | -0.037315 | 0.14841 | 0.037357 | 0.00010782 | 4.1283e-05 | 0.2209 | 0.2209 | 0.2209 | 0.99925 | -0.0052065 | 1 | 0 | 40.9072
39 | 0.056964 | 0.014295 | -0.056957 | -0.014292 | 7.4652e-06 | 2.85e-06 | 0.085379 | 0.085379 | 0.085379 | 0.99287 | -0.04984 | 0.99274 | -0.050784 | 31.6219
40 | 0.046933 | 0.0118 | -0.046923 | -0.011796 | 1.0178e-05 | 3.871e-06 | 0.069981 | 0.069981 | 0.069981 | 0.99813 | -0.012988 | 0.99791 | -0.014545 | 25.9188
41 | 0.090814 | 0.02295 | -0.090704 | -0.022908 | 0.00010918 | 4.1866e-05 | 0.1352 | 0.1352 | 0.1352 | 1 | 0 | 0.99876 | -0.0085509 | 50.0737
42 | 0.046923 | 0.011796 | -0.046907 | -0.01179 | 1.6148e-05 | 6.1419e-06 | 0.069981 | 0.069981 | 0.069981 | 0.99791 | -0.014545 | 0.99756 | -0.017017 | 25.9188
43 | 0.044598 | 0.011212 | -0.044548 | -0.011192 | 5.0636e-05 | 1.9236e-05 | 0.066538 | 0.066538 | 0.066538 | 0.99756 | -0.017017 | 0.99639 | -0.025177 | 24.6436
44 | 0.047671 | 0.011965 | -0.047611 | -0.011942 | 5.9524e-05 | 2.2652e-05 | 0.07146 | 0.07146 | 0.07146 | 0.99274 | -0.050784 | 0.99146 | -0.059789 | 26.4668
45 | 0.038584 | 0.0096982 | -0.03843 | -0.0096401 | 0.00015375 | 5.8174e-05 | 0.057632 | 0.057632 | 0.057632 | 0.99639 | -0.025177 | 0.99229 | -0.053911 | 21.3452
46 | 0.0059635 | 0.0014942 | -0.0059605 | -0.0014938 | 3.0837e-06 | 3.7498e-07 | 0.0089059 | 0.0089062 | 0.0089062 | 0.99639 | -0.025177 | 0.99586 | -0.028915 | 3.2986
47 | 0.027873 | 0.0069941 | -0.027871 | -0.0069933 | 2.0164e-06 | 7.5167e-07 | 0.0418 | 0.0418 | 0.0418 | 0.99229 | -0.053911 | 0.99222 | -0.054432 | 15.4816
48 | 0.027871 | 0.0069933 | -0.027827 | -0.0069771 | 4.3365e-05 | 1.6166e-05 | 0.0418 | 0.0418 | 0.0418 | 0.99222 | -0.054432 | 0.99063 | -0.065662 | 15.4816
49 | 0.018152 | 0.0045522 | -0.018142 | -0.0045484 | 1.0721e-05 | 3.826e-06 | 0.027268 | 0.027268 | 0.027268 | 0.99063 | -0.065662 | 0.99002 | -0.069926 | 10.0991
50 | 0.009675 | 0.0024249 | -0.0096715 | -0.0024239 | 3.4585e-06 | 9.9245e-07 | 0.014533 | 0.014533 | 0.014533 | 0.99063 | -0.065662 | 0.99026 | -0.068245 | 5.3826
51 | 0.018142 | 0.0045484 | -0.018126 | -0.0045427 | 1.5984e-05 | 5.7049e-06 | 0.027268 | 0.027268 | 0.027268 | 0.99002 | -0.069926 | 0.98912 | -0.07629 | 10.0992

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.24452 | 0.061432

## res_load
| p_mw | q_mvar
0 | 0.014452 | 0.003622
1 | 0.019505 | 0.0048884
2 | 0.0034063 | 0.0008537
3 | 0.00086912 | 0.00021782
4 | 0.017547 | 0.0043978
5 | 0.0080675 | 0.0020219
6 | 0.0014938 | 0.00037438
7 | 0.0036623 | 0.00091785
8 | 0.0029386 | 0.00073649
9 | 0.002096 | 0.00052531
10 | 0.0017715 | 0.00044397
11 | 0.0036321 | 0.00091028
12 | 0.0053332 | 0.0013366
13 | 0.0027457 | 0.00068814
14 | 0.0034894 | 0.00087453
15 | 0.0052113 | 0.0013061
16 | 0.0088519 | 0.0022185
17 | 0.0063347 | 0.0015876
18 | 0.0019129 | 0.00047942
19 | 0.0044982 | 0.0011274
20 | 0.0076917 | 0.0019277
21 | 0.017966 | 0.0045026
22 | 0.0065575 | 0.0016435
23 | 0.0017632 | 0.0004419
24 | 0.007445 | 0.0018659
25 | 0.0022971 | 0.00057571
26 | 0.0044903 | 0.0011254
27 | 0.0023083 | 0.00057851
28 | 0.009286 | 0.0023273
29 | 0.0051519 | 0.0012912
30 | 0.0029012 | 0.00072711
31 | 0.0047629 | 0.0011937
32 | 0.010558 | 0.002646
33 | 0.0059605 | 0.0014938
34 | 0.0062231 | 0.0015597
35 | 0.0096715 | 0.0024239
36 | 0.018126 | 0.0045427

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1