## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1631-124_1_3_node_4 | 0.4 | n |  | TRUE
1 | bus_LV_1631-124_1_3_node_6 | 0.4 | n |  | TRUE
2 | bus_LV_1631-124_1_3_node_7 | 0.4 | n |  | TRUE
3 | bus_LV_1631-124_1_3_node_8 | 0.4 | n |  | TRUE
4 | bus_LV_1631-124_1_3_node_41 | 0.4 | n |  | TRUE
5 | bus_LV_1631-124_1_3_node_76 | 0.4 | n |  | TRUE
6 | bus_LV_1631-124_1_3_node_32 | 0.4 | n |  | TRUE
7 | bus_LV_1631-124_1_3_node_39 | 0.4 | n |  | TRUE
8 | bus_LV_1631-124_1_3_node_75 | 0.4 | n |  | TRUE
9 | bus_LV_1631-124_1_3_node_31 | 0.4 | n |  | TRUE
10 | bus_LV_1631-124_1_3_node_30 | 0.4 | n |  | TRUE
11 | bus_LV_1631-124_1_3_node_33 | 0.4 | n |  | TRUE
12 | bus_LV_1631-124_1_3_node_34 | 0.4 | n |  | TRUE
13 | bus_LV_1631-124_1_3_node_35 | 0.4 | n |  | TRUE
14 | bus_LV_1631-124_1_3_node_36 | 0.4 | n |  | TRUE
15 | bus_LV_1631-124_1_3_node_47 | 0.4 | n |  | TRUE
16 | bus_LV_1631-124_1_3_node_48 | 0.4 | n |  | TRUE
17 | bus_LV_1631-124_1_3_node_49 | 0.4 | n |  | TRUE
18 | bus_LV_1631-124_1_3_node_71 | 0.4 | n |  | TRUE
19 | bus_LV_1631-124_1_3_node_38 | 0.4 | n |  | TRUE
20 | bus_LV_1631-124_1_3_node_40 | 0.4 | n |  | TRUE
21 | bus_LV_1631-124_1_3_node_42 | 0.4 | n |  | TRUE
22 | bus_LV_1631-124_1_3_node_46 | 0.4 | n |  | TRUE
23 | bus_LV_1631-124_1_3_node_61 | 0.4 | n |  | TRUE
24 | bus_LV_1631-124_1_3_node_44 | 0.4 | n |  | TRUE
25 | bus_LV_1631-124_1_3_node_53 | 0.4 | n |  | TRUE
26 | bus_LV_1631-124_1_3_node_59 | 0.4 | n |  | TRUE
27 | bus_LV_1631-124_1_3_node_43 | 0.4 | n |  | TRUE
28 | bus_LV_1631-124_1_3_node_45 | 0.4 | n |  | TRUE
29 | bus_LV_1631-124_1_3_node_50 | 0.4 | n |  | TRUE
30 | bus_LV_1631-124_1_3_node_51 | 0.4 | n |  | TRUE
31 | bus_LV_1631-124_1_3_node_52 | 0.4 | n |  | TRUE
32 | bus_LV_1631-124_1_3_node_74 | 0.4 | n |  | TRUE
33 | bus_LV_1631-124_1_3_node_56 | 0.4 | n |  | TRUE
34 | bus_LV_1631-124_1_3_node_58 | 0.4 | n |  | TRUE
35 | bus_LV_1631-124_1_3_node_54 | 0.4 | n |  | TRUE
36 | bus_LV_1631-124_1_3_node_55 | 0.4 | n |  | TRUE
37 | bus_LV_1631-124_1_3_node_57 | 0.4 | n |  | TRUE
38 | bus_LV_1631-124_1_3_node_67 | 0.4 | n |  | TRUE
39 | bus_LV_1631-124_1_3_node_68 | 0.4 | n |  | TRUE
40 | bus_LV_1631-124_1_3_node_66 | 0.4 | n |  | TRUE
41 | bus_LV_1631-124_1_3_node_69 | 0.4 | n |  | TRUE
42 | bus_LV_1631-124_1_3_node_70 | 0.4 | n |  | TRUE
43 | bus_LV_1631-124_1_3_node_60 | 0.4 | n |  | TRUE
44 | bus_LV_1631-124_1_3_node_62 | 0.4 | n |  | TRUE
45 | bus_LV_1631-124_1_3_node_63 | 0.4 | n |  | TRUE
46 | bus_LV_1631-124_1_3_node_64 | 0.4 | n |  | TRUE
47 | bus_LV_1631-124_1_3_node_65 | 0.4 | n |  | TRUE
48 | bus_LV_1631-124_1_3_node_73 | 0.4 | n |  | TRUE
49 | bus_MV_145_0_node_252 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1631-124_1_3_load_4 | 0 | 0.0067007 | 0.0016794 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1631-124_1_3_load_7 | 2 | 0.005082 | 0.0012737 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1631-124_1_3_load_41 | 4 | 0.004903 | 0.0012288 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1631-124_1_3_load_76 | 5 | 0.0024219 | 0.00060698 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1631-124_1_3_load_75 | 8 | 0.0077493 | 0.0019421 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1631-124_1_3_load_30 | 10 | 0.003145 | 0.00078821 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1631-124_1_3_load_33 | 11 | 0.0051694 | 0.0012956 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1631-124_1_3_load_34 | 12 | 0.0033714 | 0.00084494 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1631-124_1_3_load_35 | 13 | 0.0039688 | 0.00099467 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1631-124_1_3_load_47 | 15 | 0.008242 | 0.0020656 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1631-124_1_3_load_48 | 16 | 0.0061682 | 0.0015459 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1631-124_1_3_load_49 | 17 | 0.0063865 | 0.0016006 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1631-124_1_3_load_71 | 18 | 0.0033854 | 0.00084847 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1631-124_1_3_load_38 | 19 | 0.0029604 | 0.00074194 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1631-124_1_3_load_40 | 20 | 0.0033764 | 0.0008462 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1631-124_1_3_load_46 | 22 | 0.0025564 | 0.00064069 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1631-124_1_3_load_44 | 24 | 0.0045588 | 0.0011426 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1631-124_1_3_load_53 | 25 | 0.0038283 | 0.00095946 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1631-124_1_3_load_59 | 26 | 0.0025012 | 0.00062687 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1631-124_1_3_load_43 | 27 | 0.0068748 | 0.001723 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1631-124_1_3_load_45 | 28 | 0.0056829 | 0.0014243 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1631-124_1_3_load_50 | 29 | 0.0055242 | 0.0013845 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1631-124_1_3_load_74 | 32 | 0.0096329 | 0.0024142 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1631-124_1_3_load_58 | 34 | 0.0073268 | 0.0018363 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1631-124_1_3_load_54 | 35 | 0.0095093 | 0.0023833 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1631-124_1_3_load_55 | 36 | 0.0039482 | 0.00098951 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1631-124_1_3_load_66 | 40 | 0.0091122 | 0.0022837 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1631-124_1_3_load_69 | 41 | 0.0056306 | 0.0014112 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1631-124_1_3_load_70 | 42 | 0.0056848 | 0.0014247 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1631-124_1_3_load_60 | 43 | 0.0039272 | 0.00098426 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1631-124_1_3_load_62 | 44 | 0.0031874 | 0.00079884 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1631-124_1_3_load_63 | 45 | 0.0063178 | 0.0015834 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1631-124_1_3_load_64 | 46 | 0.0038727 | 0.00097058 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1631-124_1_3_load_73 | 48 | 0.0069688 | 0.0017465 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 23 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1631-124_1_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.062958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1631-124_1_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.00089375 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1631-124_1_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.007842 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1631-124_1_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.0038354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1631-124_1_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.01073 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1631-124_1_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.019405 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1631-124_1_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.01109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1631-124_1_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.040368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1631-124_1_3_line_8 | NAYY 4x150 SE | 6 | 9 | 0.029298 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1631-124_1_3_line_9 | NAYY 4x150 SE | 7 | 21 | 0.006282 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1631-124_1_3_line_10 | NAYY 4x150 SE | 7 | 19 | 0.017586 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1631-124_1_3_line_11 | NAYY 4x150 SE | 9 | 10 | 0.013838 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1631-124_1_3_line_12 | NAYY 4x150 SE | 11 | 12 | 0.061912 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1631-124_1_3_line_13 | NAYY 4x150 SE | 11 | 13 | 0.023679 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1631-124_1_3_line_14 | NAYY 4x150 SE | 12 | 14 | 0.044755 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1631-124_1_3_line_15 | NAYY 4x150 SE | 14 | 15 | 0.035293 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1631-124_1_3_line_16 | NAYY 4x150 SE | 14 | 16 | 0.012712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1631-124_1_3_line_17 | NAYY 4x150 SE | 15 | 17 | 0.0049811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1631-124_1_3_line_18 | NAYY 4x150 SE | 16 | 18 | 0.0311 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1631-124_1_3_line_19 | NAYY 4x150 SE | 17 | 29 | 0.0012315 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1631-124_1_3_line_20 | NAYY 4x150 SE | 19 | 20 | 0.0059086 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1631-124_1_3_line_21 | NAYY 4x150 SE | 21 | 22 | 0.022957 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1631-124_1_3_line_22 | NAYY 4x150 SE | 21 | 23 | 0.012135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1631-124_1_3_line_23 | NAYY 4x150 SE | 22 | 24 | 0.014172 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1631-124_1_3_line_24 | NAYY 4x150 SE | 23 | 25 | 0.011687 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1631-124_1_3_line_25 | NAYY 4x150 SE | 23 | 26 | 0.013377 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1631-124_1_3_line_26 | NAYY 4x150 SE | 24 | 27 | 0.0014051 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1631-124_1_3_line_27 | NAYY 4x150 SE | 25 | 30 | 0.021016 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1631-124_1_3_line_28 | NAYY 4x150 SE | 26 | 43 | 0.011933 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1631-124_1_3_line_29 | NAYY 4x150 SE | 27 | 28 | 0.015526 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1631-124_1_3_line_30 | NAYY 4x150 SE | 29 | 30 | 0.021138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1631-124_1_3_line_31 | NAYY 4x150 SE | 30 | 31 | 0.009196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1631-124_1_3_line_32 | NAYY 4x150 SE | 31 | 32 | 0.031607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1631-124_1_3_line_33 | NAYY 4x150 SE | 31 | 33 | 0.020253 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1631-124_1_3_line_34 | NAYY 4x150 SE | 33 | 34 | 0.019171 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1631-124_1_3_line_35 | NAYY 4x150 SE | 33 | 35 | 0.0020467 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1631-124_1_3_line_36 | NAYY 4x150 SE | 34 | 39 | 0.022293 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1631-124_1_3_line_37 | NAYY 4x150 SE | 35 | 36 | 0.015765 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1631-124_1_3_line_38 | NAYY 4x150 SE | 36 | 37 | 0.022638 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1631-124_1_3_line_39 | NAYY 4x150 SE | 37 | 38 | 0.090403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1631-124_1_3_line_40 | NAYY 4x150 SE | 38 | 40 | 0.086138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1631-124_1_3_line_41 | NAYY 4x150 SE | 39 | 41 | 0.011271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1631-124_1_3_line_42 | NAYY 4x150 SE | 39 | 42 | 0.018586 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1631-124_1_3_line_43 | NAYY 4x150 SE | 43 | 44 | 0.007717 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1631-124_1_3_line_44 | NAYY 4x150 SE | 44 | 45 | 0.0084567 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1631-124_1_3_line_45 | NAYY 4x150 SE | 45 | 46 | 0.0014103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1631-124_1_3_line_46 | NAYY 4x150 SE | 46 | 47 | 0.020002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1631-124_1_3_line_47 | NAYY 4x150 SE | 47 | 48 | 0.039259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1631-124_1_3_trafo_61 | 0.25 MVA 20/0.4 kV | 49 | 23 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2722899.0436 | 1205134.6083 | 2722896.0965 | 1205131.0227 | 2722867.1059 | 1205096.9894 | 2722858.3862 | 1205086.5406
1 | 2722899.6224 | 1205135.2893 | 2722899.0436 | 1205134.6083
2 | 2722891.1898 | 1205135.0248 | 2722899.0436 | 1205134.6083
3 | 2722902.1063 | 1205138.2117 | 2722899.6224 | 1205135.2893
4 | 2722891.1898 | 1205135.0248 | 2722885.1404 | 1205143.8959
5 | 2722891.1898 | 1205135.0248 | 2722872.7429 | 1205128.8405
6 | 2722909.2885 | 1205146.6616 | 2722902.1063 | 1205138.2117
7 | 2722848.0673 | 1205157.6101 | 2722852.041 | 1205154.2004 | 2722853.0781 | 1205152.2425 | 2722858.1318 | 1205138.5139 | 2722859.4844 | 1205136.0176 | 2722861.0564 | 1205133.9484 | 2722863.4353 | 1205132.2405 | 2722866.0451 | 1205130.7708 | 2722872.7429 | 1205128.8405
8 | 2722847.3618 | 1205114.9968 | 2722852.1913 | 1205115.8523 | 2722858.3192 | 1205118.3247 | 2722870.8827 | 1205127.5346 | 2722872.7429 | 1205128.8405
9 | 2722913.3674 | 1205151.4491 | 2722909.2885 | 1205146.6616
10 | 2722909.2885 | 1205146.6616 | 2722894.8208 | 1205156.6592
11 | 2722847.3618 | 1205114.9968 | 2722838.2482 | 1205104.5837
12 | 2722819.9936 | 1205193.1792 | 2722828.5701 | 1205202.454 | 2722832.332 | 1205205.6338 | 2722835.9682 | 1205207.5322 | 2722839.9314 | 1205208.3254 | 2722845.9966 | 1205208.6616 | 2722868.5988 | 1205211.1062 | 2722875.6587 | 1205213.3283
13 | 2722819.9936 | 1205193.1792 | 2722803.9171 | 1205175.7935 | 2722803.9171 | 1205175.7935
14 | 2722911.4426 | 1205239.3536 | 2722902.2443 | 1205230.0573 | 2722889.7308 | 1205220.6482 | 2722882.6873 | 1205215.7218 | 2722876.915 | 1205213.7237 | 2722875.6587 | 1205213.3283
15 | 2722911.4426 | 1205239.3536 | 2722918.8984 | 1205223.8954 | 2722923.0027 | 1205213.0384 | 2722925.6421 | 1205207.0728
16 | 2722911.4426 | 1205239.3536 | 2722921.1286 | 1205247.5857
17 | 2722925.6421 | 1205207.0728 | 2722926.3227 | 1205205.5344 | 2722928.1985 | 1205202.8207
18 | 2722921.1286 | 1205247.5857 | 2722924.0733 | 1205250.0884 | 2722936.6849 | 1205254.7293 | 2722949.7419 | 1205259.1876
19 | 2722928.8988 | 1205201.8076 | 2722928.1985 | 1205202.8207
20 | 2722889.9598 | 1205160.0183 | 2722894.8208 | 1205156.6592
21 | 2722913.3674 | 1205151.4491 | 2722907.3289 | 1205157.9409 | 2722908.3578 | 1205164.8784 | 2722902.3881 | 1205168.681
22 | 2722921.2349 | 1205160.707 | 2722913.3674 | 1205151.4491
23 | 2722902.3881 | 1205168.681 | 2722897.0621 | 1205172.0736 | 2722890.0113 | 1205175.5413
24 | 2722921.2349 | 1205160.707 | 2722928.8071 | 1205169.6095
25 | 2722921.2349 | 1205160.707 | 2722926.8878 | 1205148.5834
26 | 2722888.7504 | 1205176.1615 | 2722890.0113 | 1205175.5413
27 | 2722942.4232 | 1205185.6175 | 2722928.8071 | 1205169.6095
28 | 2722926.8878 | 1205148.5834 | 2722930.5094 | 1205140.8162 | 2722931.1787 | 1205137.52
29 | 2722874.4524 | 1205182.1826 | 2722884.5629 | 1205178.221 | 2722888.7504 | 1205176.1615
30 | 2722942.4232 | 1205185.6175 | 2722932.8402 | 1205196.1059 | 2722928.8988 | 1205201.8076
31 | 2722942.4232 | 1205185.6175 | 2722945.3759 | 1205188.9252 | 2722948.5593 | 1205192.4823
32 | 2722948.5593 | 1205192.4823 | 2722953.141 | 1205184.3149 | 2722957.3065 | 1205175.2939 | 2722959.2433 | 1205170.2967 | 2722961.0178 | 1205163.5726
33 | 2722963.6981 | 1205205.9486 | 2722955.4577 | 1205199.2851 | 2722948.5593 | 1205192.4823
34 | 2722963.6981 | 1205205.9486 | 2722973.0842 | 1205189.2329
35 | 2722963.6981 | 1205205.9486 | 2722965.4061 | 1205207.0763
36 | 2722983.9988 | 1205169.795 | 2722973.0842 | 1205189.2329
37 | 2722965.4061 | 1205207.0763 | 2722978.562 | 1205215.7621 | 2722978.562 | 1205215.7621
38 | 2722998.6006 | 1205226.2939 | 2722978.562 | 1205215.7621
39 | 2722998.6006 | 1205226.2939 | 2723018.0565 | 1205236.2911 | 2723024.9549 | 1205215.0394 | 2723026.1381 | 1205204.8894 | 2723029.6003 | 1205169.0893
40 | 2723029.6003 | 1205169.0893 | 2723030.3066 | 1205161.7761 | 2723033.8277 | 1205103.9272 | 2723038.1915 | 1205083.5549
41 | 2722983.9988 | 1205169.795 | 2722993.959 | 1205175.0695
42 | 2722992.1494 | 1205153.128 | 2722988.8709 | 1205161.1999 | 2722983.9988 | 1205169.795
43 | 2722931.1787 | 1205137.52 | 2722931.7034 | 1205134.9363 | 2722931.8081 | 1205129.8569
44 | 2722930.3143 | 1205121.5332 | 2722931.8081 | 1205129.8569 | 2722931.8081 | 1205129.8569
45 | 2722930.3143 | 1205121.5332 | 2722930.0675 | 1205120.1582 | 2722930.0646 | 1205120.1452
46 | 2722925.63 | 1205100.641 | 2722930.0646 | 1205120.1452
47 | 2722925.63 | 1205100.641 | 2722952.9859 | 1205092.498 | 2722963.6385 | 1205093.674

## bus_geodata
| x | y | coords
0 | 2722858.3862 | 1205086.5406
1 | 2722899.0436 | 1205134.6083
2 | 2722899.6224 | 1205135.2893
3 | 2722891.1898 | 1205135.0248
4 | 2722902.1063 | 1205138.2117
5 | 2722885.1404 | 1205143.8959
6 | 2722872.7429 | 1205128.8405
7 | 2722909.2885 | 1205146.6616
8 | 2722848.0673 | 1205157.6101
9 | 2722847.3618 | 1205114.9968
10 | 2722838.2482 | 1205104.5837
11 | 2722819.9936 | 1205193.1792
12 | 2722875.6587 | 1205213.3283
13 | 2722803.9171 | 1205175.7935
14 | 2722911.4426 | 1205239.3536
15 | 2722925.6421 | 1205207.0728
16 | 2722921.1286 | 1205247.5857
17 | 2722928.1985 | 1205202.8207
18 | 2722949.7419 | 1205259.1876
19 | 2722894.8208 | 1205156.6592
20 | 2722889.9598 | 1205160.0183
21 | 2722913.3674 | 1205151.4491
22 | 2722902.3881 | 1205168.681
23 | 2722921.2349 | 1205160.707
24 | 2722890.0113 | 1205175.5413
25 | 2722928.8071 | 1205169.6095
26 | 2722926.8878 | 1205148.5834
27 | 2722888.7504 | 1205176.1615
28 | 2722874.4524 | 1205182.1826
29 | 2722928.8988 | 1205201.8076
30 | 2722942.4232 | 1205185.6175
31 | 2722948.5593 | 1205192.4823
32 | 2722961.0178 | 1205163.5726
33 | 2722963.6981 | 1205205.9486
34 | 2722973.0842 | 1205189.2329
35 | 2722965.4061 | 1205207.0763
36 | 2722978.562 | 1205215.7621
37 | 2722998.6006 | 1205226.2939
38 | 2723029.6003 | 1205169.0893
39 | 2722983.9988 | 1205169.795
40 | 2723038.1915 | 1205083.5549
41 | 2722993.959 | 1205175.0695
42 | 2722992.1494 | 1205153.128
43 | 2722931.1787 | 1205137.52
44 | 2722931.8081 | 1205129.8569
45 | 2722930.3143 | 1205121.5332
46 | 2722930.0646 | 1205120.1452
47 | 2722925.63 | 1205100.641
48 | 2722963.6385 | 1205093.674
49 | 2722913.3674 | 1205151.4491

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99746 | -0.017787 | 0.0067007 | 0.0016794
1 | 0.99806 | -0.013556 | 0 | 0
2 | 0.99809 | -0.013376 | 0.005082 | 0.0012737
3 | 0.99792 | -0.014603 | 0 | 0
4 | 0.99823 | -0.012411 | 0.004903 | 0.0012288
5 | 0.99788 | -0.014864 | 0.0024219 | 0.00060698
6 | 0.99761 | -0.016724 | 0 | 0
7 | 0.9987 | -0.0090785 | 0 | 0
8 | 0.99717 | -0.019863 | 0.0077493 | 0.0019421
9 | 0.99748 | -0.017649 | 0 | 0
10 | 0.99742 | -0.018086 | 0.003145 | 0.00078821
11 | 0.99127 | -0.061263 | 0.0051694 | 0.0012956
12 | 0.99208 | -0.055518 | 0.0033714 | 0.00084494
13 | 0.99113 | -0.062218 | 0.0039688 | 0.00099467
14 | 0.99289 | -0.049841 | 0 | 0
15 | 0.99401 | -0.04196 | 0.008242 | 0.0020656
16 | 0.99271 | -0.051071 | 0.0061682 | 0.0015459
17 | 0.99422 | -0.040435 | 0.0063865 | 0.0016006
18 | 0.99256 | -0.052138 | 0.0033854 | 0.00084847
19 | 0.99854 | -0.010194 | 0.0029604 | 0.00074194
20 | 0.99852 | -0.010394 | 0.0033764 | 0.0008462
21 | 0.99903 | -0.0067936 | 0 | 0
22 | 0.99838 | -0.011314 | 0.0025564 | 0.00064069
23 | 1 | 0 | -0.18127 | -0.045323
24 | 0.99804 | -0.013744 | 0.0045588 | 0.0011426
25 | 0.99837 | -0.011327 | 0.0038283 | 0.00095946
26 | 0.99949 | -0.0035777 | 0.0025012 | 0.00062687
27 | 0.99801 | -0.013921 | 0.0068748 | 0.001723
28 | 0.99789 | -0.014805 | 0.0056829 | 0.0014243
29 | 0.99429 | -0.039978 | 0.0055242 | 0.0013845
30 | 0.99557 | -0.030976 | 0 | 0
31 | 0.9949 | -0.035691 | 0 | 0
32 | 0.99446 | -0.038763 | 0.0096329 | 0.0024142
33 | 0.9937 | -0.044123 | 0 | 0
34 | 0.99318 | -0.047738 | 0.0073268 | 0.0018363
35 | 0.99363 | -0.04459 | 0.0095093 | 0.0023833
36 | 0.99334 | -0.046675 | 0.0039482 | 0.00098951
37 | 0.99304 | -0.048766 | 0 | 0
38 | 0.99185 | -0.057125 | 0 | 0
39 | 0.99282 | -0.050292 | 0 | 0
40 | 0.99072 | -0.065101 | 0.0091122 | 0.0022837
41 | 0.99273 | -0.050935 | 0.0056306 | 0.0014112
42 | 0.99267 | -0.051362 | 0.0056848 | 0.0014247
43 | 0.99908 | -0.0064738 | 0.0039272 | 0.00098426
44 | 0.99885 | -0.0080446 | 0.0031874 | 0.00079884
45 | 0.99864 | -0.0094971 | 0.0063178 | 0.0015834
46 | 0.99862 | -0.0096502 | 0.0038727 | 0.00097058
47 | 0.99842 | -0.011046 | 0 | 0
48 | 0.99803 | -0.013787 | 0.0069688 | 0.0017465
49 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0067007 | -0.0016794 | 0.0067046 | 0.00168 | 3.9254e-06 | 6.8749e-07 | 0.0099961 | 0.0099958 | 0.0099961 | 0.99746 | -0.017787 | 0.99806 | -0.013556 | 3.7023
1 | -0.02003 | -0.0050193 | 0.02003 | 0.0050195 | 4.9733e-07 | 1.796e-07 | 0.029862 | 0.029862 | 0.029862 | 0.99806 | -0.013556 | 0.99809 | -0.013376 | 11.0602
2 | 0.013325 | 0.0033393 | -0.013323 | -0.0033386 | 1.9313e-06 | 6.4036e-07 | 0.019867 | 0.019867 | 0.019867 | 0.99806 | -0.013556 | 0.99792 | -0.014603 | 7.358
3 | -0.025112 | -0.0062932 | 0.025116 | 0.0062944 | 3.3546e-06 | 1.2401e-06 | 0.037439 | 0.037439 | 0.037439 | 0.99809 | -0.013376 | 0.99823 | -0.012411 | 13.8663
4 | 0.002422 | 0.00060688 | -0.0024219 | -0.00060698 | 8.7327e-08 | -1.0659e-07 | 0.0036114 | 0.0036115 | 0.0036115 | 0.99792 | -0.014603 | 0.99788 | -0.014864 | 1.3376
5 | 0.010901 | 0.0027318 | -0.010898 | -0.0027308 | 3.1995e-06 | 9.7714e-07 | 0.016255 | 0.016255 | 0.016255 | 0.99792 | -0.014603 | 0.99761 | -0.016724 | 6.0205
6 | -0.030019 | -0.0075232 | 0.030033 | 0.0075284 | 1.3856e-05 | 5.1844e-06 | 0.044748 | 0.044748 | 0.044748 | 0.99823 | -0.012411 | 0.9987 | -0.0090785 | 16.5733
7 | 0.0077526 | 0.0019429 | -0.0077493 | -0.0019421 | 3.3683e-06 | 7.6867e-07 | 0.011564 | 0.011564 | 0.011564 | 0.99761 | -0.016724 | 0.99717 | -0.019863 | 4.2829
8 | 0.0031456 | 0.00078787 | -0.0031452 | -0.0007881 | 4.0243e-07 | -2.277e-07 | 0.0046917 | 0.0046918 | 0.0046918 | 0.99761 | -0.016724 | 0.99748 | -0.017649 | 1.7377
9 | -0.036371 | -0.0091167 | 0.036382 | 0.009121 | 1.1512e-05 | 4.3453e-06 | 0.054191 | 0.054191 | 0.054191 | 0.9987 | -0.0090785 | 0.99903 | -0.0067936 | 20.0706
10 | 0.0063379 | 0.0015883 | -0.0063369 | -0.0015881 | 9.7854e-07 | 1.4628e-07 | 0.009443 | 0.0094431 | 0.0094431 | 0.9987 | -0.0090785 | 0.99854 | -0.010194 | 3.4974
11 | 0.0031452 | 0.0007881 | -0.003145 | -0.00078821 | 1.9009e-07 | -1.0751e-07 | 0.0046918 | 0.0046919 | 0.0046919 | 0.99748 | -0.017649 | 0.99742 | -0.018086 | 1.7377
12 | -0.0091387 | -0.0022901 | 0.009146 | 0.0022921 | 7.2702e-06 | 1.9974e-06 | 0.013718 | 0.013718 | 0.013718 | 0.99127 | -0.061263 | 0.99208 | -0.055518 | 5.0808
13 | 0.0039693 | 0.00099456 | -0.0039688 | -0.00099466 | 5.2458e-07 | -1.0345e-07 | 0.0059583 | 0.0059584 | 0.0059584 | 0.99127 | -0.061263 | 0.99113 | -0.062218 | 2.2068
14 | -0.012517 | -0.0031371 | 0.012527 | 0.0031403 | 9.8438e-06 | 3.2077e-06 | 0.018775 | 0.018774 | 0.018775 | 0.99208 | -0.055518 | 0.99289 | -0.049841 | 6.9536
15 | -0.022083 | -0.0055349 | 0.022107 | 0.0055437 | 2.4121e-05 | 8.8204e-06 | 0.033095 | 0.033095 | 0.033095 | 0.99289 | -0.049841 | 0.99401 | -0.04196 | 12.2575
16 | 0.0095558 | 0.0023946 | -0.0095541 | -0.0023942 | 1.6268e-06 | 4.6131e-07 | 0.014321 | 0.014321 | 0.014321 | 0.99289 | -0.049841 | 0.99271 | -0.051071 | 5.3041
17 | -0.030349 | -0.0076093 | 0.030355 | 0.0076117 | 6.4159e-06 | 2.4031e-06 | 0.045433 | 0.045433 | 0.045433 | 0.99401 | -0.04196 | 0.99422 | -0.040435 | 16.8271
18 | 0.0033859 | 0.00084826 | -0.0033854 | -0.00084847 | 4.9988e-07 | -2.0976e-07 | 0.0050752 | 0.0050753 | 0.0050753 | 0.99271 | -0.051071 | 0.99256 | -0.052138 | 1.8798
19 | -0.036742 | -0.0092124 | 0.036744 | 0.0092132 | 2.3239e-06 | 8.7785e-07 | 0.054992 | 0.054992 | 0.054992 | 0.99422 | -0.040435 | 0.99429 | -0.039978 | 20.3673
20 | 0.0033765 | 0.00084616 | -0.0033764 | -0.0008462 | 9.3343e-08 | -4.1388e-08 | 0.0050316 | 0.0050316 | 0.0050316 | 0.99854 | -0.010194 | 0.99852 | -0.010394 | 1.8636
21 | 0.019692 | 0.0049371 | -0.01968 | -0.0049327 | 1.2324e-05 | 4.4397e-06 | 0.029331 | 0.029331 | 0.029331 | 0.99903 | -0.0067936 | 0.99838 | -0.011314 | 10.8634
22 | -0.056074 | -0.014058 | 0.056127 | 0.014078 | 5.2823e-05 | 2.0158e-05 | 0.083522 | 0.083522 | 0.083522 | 0.99903 | -0.0067936 | 1 | 0 | 30.934
23 | 0.017123 | 0.004292 | -0.017118 | -0.00429 | 5.76e-06 | 2.0301e-06 | 0.025521 | 0.025521 | 0.025521 | 0.99838 | -0.011314 | 0.99804 | -0.013744 | 9.4523
24 | 0.097532 | 0.024522 | -0.097378 | -0.024463 | 0.00015366 | 5.8949e-05 | 0.14516 | 0.14516 | 0.14516 | 1 | 0 | 0.99837 | -0.011327 | 53.7617
25 | 0.02681 | 0.0067227 | -0.026797 | -0.0067177 | 1.3286e-05 | 4.9344e-06 | 0.039895 | 0.039895 | 0.039895 | 1 | 0 | 0.99949 | -0.0035777 | 14.7761
26 | 0.012559 | 0.0031474 | -0.012558 | -0.0031473 | 3.074e-07 | 9.9868e-08 | 0.018724 | 0.018724 | 0.018724 | 0.99804 | -0.013744 | 0.99801 | -0.013921 | 6.9349
27 | 0.09355 | 0.023504 | -0.093295 | -0.023406 | 0.00025502 | 9.7809e-05 | 0.13945 | 0.13945 | 0.13945 | 0.99837 | -0.011327 | 0.99557 | -0.030976 | 51.6484
28 | 0.024296 | 0.0060909 | -0.024286 | -0.0060873 | 9.7429e-06 | 3.5909e-06 | 0.036172 | 0.036172 | 0.036172 | 0.99949 | -0.0035777 | 0.99908 | -0.0064738 | 13.3969
29 | 0.0056836 | 0.0014243 | -0.0056829 | -0.0014243 | 6.957e-07 | 6.4726e-08 | 0.0084741 | 0.0084742 | 0.0084742 | 0.99801 | -0.013921 | 0.99789 | -0.014805 | 3.1386
30 | -0.042268 | -0.010598 | 0.042321 | 0.010618 | 5.2784e-05 | 2.0027e-05 | 0.063259 | 0.063259 | 0.063259 | 0.99429 | -0.039978 | 0.99557 | -0.030976 | 23.4293
31 | 0.050974 | 0.012788 | -0.05094 | -0.012775 | 3.3312e-05 | 1.2693e-05 | 0.076192 | 0.076192 | 0.076192 | 0.99557 | -0.030976 | 0.9949 | -0.035691 | 28.2192
32 | 0.009637 | 0.0024154 | -0.0096329 | -0.0024142 | 4.0975e-06 | 1.1657e-06 | 0.014414 | 0.014414 | 0.014414 | 0.9949 | -0.035691 | 0.99446 | -0.038763 | 5.3384
33 | 0.041303 | 0.01036 | -0.041255 | -0.010342 | 4.8233e-05 | 1.8289e-05 | 0.061778 | 0.061778 | 0.061778 | 0.9949 | -0.035691 | 0.9937 | -0.044123 | 22.8808
34 | 0.018657 | 0.0046769 | -0.018648 | -0.0046735 | 9.3372e-06 | 3.343e-06 | 0.027938 | 0.027938 | 0.027938 | 0.9937 | -0.044123 | 0.99318 | -0.047738 | 10.3475
35 | 0.022598 | 0.0056647 | -0.022597 | -0.0056641 | 1.4625e-06 | 5.36e-07 | 0.03384 | 0.03384 | 0.03384 | 0.9937 | -0.044123 | 0.99363 | -0.04459 | 12.5334
36 | 0.011321 | 0.0028373 | -0.011317 | -0.002836 | 4.0018e-06 | 1.2508e-06 | 0.016961 | 0.016961 | 0.016961 | 0.99318 | -0.047738 | 0.99282 | -0.050292 | 6.2819
37 | 0.013087 | 0.0032809 | -0.013084 | -0.0032796 | 3.7788e-06 | 1.2493e-06 | 0.019599 | 0.0196 | 0.0196 | 0.99363 | -0.04459 | 0.99334 | -0.046675 | 7.2591
38 | 0.0091355 | 0.0022901 | -0.0091328 | -0.0022894 | 2.6456e-06 | 7.2457e-07 | 0.013685 | 0.013685 | 0.013685 | 0.99334 | -0.046675 | 0.99304 | -0.048766 | 5.0686
39 | 0.0091328 | 0.0022894 | -0.0091223 | -0.0022865 | 1.0565e-05 | 2.8955e-06 | 0.013685 | 0.013686 | 0.013686 | 0.99304 | -0.048766 | 0.99185 | -0.057125 | 5.0688
40 | 0.0091223 | 0.0022865 | -0.0091122 | -0.0022837 | 1.0068e-05 | 2.7617e-06 | 0.013686 | 0.013686 | 0.013686 | 0.99185 | -0.057125 | 0.99072 | -0.065101 | 5.0689
41 | 0.0056311 | 0.0014112 | -0.0056306 | -0.0014112 | 5.0094e-07 | 4.6936e-08 | 0.0084397 | 0.0084397 | 0.0084397 | 0.99282 | -0.050292 | 0.99273 | -0.050935 | 3.1258
42 | 0.0056856 | 0.0014248 | -0.0056848 | -0.0014247 | 8.4216e-07 | 8.3599e-08 | 0.0085214 | 0.0085215 | 0.0085215 | 0.99282 | -0.050292 | 0.99267 | -0.051362 | 3.1561
43 | 0.020359 | 0.005103 | -0.020354 | -0.0051014 | 4.4275e-06 | 1.6019e-06 | 0.030322 | 0.030322 | 0.030322 | 0.99908 | -0.0064738 | 0.99885 | -0.0080446 | 11.2305
44 | 0.017167 | 0.0043026 | -0.017163 | -0.0043013 | 3.4513e-06 | 1.2168e-06 | 0.025574 | 0.025574 | 0.025574 | 0.99885 | -0.0080446 | 0.99864 | -0.0094971 | 9.4719
45 | 0.010846 | 0.002718 | -0.010845 | -0.0027179 | 2.2982e-07 | 6.9942e-08 | 0.01616 | 0.01616 | 0.01616 | 0.99864 | -0.0094971 | 0.99862 | -0.0096502 | 5.9853
46 | 0.0069728 | 0.0017473 | -0.0069714 | -0.001747 | 1.3473e-06 | 2.5657e-07 | 0.01039 | 0.01039 | 0.01039 | 0.99862 | -0.0096502 | 0.99842 | -0.011046 | 3.8481
47 | 0.0069714 | 0.001747 | -0.0069688 | -0.0017465 | 2.6446e-06 | 5.0392e-07 | 0.01039 | 0.01039 | 0.01039 | 0.99842 | -0.011046 | 0.99803 | -0.013787 | 3.8482

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.18127 | 0.045323

## res_load
| p_mw | q_mvar
0 | 0.0067007 | 0.0016794
1 | 0.005082 | 0.0012737
2 | 0.004903 | 0.0012288
3 | 0.0024219 | 0.00060698
4 | 0.0077493 | 0.0019421
5 | 0.003145 | 0.00078821
6 | 0.0051694 | 0.0012956
7 | 0.0033714 | 0.00084494
8 | 0.0039688 | 0.00099467
9 | 0.008242 | 0.0020656
10 | 0.0061682 | 0.0015459
11 | 0.0063865 | 0.0016006
12 | 0.0033854 | 0.00084847
13 | 0.0029604 | 0.00074194
14 | 0.0033764 | 0.0008462
15 | 0.0025564 | 0.00064069
16 | 0.0045588 | 0.0011426
17 | 0.0038283 | 0.00095946
18 | 0.0025012 | 0.00062687
19 | 0.0068748 | 0.001723
20 | 0.0056829 | 0.0014243
21 | 0.0055242 | 0.0013845
22 | 0.0096329 | 0.0024142
23 | 0.0073268 | 0.0018363
24 | 0.0095093 | 0.0023833
25 | 0.0039482 | 0.00098951
26 | 0.0091122 | 0.0022837
27 | 0.0056306 | 0.0014112
28 | 0.0056848 | 0.0014247
29 | 0.0039272 | 0.00098426
30 | 0.0031874 | 0.00079884
31 | 0.0063178 | 0.0015834
32 | 0.0038727 | 0.00097058
33 | 0.0069688 | 0.0017465

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1