## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1631-130_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1631-130_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1631-130_0_2_node_16 | 0.4 | n |  | TRUE
3 | bus_LV_1631-130_0_2_node_17 | 0.4 | n |  | TRUE
4 | bus_LV_1631-130_0_2_node_22 | 0.4 | n |  | TRUE
5 | bus_LV_1631-130_0_2_node_2 | 0.4 | n |  | TRUE
6 | bus_LV_1631-130_0_2_node_34 | 0.4 | n |  | TRUE
7 | bus_LV_1631-130_0_2_node_33 | 0.4 | n |  | TRUE
8 | bus_LV_1631-130_0_2_node_3 | 0.4 | n |  | TRUE
9 | bus_LV_1631-130_0_2_node_31 | 0.4 | n |  | TRUE
10 | bus_LV_1631-130_0_2_node_32 | 0.4 | n |  | TRUE
11 | bus_LV_1631-130_0_2_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_1631-130_0_2_node_19 | 0.4 | n |  | TRUE
13 | bus_LV_1631-130_0_2_node_40 | 0.4 | n |  | TRUE
14 | bus_LV_1631-130_0_2_node_30 | 0.4 | n |  | TRUE
15 | bus_LV_1631-130_0_2_node_18 | 0.4 | n |  | TRUE
16 | bus_LV_1631-130_0_2_node_20 | 0.4 | n |  | TRUE
17 | bus_LV_1631-130_0_2_node_29 | 0.4 | n |  | TRUE
18 | bus_LV_1631-130_0_2_node_25 | 0.4 | n |  | TRUE
19 | bus_LV_1631-130_0_2_node_5 | 0.4 | n |  | TRUE
20 | bus_LV_1631-130_0_2_node_6 | 0.4 | n |  | TRUE
21 | bus_LV_1631-130_0_2_node_9 | 0.4 | n |  | TRUE
22 | bus_LV_1631-130_0_2_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_1631-130_0_2_node_35 | 0.4 | n |  | TRUE
24 | bus_LV_1631-130_0_2_node_38 | 0.4 | n |  | TRUE
25 | bus_LV_1631-130_0_2_node_37 | 0.4 | n |  | TRUE
26 | bus_LV_1631-130_0_2_node_39 | 0.4 | n |  | TRUE
27 | bus_LV_1631-130_0_2_node_36 | 0.4 | n |  | TRUE
28 | bus_LV_1631-130_0_2_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_1631-130_0_2_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_1631-130_0_2_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_1631-130_0_2_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_1631-130_0_2_node_27 | 0.4 | n |  | TRUE
33 | bus_LV_1631-130_0_2_node_28 | 0.4 | n |  | TRUE
34 | bus_MV_145_0_node_23 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1631-130_0_2_load_0 | 0 | 0.0018799 | 0.00047115 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1631-130_0_2_load_16 | 2 | 0.0025958 | 0.00065057 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1631-130_0_2_load_17 | 3 | 0.0094625 | 0.0023715 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1631-130_0_2_load_22 | 4 | 0.0036022 | 0.0009028 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1631-130_0_2_load_34 | 6 | 0.0019517 | 0.00048915 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1631-130_0_2_load_33 | 7 | 0.0069852 | 0.0017507 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1631-130_0_2_load_31 | 9 | 0.0033638 | 0.00084306 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1631-130_0_2_load_32 | 10 | 0.0081605 | 0.0020452 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1631-130_0_2_load_40 | 13 | 0.0024798 | 0.0006215 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1631-130_0_2_load_20 | 16 | 0.0025441 | 0.00063761 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1631-130_0_2_load_29 | 17 | 0.0064013 | 0.0016043 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1631-130_0_2_load_25 | 18 | 0.027887 | 0.0069892 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1631-130_0_2_load_5 | 19 | 0.061878 | 0.015508 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1631-130_0_2_load_38 | 24 | 0.0024703 | 0.00061911 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1631-130_0_2_load_37 | 25 | 0.0015998 | 0.00040095 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1631-130_0_2_load_39 | 26 | 0.0026435 | 0.00066251 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1631-130_0_2_load_36 | 27 | 0.0022519 | 0.00056438 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1631-130_0_2_load_21 | 28 | 0.0074403 | 0.0018647 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1631-130_0_2_load_23 | 29 | 0.0039284 | 0.00098454 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1631-130_0_2_load_24 | 30 | 0.0093734 | 0.0023492 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1631-130_0_2_load_26 | 31 | 0.013038 | 0.0032677 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1631-130_0_2_load_27 | 32 | 0.0050254 | 0.0012595 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1631-130_0_2_load_28 | 33 | 0.0015247 | 0.00038212 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 30 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1631-130_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.016083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1631-130_0_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.16415 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1631-130_0_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.023604 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
3 | LV_1631-130_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.024858 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
4 | LV_1631-130_0_2_line_4 | NAYY 4x150 SE | 3 | 15 | 0.022958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
5 | LV_1631-130_0_2_line_5 | NAYY 4x150 SE | 4 | 29 | 0.013513 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
6 | LV_1631-130_0_2_line_6 | NAYY 4x150 SE | 4 | 28 | 0.014857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1631-130_0_2_line_7 | NAYY 4x150 SE | 5 | 6 | 0.015374 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1631-130_0_2_line_8 | NAYY 4x150 SE | 5 | 7 | 0.027222 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1631-130_0_2_line_9 | NAYY 4x150 SE | 7 | 10 | 0.010964 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1631-130_0_2_line_10 | NAYY 4x150 SE | 8 | 9 | 0.011627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1631-130_0_2_line_11 | NAYY 4x150 SE | 8 | 10 | 0.0073726 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1631-130_0_2_line_12 | NAYY 4x150 SE | 9 | 14 | 0.0053427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1631-130_0_2_line_13 | NAYY 4x150 SE | 11 | 12 | 0.024327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1631-130_0_2_line_14 | NAYY 4x150 SE | 11 | 13 | 0.011122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1631-130_0_2_line_15 | NAYY 4x150 SE | 12 | 15 | 0.027599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1631-130_0_2_line_16 | NAYY 4x150 SE | 12 | 18 | 0.044708 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1631-130_0_2_line_17 | NAYY 4x150 SE | 12 | 27 | 0.010061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1631-130_0_2_line_18 | NAYY 4x150 SE | 14 | 17 | 0.015063 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1631-130_0_2_line_19 | NAYY 4x150 SE | 14 | 33 | 0.0094152 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1631-130_0_2_line_20 | NAYY 4x150 SE | 15 | 16 | 0.011176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1631-130_0_2_line_21 | NAYY 4x150 SE | 15 | 17 | 0.083013 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1631-130_0_2_line_22 | NAYY 4x150 SE | 16 | 23 | 0.0065085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1631-130_0_2_line_23 | NAYY 4x150 SE | 19 | 20 | 0.018074 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1631-130_0_2_line_24 | NAYY 4x150 SE | 20 | 21 | 0.027305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1631-130_0_2_line_25 | NAYY 4x150 SE | 20 | 22 | 0.065231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1631-130_0_2_line_26 | NAYY 4x150 SE | 21 | 23 | 0.028273 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1631-130_0_2_line_27 | NAYY 4x150 SE | 21 | 24 | 0.010974 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1631-130_0_2_line_28 | NAYY 4x150 SE | 22 | 25 | 0.026011 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1631-130_0_2_line_29 | NAYY 4x150 SE | 24 | 26 | 0.00028456 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1631-130_0_2_line_30 | NAYY 4x150 SE | 29 | 30 | 0.019239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
31 | LV_1631-130_0_2_line_31 | NAYY 4x150 SE | 31 | 32 | 0.0024199 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1631-130_0_2_line_32 | NAYY 4x150 SE | 32 | 33 | 0.017915 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1631-130_0_2_trafo_24 | 0.25 MVA 20/0.4 kV | 34 | 30 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2724163.5637 | 1205766.5794 | 2724174.2056 | 1205754.5208
1 | 2724076.6041 | 1205905.8048 | 2724163.5637 | 1205766.5794
2 | 2724076.6041 | 1205905.8048 | 2724097.118 | 1205917.4803
3 | 2724076.6041 | 1205905.8048 | 2724083.2602 | 1205881.8546
4 | 2724117.0392 | 1205928.8911 | 2724110.8447 | 1205925.2929 | 2724097.118 | 1205917.4803
5 | 2724083.2602 | 1205881.8546 | 2724089.1693 | 1205884.289 | 2724095.6217 | 1205887.3047
6 | 2724069.5231 | 1205876.1951 | 2724083.2602 | 1205881.8546
7 | 2724213.2636 | 1205871.0592 | 2724206.9031 | 1205877.6318 | 2724203.8716 | 1205883.0716
8 | 2724213.2636 | 1205871.0592 | 2724189.3296 | 1205858.0899
9 | 2724189.3296 | 1205858.0899 | 2724179.6903 | 1205852.8665
10 | 2724173.2081 | 1205849.354 | 2724163.3537 | 1205843.1835
11 | 2724173.2081 | 1205849.354 | 2724179.6903 | 1205852.8665
12 | 2724158.8254 | 1205840.348 | 2724163.3537 | 1205843.1835
13 | 2724161.9835 | 1205955.1232 | 2724140.9284 | 1205942.8316
14 | 2724161.9835 | 1205955.1232 | 2724156.2595 | 1205964.6591
15 | 2724117.0392 | 1205928.8911 | 2724140.9284 | 1205942.8316
16 | 2724140.9284 | 1205942.8316 | 2724165.8663 | 1205905.7252
17 | 2724140.9284 | 1205942.8316 | 2724135.8669 | 1205951.5264
18 | 2724158.8254 | 1205840.348 | 2724150.5872 | 1205852.9588
19 | 2724158.8254 | 1205840.348 | 2724154.5743 | 1205837.691 | 2724150.7442 | 1205835.5213
20 | 2724117.0392 | 1205928.8911 | 2724111.3292 | 1205938.4978
21 | 2724117.0392 | 1205928.8911 | 2724150.5872 | 1205852.9588
22 | 2724108.0038 | 1205944.0926 | 2724111.3292 | 1205938.4978
23 | 2724075.222 | 1205955.6868 | 2724059.6391 | 1205946.5295
24 | 2724075.222 | 1205955.6868 | 2724080.0777 | 1205958.5343 | 2724084.7088 | 1205967.4262 | 2724085.7163 | 1205968.0031 | 2724087.4606 | 1205969.0068 | 2724088.393 | 1205969.5377 | 2724090.0073 | 1205966.5467 | 2724093.552 | 1205968.4107
25 | 2724075.222 | 1205955.6868 | 2724074.1938 | 1205957.5668 | 2724073.1341 | 1205959.5018 | 2724072.5092 | 1205960.6453 | 2724074.4482 | 1205961.7976 | 2724062.1443 | 1205983.0803 | 2724048.4026 | 1205974.7218 | 2724042.1356 | 1205974.9807 | 2724040.5345 | 1205974.0467 | 2724038.1743 | 1205972.6633 | 2724036.1081 | 1205976.1675 | 2724035.2251 | 1205977.6502
26 | 2724093.552 | 1205968.4107 | 2724108.0038 | 1205944.0926
27 | 2724093.552 | 1205968.4107 | 2724103.0668 | 1205973.8777
28 | 2724035.2251 | 1205977.6502 | 2724048.9155 | 1205985.5518 | 2724050.8779 | 1205986.6712 | 2724057.621 | 1205990.592 | 2724057.5454 | 1205990.7153
29 | 2724103.0668 | 1205973.8777 | 2724103.3135 | 1205974.0195
30 | 2724113.0512 | 1205895.4508 | 2724095.6217 | 1205887.3047
31 | 2724134.8423 | 1205827.2903 | 2724132.6624 | 1205826.2396
32 | 2724134.8423 | 1205827.2903 | 2724144.0391 | 1205831.7229 | 2724150.7442 | 1205835.5213

## bus_geodata
| x | y | coords
0 | 2724174.2056 | 1205754.5208
1 | 2724163.5637 | 1205766.5794
2 | 2724076.6041 | 1205905.8048
3 | 2724097.118 | 1205917.4803
4 | 2724083.2602 | 1205881.8546
5 | 2724213.2636 | 1205871.0592
6 | 2724203.8716 | 1205883.0716
7 | 2724189.3296 | 1205858.0899
8 | 2724173.2081 | 1205849.354
9 | 2724163.3537 | 1205843.1835
10 | 2724179.6903 | 1205852.8665
11 | 2724161.9835 | 1205955.1232
12 | 2724140.9284 | 1205942.8316
13 | 2724156.2595 | 1205964.6591
14 | 2724158.8254 | 1205840.348
15 | 2724117.0392 | 1205928.8911
16 | 2724111.3292 | 1205938.4978
17 | 2724150.5872 | 1205852.9588
18 | 2724165.8663 | 1205905.7252
19 | 2724059.6391 | 1205946.5295
20 | 2724075.222 | 1205955.6868
21 | 2724093.552 | 1205968.4107
22 | 2724035.2251 | 1205977.6502
23 | 2724108.0038 | 1205944.0926
24 | 2724103.0668 | 1205973.8777
25 | 2724057.5454 | 1205990.7153
26 | 2724103.3135 | 1205974.0195
27 | 2724135.8669 | 1205951.5264
28 | 2724069.5231 | 1205876.1951
29 | 2724095.6217 | 1205887.3047
30 | 2724113.0512 | 1205895.4508
31 | 2724132.6624 | 1205826.2396
32 | 2724134.8423 | 1205827.2903
33 | 2724150.7442 | 1205835.5213
34 | 2724052.8989 | 1205869.3462

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99233 | -0.0532 | 0.0018799 | 0.00047115
1 | 0.99238 | -0.052893 | 0 | 0
2 | 0.99282 | -0.049751 | 0.0025958 | 0.00065057
3 | 0.99008 | -0.068891 | 0.0094625 | 0.0023715
4 | 0.99578 | -0.029146 | 0.0036022 | 0.0009028
5 | 0.98025 | -0.13852 | 0 | 0
6 | 0.9802 | -0.13883 | 0.0019517 | 0.00048915
7 | 0.98032 | -0.13797 | 0.0069852 | 0.0017507
8 | 0.98065 | -0.13564 | 0 | 0
9 | 0.98094 | -0.13358 | 0.0033638 | 0.00084306
10 | 0.98047 | -0.13695 | 0.0081605 | 0.0020452
11 | 0.98619 | -0.096342 | 0 | 0
12 | 0.98628 | -0.095723 | 0 | 0
13 | 0.98615 | -0.096625 | 0.0024798 | 0.0006215
14 | 0.9811 | -0.13244 | 0 | 0
15 | 0.98758 | -0.086495 | 0 | 0
16 | 0.98642 | -0.094642 | 0.0025441 | 0.00063761
17 | 0.98197 | -0.12619 | 0.0064013 | 0.0016043
18 | 0.98447 | -0.10854 | 0.027887 | 0.0069892
19 | 0.9788 | -0.14879 | 0.061878 | 0.015508
20 | 0.98042 | -0.13716 | 0 | 0
21 | 0.98295 | -0.1192 | 0 | 0
22 | 0.98027 | -0.13824 | 0 | 0
23 | 0.98577 | -0.099225 | 0 | 0
24 | 0.98287 | -0.11978 | 0.0024703 | 0.00061911
25 | 0.98021 | -0.13868 | 0.0015998 | 0.00040095
26 | 0.98287 | -0.11979 | 0.0026435 | 0.00066251
27 | 0.98624 | -0.095955 | 0.0022519 | 0.00056438
28 | 0.99563 | -0.030259 | 0.0074403 | 0.0018647
29 | 0.9975 | -0.017248 | 0.0039284 | 0.00098454
30 | 1 | 0 | -0.18293 | -0.046037
31 | 0.98031 | -0.13804 | 0.013038 | 0.0032677
32 | 0.98036 | -0.13772 | 0.0050254 | 0.0012595
33 | 0.98083 | -0.13436 | 0.0015247 | 0.00038212
34 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0018799 | -0.00047115 | 0.00188 | 0.00047098 | 7.9748e-08 | -1.7711e-07 | 0.002819 | 0.0028189 | 0.002819 | 0.99233 | -0.0532 | 0.99238 | -0.052893 | 1.0441
1 | -0.00188 | -0.00047098 | 0.0018808 | 0.00046917 | 8.1372e-07 | -1.8088e-06 | 0.0028189 | 0.0028182 | 0.0028189 | 0.99238 | -0.052893 | 0.99282 | -0.049751 | 1.044
2 | 0.16146 | 0.040698 | -0.16103 | -0.040532 | 0.00043155 | 0.00016537 | 0.24207 | 0.24207 | 0.24207 | 0.99282 | -0.049751 | 0.99008 | -0.068891 | 44.8283
3 | -0.16594 | -0.041817 | 0.16642 | 0.042001 | 0.00048001 | 0.00018398 | 0.24878 | 0.24878 | 0.24878 | 0.99282 | -0.049751 | 0.99578 | -0.029146 | 46.0706
4 | 0.15156 | 0.038161 | -0.15119 | -0.038018 | 0.00037187 | 0.00014244 | 0.22785 | 0.22785 | 0.22785 | 0.99008 | -0.068891 | 0.98758 | -0.086495 | 42.1948
5 | -0.17746 | -0.044769 | 0.17776 | 0.044883 | 0.00029671 | 0.00011377 | 0.26528 | 0.26528 | 0.26528 | 0.99578 | -0.029146 | 0.9975 | -0.017248 | 49.1267
6 | 0.0074415 | 0.001865 | -0.0074403 | -0.0018647 | 1.1464e-06 | 2.4767e-07 | 0.01112 | 0.01112 | 0.01112 | 0.99578 | -0.029146 | 0.99563 | -0.030259 | 4.1185
7 | 0.0019518 | 0.00048899 | -0.0019517 | -0.00048915 | 8.4214e-08 | -1.6141e-07 | 0.0029628 | 0.0029629 | 0.0029629 | 0.98025 | -0.13852 | 0.9802 | -0.13883 | 1.0974
8 | -0.0019518 | -0.00048899 | 0.001952 | 0.0004887 | 1.4911e-07 | -2.8584e-07 | 0.0029628 | 0.0029627 | 0.0029628 | 0.98025 | -0.13852 | 0.98032 | -0.13797 | 1.0973
9 | -0.0089372 | -0.0022394 | 0.0089384 | 0.0022397 | 1.2589e-06 | 3.4595e-07 | 0.013565 | 0.013565 | 0.013565 | 0.98032 | -0.13797 | 0.98047 | -0.13695 | 5.0242
10 | -0.017102 | -0.004286 | 0.017107 | 0.0042878 | 4.8857e-06 | 1.7324e-06 | 0.02595 | 0.02595 | 0.02595 | 0.98065 | -0.13564 | 0.98094 | -0.13358 | 9.6112
11 | 0.017102 | 0.004286 | -0.017099 | -0.0042849 | 3.0981e-06 | 1.0986e-06 | 0.02595 | 0.02595 | 0.02595 | 0.98065 | -0.13564 | 0.98047 | -0.13695 | 9.6112
12 | -0.020471 | -0.0051308 | 0.020474 | 0.005132 | 3.2148e-06 | 1.169e-06 | 0.031053 | 0.031053 | 0.031053 | 0.98094 | -0.13358 | 0.9811 | -0.13244 | 11.5011
13 | -0.0024799 | -0.00062139 | 0.0024801 | 0.00062116 | 2.1253e-07 | -2.2868e-07 | 0.0037418 | 0.0037416 | 0.0037418 | 0.98619 | -0.096342 | 0.98628 | -0.095723 | 1.3858
14 | 0.0024799 | 0.00062139 | -0.0024798 | -0.0006215 | 9.7168e-08 | -1.0453e-07 | 0.0037418 | 0.0037418 | 0.0037418 | 0.98619 | -0.096342 | 0.98615 | -0.096625 | 1.3859
15 | -0.032669 | -0.0081932 | 0.032711 | 0.0082089 | 4.1841e-05 | 1.574e-05 | 0.04929 | 0.04929 | 0.04929 | 0.98628 | -0.095723 | 0.98758 | -0.086495 | 18.2557
16 | 0.027937 | 0.0070077 | -0.027887 | -0.0069892 | 4.9567e-05 | 1.8495e-05 | 0.042151 | 0.042151 | 0.042151 | 0.98628 | -0.095723 | 0.98447 | -0.10854 | 15.6116
17 | 0.002252 | 0.00056428 | -0.0022519 | -0.00056438 | 7.247e-08 | -1.0051e-07 | 0.0033976 | 0.0033976 | 0.0033976 | 0.98628 | -0.095723 | 0.98624 | -0.095955 | 1.2584
18 | -0.040076 | -0.010046 | 0.040111 | 0.010059 | 3.4728e-05 | 1.3167e-05 | 0.060784 | 0.060784 | 0.060784 | 0.9811 | -0.13244 | 0.98197 | -0.12619 | 22.5126
19 | 0.019602 | 0.0049143 | -0.019597 | -0.0049125 | 5.1932e-06 | 1.8785e-06 | 0.029731 | 0.029731 | 0.029731 | 0.9811 | -0.13244 | 0.98083 | -0.13436 | 11.0116
20 | 0.071712 | 0.018048 | -0.071631 | -0.018016 | 8.1457e-05 | 3.1187e-05 | 0.10808 | 0.10808 | 0.10808 | 0.98758 | -0.086495 | 0.98642 | -0.094642 | 40.0288
21 | 0.04677 | 0.011762 | -0.046512 | -0.011664 | 0.00025734 | 9.7921e-05 | 0.070484 | 0.070484 | 0.070484 | 0.98758 | -0.086495 | 0.98197 | -0.12619 | 26.1052
22 | 0.069087 | 0.017379 | -0.069043 | -0.017362 | 4.413e-05 | 1.689e-05 | 0.10424 | 0.10424 | 0.10424 | 0.98642 | -0.094642 | 0.98577 | -0.099225 | 38.6075
23 | -0.061878 | -0.015508 | 0.061978 | 0.015546 | 9.9805e-05 | 3.8159e-05 | 0.09407 | 0.09407 | 0.09407 | 0.9788 | -0.14879 | 0.98042 | -0.13716 | 34.8409
24 | -0.063578 | -0.015946 | 0.063737 | 0.016007 | 0.00015866 | 6.0677e-05 | 0.096498 | 0.096498 | 0.096498 | 0.98042 | -0.13716 | 0.98295 | -0.1192 | 35.7402
25 | 0.0016001 | 0.00039993 | -0.0015999 | -0.00040066 | 2.4002e-07 | -7.3016e-07 | 0.0024282 | 0.0024285 | 0.0024285 | 0.98042 | -0.13716 | 0.98027 | -0.13824 | 0.89944
26 | -0.068851 | -0.017289 | 0.069043 | 0.017362 | 0.0001917 | 7.3372e-05 | 0.10424 | 0.10424 | 0.10424 | 0.98295 | -0.1192 | 0.98577 | -0.099225 | 38.6075
27 | 0.0051142 | 0.0012816 | -0.0051137 | -0.0012816 | 4.1042e-07 | 1.8769e-08 | 0.0077419 | 0.007742 | 0.007742 | 0.98295 | -0.1192 | 0.98287 | -0.11978 | 2.8674
28 | 0.0015999 | 0.00040066 | -0.0015998 | -0.00040095 | 9.5726e-08 | -2.9108e-07 | 0.0024285 | 0.0024286 | 0.0024286 | 0.98027 | -0.13824 | 0.98021 | -0.13868 | 0.89948
29 | 0.0026435 | 0.00066251 | -0.0026435 | -0.00066251 | 2.8436e-09 | -2.5126e-09 | 0.0040021 | 0.0040021 | 0.0040021 | 0.98287 | -0.11978 | 0.98287 | -0.11979 | 1.4822
30 | -0.18168 | -0.045867 | 0.18213 | 0.046037 | 0.00044131 | 0.00016923 | 0.27114 | 0.27114 | 0.27114 | 0.9975 | -0.017248 | 1 | 0 | 50.2118
31 | -0.013038 | -0.0032677 | 0.013039 | 0.0032679 | 5.9142e-07 | 1.9696e-07 | 0.019791 | 0.019791 | 0.019791 | 0.98031 | -0.13804 | 0.98036 | -0.13772 | 7.3299
32 | -0.018064 | -0.0045273 | 0.018073 | 0.0045303 | 8.4041e-06 | 3.0063e-06 | 0.027418 | 0.027418 | 0.027418 | 0.98036 | -0.13772 | 0.98083 | -0.13436 | 10.1549

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.1923 | 0.048386

## res_load
| p_mw | q_mvar
0 | 0.0018799 | 0.00047115
1 | 0.0025958 | 0.00065057
2 | 0.0094625 | 0.0023715
3 | 0.0036022 | 0.0009028
4 | 0.0019517 | 0.00048915
5 | 0.0069852 | 0.0017507
6 | 0.0033638 | 0.00084306
7 | 0.0081605 | 0.0020452
8 | 0.0024798 | 0.0006215
9 | 0.0025441 | 0.00063761
10 | 0.0064013 | 0.0016043
11 | 0.027887 | 0.0069892
12 | 0.061878 | 0.015508
13 | 0.0024703 | 0.00061911
14 | 0.0015998 | 0.00040095
15 | 0.0026435 | 0.00066251
16 | 0.0022519 | 0.00056438
17 | 0.0074403 | 0.0018647
18 | 0.0039284 | 0.00098454
19 | 0.0093734 | 0.0023492
20 | 0.013038 | 0.0032677
21 | 0.0050254 | 0.0012595
22 | 0.0015247 | 0.00038212

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1