## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1631-14_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1631-14_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1631-14_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1631-14_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1631-14_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1631-14_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1631-14_0_3_node_46 | 0.4 | n |  | TRUE
7 | bus_LV_1631-14_0_3_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_1631-14_0_3_node_21 | 0.4 | n |  | TRUE
9 | bus_LV_1631-14_0_3_node_23 | 0.4 | n |  | TRUE
10 | bus_LV_1631-14_0_3_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1631-14_0_3_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_1631-14_0_3_node_45 | 0.4 | n |  | TRUE
13 | bus_LV_1631-14_0_3_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_1631-14_0_3_node_34 | 0.4 | n |  | TRUE
15 | bus_LV_1631-14_0_3_node_33 | 0.4 | n |  | TRUE
16 | bus_LV_1631-14_0_3_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_1631-14_0_3_node_44 | 0.4 | n |  | TRUE
18 | bus_LV_1631-14_0_3_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_1631-14_0_3_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_1631-14_0_3_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_1631-14_0_3_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_1631-14_0_3_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_1631-14_0_3_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_1631-14_0_3_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_1631-14_0_3_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_1631-14_0_3_node_26 | 0.4 | n |  | TRUE
27 | bus_LV_1631-14_0_3_node_32 | 0.4 | n |  | TRUE
28 | bus_LV_1631-14_0_3_node_31 | 0.4 | n |  | TRUE
29 | bus_LV_1631-14_0_3_node_51 | 0.4 | n |  | TRUE
30 | bus_LV_1631-14_0_3_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_1631-14_0_3_node_30 | 0.4 | n |  | TRUE
32 | bus_LV_1631-14_0_3_node_39 | 0.4 | n |  | TRUE
33 | bus_LV_1631-14_0_3_node_49 | 0.4 | n |  | TRUE
34 | bus_LV_1631-14_0_3_node_36 | 0.4 | n |  | TRUE
35 | bus_LV_1631-14_0_3_node_29 | 0.4 | n |  | TRUE
36 | bus_LV_1631-14_0_3_node_38 | 0.4 | n |  | TRUE
37 | bus_LV_1631-14_0_3_node_35 | 0.4 | n |  | TRUE
38 | bus_LV_1631-14_0_3_node_20 | 0.4 | n |  | TRUE
39 | bus_LV_1631-14_0_3_node_22 | 0.4 | n |  | TRUE
40 | bus_LV_1631-14_0_3_node_25 | 0.4 | n |  | TRUE
41 | bus_LV_1631-14_0_3_node_27 | 0.4 | n |  | TRUE
42 | bus_LV_1631-14_0_3_node_28 | 0.4 | n |  | TRUE
43 | bus_LV_1631-14_0_3_node_41 | 0.4 | n |  | TRUE
44 | bus_LV_1631-14_0_3_node_50 | 0.4 | n |  | TRUE
45 | bus_LV_1631-14_0_3_node_42 | 0.4 | n |  | TRUE
46 | bus_LV_1631-14_0_3_node_43 | 0.4 | n |  | TRUE
47 | bus_LV_1631-14_0_3_node_48 | 0.4 | n |  | TRUE
48 | bus_MV_144_0_node_6 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1631-14_0_3_load_0 | 0 | 0.0017913 | 0.00044894 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1631-14_0_3_load_2 | 2 | 0.004828 | 0.00121 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1631-14_0_3_load_5 | 5 | 0.0042527 | 0.0010658 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1631-14_0_3_load_46 | 6 | 0.0053542 | 0.0013419 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1631-14_0_3_load_23 | 9 | 0.0080884 | 0.0020271 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1631-14_0_3_load_45 | 12 | 0.0060619 | 0.0015193 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1631-14_0_3_load_33 | 15 | 0.0018879 | 0.00047315 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1631-14_0_3_load_10 | 16 | 0.0022975 | 0.00057582 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1631-14_0_3_load_44 | 17 | 0.0041067 | 0.0010292 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1631-14_0_3_load_11 | 18 | 0.0044962 | 0.0011269 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1631-14_0_3_load_16 | 19 | 0.0087454 | 0.0021918 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1631-14_0_3_load_19 | 20 | 0.0084419 | 0.0021157 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1631-14_0_3_load_12 | 21 | 0.0074994 | 0.0018795 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1631-14_0_3_load_32 | 27 | 0.0077278 | 0.0019368 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1631-14_0_3_load_31 | 28 | 0.0066258 | 0.0016606 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1631-14_0_3_load_51 | 29 | 0.0037308 | 0.00093503 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1631-14_0_3_load_24 | 30 | 0.0062362 | 0.001563 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1631-14_0_3_load_30 | 31 | 0.0078004 | 0.001955 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1631-14_0_3_load_49 | 33 | 0.016022 | 0.0040154 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1631-14_0_3_load_29 | 35 | 0.0073741 | 0.0018481 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1631-14_0_3_load_35 | 37 | 0.022903 | 0.0057401 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1631-14_0_3_load_20 | 38 | 0.0047762 | 0.001197 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1631-14_0_3_load_22 | 39 | 0.0064333 | 0.0016123 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1631-14_0_3_load_27 | 41 | 0.0072485 | 0.0018166 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1631-14_0_3_load_50 | 44 | 0.010667 | 0.0026733 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1631-14_0_3_load_42 | 45 | 0.013171 | 0.003301 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1631-14_0_3_load_43 | 46 | 0.012545 | 0.003144 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1631-14_0_3_load_48 | 47 | 0.02998 | 0.0075137 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 28 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1631-14_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.033874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1631-14_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.039303 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1631-14_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.023823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1631-14_0_3_line_3 | NAYY 4x150 SE | 1 | 4 | 0.11452 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1631-14_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.009322 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1631-14_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.018199 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1631-14_0_3_line_6 | NAYY 4x150 SE | 5 | 11 | 0.0053524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1631-14_0_3_line_7 | NAYY 4x150 SE | 6 | 12 | 0.069277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1631-14_0_3_line_8 | NAYY 4x150 SE | 7 | 8 | 0.031485 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1631-14_0_3_line_9 | NAYY 4x150 SE | 7 | 9 | 0.015846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1631-14_0_3_line_10 | NAYY 4x150 SE | 7 | 10 | 0.024835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1631-14_0_3_line_11 | NAYY 4x150 SE | 8 | 19 | 0.033057 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1631-14_0_3_line_12 | NAYY 4x150 SE | 8 | 20 | 0.023512 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1631-14_0_3_line_13 | NAYY 4x150 SE | 10 | 16 | 0.019508 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1631-14_0_3_line_14 | NAYY 4x150 SE | 10 | 11 | 0.016457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1631-14_0_3_line_15 | NAYY 4x150 SE | 11 | 13 | 0.023587 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1631-14_0_3_line_16 | NAYY 4x150 SE | 13 | 14 | 0.031547 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1631-14_0_3_line_17 | NAYY 4x150 SE | 13 | 15 | 0.013784 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1631-14_0_3_line_18 | NAYY 4x150 SE | 14 | 17 | 0.030732 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1631-14_0_3_line_19 | NAYY 4x150 SE | 16 | 18 | 0.0038602 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1631-14_0_3_line_20 | NAYY 4x150 SE | 19 | 22 | 0.013219 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1631-14_0_3_line_21 | NAYY 4x150 SE | 20 | 38 | 0.0076869 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1631-14_0_3_line_22 | NAYY 4x150 SE | 21 | 22 | 0.023894 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1631-14_0_3_line_23 | NAYY 4x150 SE | 22 | 23 | 0.065681 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1631-14_0_3_line_24 | NAYY 4x150 SE | 22 | 24 | 0.0099024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1631-14_0_3_line_25 | NAYY 4x150 SE | 23 | 28 | 0.062982 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1631-14_0_3_line_26 | NAYY 4x150 SE | 24 | 29 | 0.009778 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1631-14_0_3_line_27 | NAYY 4x150 SE | 25 | 26 | 0.009545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
28 | LV_1631-14_0_3_line_28 | NAYY 4x150 SE | 25 | 27 | 0.02204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
29 | LV_1631-14_0_3_line_29 | NAYY 4x150 SE | 26 | 30 | 0.013965 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
30 | LV_1631-14_0_3_line_30 | NAYY 4x150 SE | 27 | 31 | 0.0086952 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
31 | LV_1631-14_0_3_line_31 | NAYY 4x150 SE | 28 | 35 | 0.0071486 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
32 | LV_1631-14_0_3_line_32 | NAYY 4x150 SE | 30 | 40 | 0.029044 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
33 | LV_1631-14_0_3_line_33 | NAYY 4x150 SE | 31 | 35 | 0.014359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
34 | LV_1631-14_0_3_line_34 | NAYY 4x150 SE | 32 | 33 | 0.019095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1631-14_0_3_line_35 | NAYY 4x150 SE | 32 | 34 | 0.021172 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1631-14_0_3_line_36 | NAYY 4x150 SE | 34 | 36 | 0.074376 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1631-14_0_3_line_37 | NAYY 4x150 SE | 34 | 37 | 0.023659 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1631-14_0_3_line_38 | NAYY 4x150 SE | 36 | 47 | 0.02114 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1631-14_0_3_line_39 | NAYY 4x150 SE | 36 | 43 | 0.009635 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1631-14_0_3_line_40 | NAYY 4x150 SE | 38 | 39 | 0.012654 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1631-14_0_3_line_41 | NAYY 4x150 SE | 40 | 41 | 0.030083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1631-14_0_3_line_42 | NAYY 4x150 SE | 40 | 42 | 0.070185 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1631-14_0_3_line_43 | NAYY 4x150 SE | 41 | 43 | 0.0082748 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1631-14_0_3_line_44 | NAYY 4x150 SE | 42 | 44 | 0.023323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1631-14_0_3_line_45 | NAYY 4x150 SE | 43 | 45 | 0.007276 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1631-14_0_3_line_46 | NAYY 4x150 SE | 43 | 46 | 0.013058 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1631-14_0_3_trafo_31 | 0.25 MVA 20/0.4 kV | 48 | 28 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2724851.7789 | 1207737.4693 | 2724860.846 | 1207749.7906 | 2724868.6038 | 1207766.6688
1 | 2724885.7651 | 1207802.0186 | 2724876.0647 | 1207782.901 | 2724868.6038 | 1207766.6688
2 | 2724851.7789 | 1207737.4693 | 2724842.4289 | 1207751.0174 | 2724838.2027 | 1207757.067
3 | 2724851.7789 | 1207737.4693 | 2724855.1606 | 1207733.9818 | 2724860.675 | 1207729.983 | 2724867.5369 | 1207726.2903 | 2724871.1698 | 1207724.6095 | 2724874.7171 | 1207723.3828 | 2724917.5211 | 1207708.6337 | 2724924.9532 | 1207706.7767 | 2724938.2279 | 1207703.4075 | 2724951.4511 | 1207704.3183 | 2724952.8959 | 1207711.5986
4 | 2724838.2027 | 1207757.067 | 2724834.5737 | 1207762.195 | 2724832.8463 | 1207764.6964
5 | 2724952.8959 | 1207711.5986 | 2724941.3491 | 1207725.6658
6 | 2724829.8048 | 1207769.1006 | 2724832.8463 | 1207764.6964
7 | 2724931.1478 | 1207790.3023 | 2724926.6644 | 1207780.5024 | 2724925.3372 | 1207770.5114 | 2724928.8047 | 1207748.7673 | 2724938.0814 | 1207729.6468 | 2724941.3491 | 1207725.6658
8 | 2724852.8017 | 1207803.4301 | 2724858.465 | 1207811.2101 | 2724861.1146 | 1207816.1693 | 2724863.1931 | 1207821.8838 | 2724865.8474 | 1207831.7024
9 | 2724852.8017 | 1207803.4301 | 2724839.7954 | 1207812.4809
10 | 2724852.8017 | 1207803.4301 | 2724838.6796 | 1207782.9746
11 | 2724865.8474 | 1207831.7024 | 2724873.486 | 1207859.9283 | 2724874.2947 | 1207863.6579
12 | 2724865.8474 | 1207831.7024 | 2724845.3 | 1207843.1313
13 | 2724838.6796 | 1207782.9746 | 2724822.6123 | 1207794.0376
14 | 2724838.6796 | 1207782.9746 | 2724829.8048 | 1207769.1006
15 | 2724829.8048 | 1207769.1006 | 2724824.1275 | 1207774.3414 | 2724810.42 | 1207782.4054
16 | 2724783.258 | 1207798.4498 | 2724804.7519 | 1207785.7562 | 2724810.42 | 1207782.4054
17 | 2724810.42 | 1207782.4054 | 2724803.1104 | 1207770.719
18 | 2724783.258 | 1207798.4498 | 2724790.4429 | 1207810.576 | 2724800.8988 | 1207823.5165
19 | 2724819.4329 | 1207796.2267 | 2724822.6123 | 1207794.0376
20 | 2724876.6885 | 1207876.6192 | 2724876.6975 | 1207874.7401 | 2724874.2947 | 1207863.6579
21 | 2724845.3 | 1207843.1313 | 2724838.5823 | 1207846.8678
22 | 2724876.6885 | 1207876.6192 | 2724891.5459 | 1207884.8252 | 2724897.4577 | 1207881.227
23 | 2724860.917 | 1207924.0701 | 2724885.282 | 1207910.4582 | 2724886.8115 | 1207908.2441 | 2724887.0539 | 1207906.1142 | 2724886.6944 | 1207904.0273 | 2724874.7889 | 1207879.4372 | 2724875.9191 | 1207878.4934 | 2724876.6885 | 1207876.6192
24 | 2724869.099 | 1207882.3759 | 2724874.7889 | 1207879.4372 | 2724875.9191 | 1207878.4934 | 2724876.6885 | 1207876.6192
25 | 2724860.917 | 1207924.0701 | 2724871.3383 | 1207943.2583 | 2724875.7047 | 1207945.4069 | 2724882.2584 | 1207941.5299 | 2724887.6121 | 1207943.0208 | 2724891.9033 | 1207950.9389 | 2724898.9937 | 1207958.4819 | 2724902.4914 | 1207959.8324
26 | 2724869.099 | 1207882.3759 | 2724864.5033 | 1207873.7398
27 | 2724949.2029 | 1207967.0282 | 2724953.3658 | 1207975.6219
28 | 2724949.2029 | 1207967.0282 | 2724934.3814 | 1207970.921 | 2724930.17 | 1207965.6894
29 | 2724953.3658 | 1207975.6219 | 2724956.4569 | 1207982.0027 | 2724959.1106 | 1207988.3443
30 | 2724922.8426 | 1207961.8836 | 2724925.162 | 1207961.8989 | 2724928.8366 | 1207964.0329 | 2724930.17 | 1207965.6894
31 | 2724909.1603 | 1207962.4071 | 2724902.4914 | 1207959.8324
32 | 2724969.5839 | 1208015.4253 | 2724964.0332 | 1208000.1085 | 2724959.1106 | 1207988.3443
33 | 2724909.1603 | 1207962.4071 | 2724912.4234 | 1207963.6669 | 2724916.3899 | 1207964.2059 | 2724922.8426 | 1207961.8836 | 2724922.8426 | 1207961.8836
34 | 2724852.3631 | 1208022.044 | 2724869.2096 | 1208012.9672
35 | 2724861.8773 | 1208040.9575 | 2724860.512 | 1208038.238 | 2724856.1675 | 1208029.596 | 2724852.3631 | 1208022.044
36 | 2724861.8773 | 1208040.9575 | 2724877.1099 | 1208033.4037 | 2724880.2433 | 1208038.8623 | 2724924.4496 | 1208012.9787
37 | 2724861.8773 | 1208040.9575 | 2724872.5099 | 1208062.093
38 | 2724924.4496 | 1208012.9787 | 2724919.5771 | 1208033.548
39 | 2724932.7371 | 1208008.0261 | 2724924.4496 | 1208012.9787
40 | 2724838.5823 | 1207846.8678 | 2724830.8019 | 1207851.1954 | 2724827.1301 | 1207850.4278
41 | 2724969.5839 | 1208015.4253 | 2724963.0556 | 1208014.0987 | 2724942.6969 | 1208007.1116 | 2724940.816 | 1208006.8666
42 | 2724968.4644 | 1208079.0173 | 2724976.4102 | 1208074.0354 | 2724978.8476 | 1208069.8722 | 2724980.1048 | 1208065.7731 | 2724980.5927 | 1208061.7247 | 2724979.9816 | 1208057.1306 | 2724971.4084 | 1208023.0916 | 2724969.5839 | 1208015.4253
43 | 2724932.7371 | 1208008.0261 | 2724935.3581 | 1208007.0802 | 2724939.443 | 1208006.6877 | 2724940.816 | 1208006.8666
44 | 2724968.4644 | 1208079.0173 | 2724956.8411 | 1208058.7807
45 | 2724932.7371 | 1208008.0261 | 2724929.0197 | 1208001.7657
46 | 2724932.7371 | 1208008.0261 | 2724939.7236 | 1208019.0697

## bus_geodata
| x | y | coords
0 | 2724868.6038 | 1207766.6688
1 | 2724851.7789 | 1207737.4693
2 | 2724885.7651 | 1207802.0186
3 | 2724838.2027 | 1207757.067
4 | 2724952.8959 | 1207711.5986
5 | 2724832.8463 | 1207764.6964
6 | 2724941.3491 | 1207725.6658
7 | 2724852.8017 | 1207803.4301
8 | 2724865.8474 | 1207831.7024
9 | 2724839.7954 | 1207812.4809
10 | 2724838.6796 | 1207782.9746
11 | 2724829.8047 | 1207769.1006
12 | 2724931.1478 | 1207790.3023
13 | 2724810.42 | 1207782.4054
14 | 2724783.258 | 1207798.4498
15 | 2724803.1104 | 1207770.719
16 | 2724822.6123 | 1207794.0376
17 | 2724800.8988 | 1207823.5165
18 | 2724819.4329 | 1207796.2267
19 | 2724874.2947 | 1207863.6579
20 | 2724845.3 | 1207843.1313
21 | 2724897.4577 | 1207881.227
22 | 2724876.6885 | 1207876.6192
23 | 2724860.917 | 1207924.0701
24 | 2724869.099 | 1207882.3759
25 | 2724949.2029 | 1207967.0282
26 | 2724953.3658 | 1207975.6219
27 | 2724930.17 | 1207965.6894
28 | 2724902.4914 | 1207959.8324
29 | 2724864.5033 | 1207873.7398
30 | 2724959.1106 | 1207988.3443
31 | 2724922.8426 | 1207961.8836
32 | 2724852.3631 | 1208022.044
33 | 2724869.2096 | 1208012.9672
34 | 2724861.8773 | 1208040.9575
35 | 2724909.1603 | 1207962.4071
36 | 2724924.4496 | 1208012.9787
37 | 2724872.5099 | 1208062.093
38 | 2724838.5823 | 1207846.8678
39 | 2724827.1301 | 1207850.4278
40 | 2724969.5839 | 1208015.4253
41 | 2724940.816 | 1208006.8666
42 | 2724968.4644 | 1208079.0173
43 | 2724932.7371 | 1208008.0261
44 | 2724956.8411 | 1208058.7807
45 | 2724929.0197 | 1208001.7657
46 | 2724939.7236 | 1208019.0697
47 | 2724919.5771 | 1208033.548
48 | 2724949.2029 | 1207967.0282

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97475 | -0.17741 | 0.0017913 | 0.00044894
1 | 0.97508 | -0.17505 | 0 | 0
2 | 0.97447 | -0.1794 | 0.004828 | 0.00121
3 | 0.9757 | -0.17054 | 0 | 0
4 | 0.97316 | -0.18882 | 0 | 0
5 | 0.97595 | -0.16877 | 0.0042527 | 0.0010658
6 | 0.97285 | -0.19101 | 0.0053542 | 0.0013419
7 | 0.97808 | -0.15353 | 0 | 0
8 | 0.98007 | -0.13937 | 0 | 0
9 | 0.97789 | -0.15487 | 0.0080884 | 0.0020271
10 | 0.97681 | -0.16264 | 0 | 0
11 | 0.97613 | -0.16752 | 0 | 0
12 | 0.97224 | -0.19545 | 0.0060619 | 0.0015193
13 | 0.97592 | -0.16901 | 0 | 0
14 | 0.97573 | -0.17037 | 0 | 0
15 | 0.97588 | -0.16928 | 0.0018879 | 0.00047315
16 | 0.97661 | -0.16403 | 0.0022975 | 0.00057582
17 | 0.97554 | -0.17169 | 0.0041067 | 0.0010292
18 | 0.97659 | -0.16421 | 0.0044962 | 0.0011269
19 | 0.9831 | -0.11784 | 0.0087454 | 0.0021918
20 | 0.97939 | -0.14417 | 0.0084419 | 0.0021157
21 | 0.98422 | -0.10992 | 0.0074994 | 0.0018795
22 | 0.98448 | -0.10808 | 0 | 0
23 | 0.9924 | -0.052485 | 0 | 0
24 | 0.98442 | -0.10846 | 0 | 0
25 | 0.99518 | -0.033402 | 0 | 0
26 | 0.99436 | -0.039121 | 0 | 0
27 | 0.99708 | -0.020232 | 0.0077278 | 0.0019368
28 | 1 | 0 | -0.22902 | -0.057683
29 | 0.98437 | -0.10883 | 0.0037308 | 0.00093503
30 | 0.99316 | -0.047504 | 0.0062362 | 0.001563
31 | 0.99787 | -0.014713 | 0.0078004 | 0.001955
32 | 0.97953 | -0.14375 | 0 | 0
33 | 0.97908 | -0.14694 | 0.016022 | 0.0040154
34 | 0.98002 | -0.14023 | 0 | 0
35 | 0.99927 | -0.0050594 | 0.0073741 | 0.0018481
36 | 0.98424 | -0.11027 | 0 | 0
37 | 0.97923 | -0.14586 | 0.022903 | 0.0057401
38 | 0.97927 | -0.14507 | 0.0047762 | 0.001197
39 | 0.97915 | -0.14592 | 0.0064333 | 0.0016123
40 | 0.99079 | -0.064085 | 0 | 0
41 | 0.98634 | -0.095388 | 0.0072485 | 0.0018166
42 | 0.98971 | -0.071708 | 0 | 0
43 | 0.9852 | -0.10343 | 0 | 0
44 | 0.98935 | -0.074244 | 0.010667 | 0.0026733
45 | 0.98506 | -0.10442 | 0.013171 | 0.003301
46 | 0.98497 | -0.10512 | 0.012545 | 0.003144
47 | 0.98332 | -0.1168 | 0.02998 | 0.0075137
48 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0066207 | -0.001659 | 0.0066228 | 0.0016594 | 2.1591e-06 | 4.0803e-07 | 0.010107 | 0.010107 | 0.010107 | 0.97475 | -0.17741 | 0.97508 | -0.17505 | 3.7433
1 | 0.0048294 | 0.00121 | -0.004828 | -0.00121 | 1.3329e-06 | 2.2903e-08 | 0.0073722 | 0.0073724 | 0.0073724 | 0.97475 | -0.17741 | 0.97447 | -0.1794 | 2.7305
2 | -0.018068 | -0.0045292 | 0.018079 | 0.0045332 | 1.1302e-05 | 4.0494e-06 | 0.027573 | 0.027573 | 0.027573 | 0.97508 | -0.17505 | 0.9757 | -0.17054 | 10.2122
3 | 0.011445 | 0.0028698 | -0.011423 | -0.0028628 | 2.1802e-05 | 6.9596e-06 | 0.017466 | 0.017467 | 0.017467 | 0.97508 | -0.17505 | 0.97316 | -0.18882 | 6.4692
4 | -0.018079 | -0.0045332 | 0.018084 | 0.0045348 | 4.4224e-06 | 1.5845e-06 | 0.027573 | 0.027573 | 0.027573 | 0.9757 | -0.17054 | 0.97595 | -0.16877 | 10.2121
5 | 0.011423 | 0.0028628 | -0.01142 | -0.0028617 | 3.4647e-06 | 1.1065e-06 | 0.017467 | 0.017467 | 0.017467 | 0.97316 | -0.18882 | 0.97285 | -0.19101 | 6.4692
6 | -0.022336 | -0.0056006 | 0.02234 | 0.0056021 | 3.8738e-06 | 1.423e-06 | 0.034057 | 0.034057 | 0.034057 | 0.97595 | -0.16877 | 0.97613 | -0.16752 | 12.6136
7 | 0.0060656 | 0.0015198 | -0.0060619 | -0.0015193 | 3.7208e-06 | 5.7145e-07 | 0.0092774 | 0.0092777 | 0.0092777 | 0.97285 | -0.19101 | 0.97224 | -0.19545 | 3.4362
8 | -0.043286 | -0.010859 | 0.043372 | 0.010891 | 8.5212e-05 | 3.2378e-05 | 0.065858 | 0.065858 | 0.065858 | 0.97808 | -0.15353 | 0.98007 | -0.13937 | 24.3918
9 | 0.0080899 | 0.0020275 | -0.0080884 | -0.0020271 | 1.4978e-06 | 3.7724e-07 | 0.012308 | 0.012308 | 0.012308 | 0.97808 | -0.15353 | 0.97789 | -0.15487 | 4.5584
10 | 0.035196 | 0.0088312 | -0.035152 | -0.0088144 | 4.444e-05 | 1.6781e-05 | 0.05355 | 0.05355 | 0.05355 | 0.97808 | -0.15353 | 0.97681 | -0.16264 | 19.8334
11 | -0.063038 | -0.015821 | 0.063227 | 0.015894 | 0.00018899 | 7.2271e-05 | 0.095718 | 0.095718 | 0.095718 | 0.98007 | -0.13937 | 0.9831 | -0.11784 | 35.451
12 | 0.019667 | 0.0049304 | -0.019654 | -0.0049257 | 1.3081e-05 | 4.7353e-06 | 0.02986 | 0.02986 | 0.02986 | 0.98007 | -0.13937 | 0.97939 | -0.14417 | 11.0593
13 | 0.0067952 | 0.0017029 | -0.0067939 | -0.0017027 | 1.3043e-06 | 2.5753e-07 | 0.010351 | 0.010351 | 0.010351 | 0.97681 | -0.16264 | 0.97661 | -0.16403 | 3.8339
14 | 0.028357 | 0.0071114 | -0.028338 | -0.0071043 | 1.9164e-05 | 7.1648e-06 | 0.043199 | 0.043199 | 0.043199 | 0.97681 | -0.16264 | 0.97613 | -0.16752 | 15.9996
15 | 0.0059974 | 0.0015022 | -0.0059962 | -0.001502 | 1.2302e-06 | 1.7836e-07 | 0.0091422 | 0.0091423 | 0.0091423 | 0.97613 | -0.16752 | 0.97592 | -0.16901 | 3.386
16 | 0.0041082 | 0.001029 | -0.0041074 | -0.0010291 | 7.7235e-07 | -9.7044e-08 | 0.0062637 | 0.0062639 | 0.0062639 | 0.97592 | -0.16901 | 0.97573 | -0.17037 | 2.32
17 | 0.001888 | 0.00047301 | -0.0018879 | -0.00047315 | 7.1275e-08 | -1.4481e-07 | 0.0028786 | 0.0028787 | 0.0028787 | 0.97592 | -0.16901 | 0.97588 | -0.16928 | 1.0662
18 | 0.0041074 | 0.0010291 | -0.0041067 | -0.0010292 | 7.5243e-07 | -9.4376e-08 | 0.0062639 | 0.006264 | 0.006264 | 0.97573 | -0.17037 | 0.97554 | -0.17169 | 2.32
19 | 0.0044964 | 0.0011269 | -0.0044962 | -0.0011269 | 1.1305e-07 | -4.8185e-09 | 0.0068509 | 0.0068509 | 0.0068509 | 0.97661 | -0.16403 | 0.97659 | -0.16421 | 2.5374
20 | -0.071973 | -0.018086 | 0.072071 | 0.018123 | 9.792e-05 | 3.7494e-05 | 0.10895 | 0.10895 | 0.10895 | 0.9831 | -0.11784 | 0.98448 | -0.10808 | 40.3536
21 | 0.011212 | 0.0028099 | -0.01121 | -0.0028095 | 1.3918e-06 | 4.3859e-07 | 0.017034 | 0.017034 | 0.017034 | 0.97939 | -0.14417 | 0.97927 | -0.14507 | 6.309
22 | -0.0074994 | -0.0018795 | 0.0075014 | 0.00188 | 1.9167e-06 | 4.3346e-07 | 0.011338 | 0.011338 | 0.011338 | 0.98422 | -0.10992 | 0.98448 | -0.10808 | 4.1993
23 | -0.083303 | -0.020938 | 0.083953 | 0.021187 | 0.00064998 | 0.00024915 | 0.12593 | 0.12593 | 0.12593 | 0.98448 | -0.10808 | 0.9924 | -0.052485 | 46.6416
24 | 0.0037312 | 0.00093493 | -0.003731 | -0.00093498 | 1.9653e-07 | -5.0316e-08 | 0.0056396 | 0.0056396 | 0.0056396 | 0.98448 | -0.10808 | 0.98442 | -0.10846 | 2.0888
25 | -0.083953 | -0.021187 | 0.084576 | 0.021426 | 0.00062326 | 0.0002389 | 0.12593 | 0.12593 | 0.12593 | 0.9924 | -0.052485 | 1 | 0 | 46.6415
26 | 0.003731 | 0.00093498 | -0.0037308 | -0.00093503 | 1.9406e-07 | -4.967e-08 | 0.0056396 | 0.0056397 | 0.0056397 | 0.98442 | -0.10846 | 0.98437 | -0.10883 | 2.0888
27 | 0.12013 | 0.030285 | -0.12004 | -0.030248 | 9.6154e-05 | 3.6735e-05 | 0.17969 | 0.17969 | 0.17969 | 0.99518 | -0.033402 | 0.99436 | -0.039121 | 33.2756
28 | -0.12013 | -0.030285 | 0.12035 | 0.03037 | 0.00022203 | 8.4822e-05 | 0.17969 | 0.17969 | 0.17969 | 0.99518 | -0.033402 | 0.99708 | -0.020232 | 33.2756
29 | 0.12004 | 0.030248 | -0.1199 | -0.030194 | 0.00014068 | 5.3744e-05 | 0.17969 | 0.17969 | 0.17969 | 0.99436 | -0.039121 | 0.99316 | -0.047504 | 33.2756
30 | -0.12808 | -0.032307 | 0.12818 | 0.032344 | 9.9198e-05 | 3.7926e-05 | 0.19122 | 0.19122 | 0.19122 | 0.99708 | -0.020232 | 0.99787 | -0.014713 | 35.4112
31 | 0.14364 | 0.036257 | -0.14354 | -0.036218 | 0.00010198 | 3.9037e-05 | 0.21383 | 0.21383 | 0.21383 | 1 | 0 | 0.99927 | -0.0050594 | 39.5987
32 | 0.11366 | 0.028632 | -0.1134 | -0.028531 | 0.00026295 | 0.00010038 | 0.17034 | 0.17034 | 0.17034 | 0.99316 | -0.047504 | 0.99079 | -0.064085 | 31.5454
33 | -0.13598 | -0.034299 | 0.13617 | 0.03437 | 0.00018434 | 7.0526e-05 | 0.20285 | 0.20285 | 0.20285 | 0.99787 | -0.014713 | 0.99927 | -0.0050594 | 37.5653
34 | 0.016029 | 0.0040179 | -0.016022 | -0.0040154 | 7.0647e-06 | 2.477e-06 | 0.02435 | 0.02435 | 0.02435 | 0.97953 | -0.14375 | 0.97908 | -0.14694 | 9.0185
35 | -0.016029 | -0.0040179 | 0.016037 | 0.0040206 | 7.833e-06 | 2.7461e-06 | 0.02435 | 0.02435 | 0.02435 | 0.97953 | -0.14375 | 0.98002 | -0.14023 | 9.0184
36 | -0.038958 | -0.0097674 | 0.03912 | 0.0098289 | 0.00016239 | 6.1518e-05 | 0.059153 | 0.059153 | 0.059153 | 0.98002 | -0.14023 | 0.98424 | -0.11027 | 21.9085
37 | 0.022921 | 0.0057467 | -0.022903 | -0.0057401 | 1.7882e-05 | 6.58e-06 | 0.034803 | 0.034803 | 0.034803 | 0.98002 | -0.14023 | 0.97923 | -0.14586 | 12.8901
38 | 0.030007 | 0.0075239 | -0.02998 | -0.0075137 | 2.7151e-05 | 1.0174e-05 | 0.045368 | 0.045368 | 0.045368 | 0.98424 | -0.11027 | 0.98332 | -0.1168 | 16.8028
39 | -0.069128 | -0.017353 | 0.069193 | 0.017378 | 6.568e-05 | 2.5139e-05 | 0.10452 | 0.10452 | 0.10452 | 0.98424 | -0.11027 | 0.9852 | -0.10343 | 38.7112
40 | 0.0064341 | 0.0016125 | -0.0064333 | -0.0016123 | 7.5476e-07 | 1.3111e-07 | 0.0097767 | 0.0097768 | 0.0097768 | 0.97927 | -0.14507 | 0.97915 | -0.14592 | 3.621
41 | 0.10272 | 0.025853 | -0.10227 | -0.025682 | 0.00044694 | 0.00017151 | 0.1543 | 0.1543 | 0.1543 | 0.99079 | -0.064085 | 0.98634 | -0.095388 | 57.149
42 | 0.010682 | 0.0026779 | -0.01067 | -0.0026745 | 1.1272e-05 | 3.4324e-06 | 0.016043 | 0.016043 | 0.016043 | 0.99079 | -0.064085 | 0.98971 | -0.071708 | 5.9418
43 | 0.09502 | 0.023865 | -0.094914 | -0.023824 | 0.00010613 | 4.0714e-05 | 0.14337 | 0.14337 | 0.14337 | 0.98634 | -0.095388 | 0.9852 | -0.10343 | 53.099
44 | 0.01067 | 0.0026745 | -0.010667 | -0.0026733 | 3.7458e-06 | 1.1411e-06 | 0.016043 | 0.016043 | 0.016043 | 0.98971 | -0.071708 | 0.98935 | -0.074244 | 5.9419
45 | 0.013173 | 0.0033016 | -0.013171 | -0.003301 | 1.7972e-06 | 5.986e-07 | 0.019896 | 0.019896 | 0.019896 | 0.9852 | -0.10343 | 0.98506 | -0.10442 | 7.3688
46 | 0.012547 | 0.0031449 | -0.012545 | -0.003144 | 2.9265e-06 | 9.5932e-07 | 0.018951 | 0.018951 | 0.018951 | 0.9852 | -0.10343 | 0.98497 | -0.10512 | 7.019

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.23564 | 0.059344

## res_load
| p_mw | q_mvar
0 | 0.0017913 | 0.00044894
1 | 0.004828 | 0.00121
2 | 0.0042527 | 0.0010658
3 | 0.0053542 | 0.0013419
4 | 0.0080884 | 0.0020271
5 | 0.0060619 | 0.0015193
6 | 0.0018879 | 0.00047315
7 | 0.0022975 | 0.00057582
8 | 0.0041067 | 0.0010292
9 | 0.0044962 | 0.0011269
10 | 0.0087454 | 0.0021918
11 | 0.0084419 | 0.0021157
12 | 0.0074994 | 0.0018795
13 | 0.0077278 | 0.0019368
14 | 0.0066258 | 0.0016606
15 | 0.0037308 | 0.00093503
16 | 0.0062362 | 0.001563
17 | 0.0078004 | 0.001955
18 | 0.016022 | 0.0040154
19 | 0.0073741 | 0.0018481
20 | 0.022903 | 0.0057401
21 | 0.0047762 | 0.001197
22 | 0.0064333 | 0.0016123
23 | 0.0072485 | 0.0018166
24 | 0.010667 | 0.0026733
25 | 0.013171 | 0.003301
26 | 0.012545 | 0.003144
27 | 0.02998 | 0.0075137

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1