## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1631-155_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1631-155_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1631-155_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1631-155_0_4_node_7 | 0.4 | n |  | TRUE
4 | bus_LV_1631-155_0_4_node_9 | 0.4 | n |  | TRUE
5 | bus_LV_1631-155_0_4_node_10 | 0.4 | n |  | TRUE
6 | bus_LV_1631-155_0_4_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_1631-155_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1631-155_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1631-155_0_4_node_14 | 0.4 | n |  | TRUE
10 | bus_LV_1631-155_0_4_node_12 | 0.4 | n |  | TRUE
11 | bus_LV_1631-155_0_4_node_18 | 0.4 | n |  | TRUE
12 | bus_LV_1631-155_0_4_node_17 | 0.4 | n |  | TRUE
13 | bus_LV_1631-155_0_4_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_1631-155_0_4_node_13 | 0.4 | n |  | TRUE
15 | bus_LV_1631-155_0_4_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_1631-155_0_4_node_16 | 0.4 | n |  | TRUE
17 | bus_LV_1631-155_0_4_node_24 | 0.4 | n |  | TRUE
18 | bus_LV_1631-155_0_4_node_19 | 0.4 | n |  | TRUE
19 | bus_LV_1631-155_0_4_node_36 | 0.4 | n |  | TRUE
20 | bus_LV_1631-155_0_4_node_34 | 0.4 | n |  | TRUE
21 | bus_LV_1631-155_0_4_node_26 | 0.4 | n |  | TRUE
22 | bus_LV_1631-155_0_4_node_22 | 0.4 | n |  | TRUE
23 | bus_LV_1631-155_0_4_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_1631-155_0_4_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_1631-155_0_4_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_1631-155_0_4_node_25 | 0.4 | n |  | TRUE
27 | bus_LV_1631-155_0_4_node_54 | 0.4 | n |  | TRUE
28 | bus_LV_1631-155_0_4_node_43 | 0.4 | n |  | TRUE
29 | bus_LV_1631-155_0_4_node_55 | 0.4 | n |  | TRUE
30 | bus_LV_1631-155_0_4_node_45 | 0.4 | n |  | TRUE
31 | bus_LV_1631-155_0_4_node_41 | 0.4 | n |  | TRUE
32 | bus_LV_1631-155_0_4_node_27 | 0.4 | n |  | TRUE
33 | bus_LV_1631-155_0_4_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_1631-155_0_4_node_29 | 0.4 | n |  | TRUE
35 | bus_LV_1631-155_0_4_node_30 | 0.4 | n |  | TRUE
36 | bus_LV_1631-155_0_4_node_31 | 0.4 | n |  | TRUE
37 | bus_LV_1631-155_0_4_node_33 | 0.4 | n |  | TRUE
38 | bus_LV_1631-155_0_4_node_37 | 0.4 | n |  | TRUE
39 | bus_LV_1631-155_0_4_node_38 | 0.4 | n |  | TRUE
40 | bus_LV_1631-155_0_4_node_32 | 0.4 | n |  | TRUE
41 | bus_LV_1631-155_0_4_node_35 | 0.4 | n |  | TRUE
42 | bus_LV_1631-155_0_4_node_39 | 0.4 | n |  | TRUE
43 | bus_LV_1631-155_0_4_node_40 | 0.4 | n |  | TRUE
44 | bus_LV_1631-155_0_4_node_46 | 0.4 | n |  | TRUE
45 | bus_LV_1631-155_0_4_node_47 | 0.4 | n |  | TRUE
46 | bus_LV_1631-155_0_4_node_48 | 0.4 | n |  | TRUE
47 | bus_LV_1631-155_0_4_node_42 | 0.4 | n |  | TRUE
48 | bus_LV_1631-155_0_4_node_44 | 0.4 | n |  | TRUE
49 | bus_LV_1631-155_0_4_node_53 | 0.4 | n |  | TRUE
50 | bus_LV_1631-155_0_4_node_49 | 0.4 | n |  | TRUE
51 | bus_LV_1631-155_0_4_node_50 | 0.4 | n |  | TRUE
52 | bus_LV_1631-155_0_4_node_51 | 0.4 | n |  | TRUE
53 | bus_LV_1631-155_0_4_node_52 | 0.4 | n |  | TRUE
54 | bus_LV_1631-155_0_4_node_56 | 0.4 | n |  | TRUE
55 | bus_LV_1631-155_0_4_node_59 | 0.4 | n |  | TRUE
56 | bus_LV_1631-155_0_4_node_58 | 0.4 | n |  | TRUE
57 | bus_MV_144_0_node_202 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1631-155_0_4_load_0 | 0 | 0.0058089 | 0.0014558 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1631-155_0_4_load_1 | 1 | 0.005357 | 0.0013426 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1631-155_0_4_load_3 | 2 | 0.0051581 | 0.0012927 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1631-155_0_4_load_7 | 3 | 0.0080848 | 0.0020263 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1631-155_0_4_load_10 | 5 | 0.0046218 | 0.0011583 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1631-155_0_4_load_4 | 6 | 0.0041221 | 0.0010331 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1631-155_0_4_load_6 | 8 | 0.0038095 | 0.00095475 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1631-155_0_4_load_14 | 9 | 0.0048474 | 0.0012149 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1631-155_0_4_load_12 | 10 | 0.0068571 | 0.0017186 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1631-155_0_4_load_18 | 11 | 0.0052719 | 0.0013213 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1631-155_0_4_load_11 | 13 | 0.0060865 | 0.0015254 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1631-155_0_4_load_15 | 15 | 0.0094441 | 0.0023669 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1631-155_0_4_load_19 | 18 | 0.0037948 | 0.00095108 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1631-155_0_4_load_36 | 19 | 0.0038044 | 0.00095348 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1631-155_0_4_load_34 | 20 | 0.0041697 | 0.001045 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1631-155_0_4_load_26 | 21 | 0.0021828 | 0.00054707 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1631-155_0_4_load_22 | 22 | 0.0080068 | 0.0020067 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1631-155_0_4_load_20 | 23 | 0.0050557 | 0.0012671 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1631-155_0_4_load_21 | 24 | 0.0086555 | 0.0021693 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1631-155_0_4_load_23 | 25 | 0.0025479 | 0.00063856 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1631-155_0_4_load_25 | 26 | 0.004319 | 0.0010825 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1631-155_0_4_load_54 | 27 | 0.0035334 | 0.00088556 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1631-155_0_4_load_41 | 31 | 0.0060181 | 0.0015083 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1631-155_0_4_load_27 | 32 | 0.004136 | 0.0010366 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1631-155_0_4_load_28 | 33 | 0.0045133 | 0.0011311 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1631-155_0_4_load_31 | 36 | 0.0028151 | 0.00070554 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1631-155_0_4_load_33 | 37 | 0.0036991 | 0.00092708 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1631-155_0_4_load_38 | 39 | 0.0043463 | 0.0010893 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1631-155_0_4_load_32 | 40 | 0.0031268 | 0.00078364 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1631-155_0_4_load_35 | 41 | 0.0033479 | 0.00083905 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1631-155_0_4_load_39 | 42 | 0.00315 | 0.00078946 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1631-155_0_4_load_46 | 44 | 0.0047026 | 0.0011786 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1631-155_0_4_load_48 | 46 | 0.0057167 | 0.0014327 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1631-155_0_4_load_42 | 47 | 0.0030914 | 0.00077477 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1631-155_0_4_load_53 | 49 | 0.0031802 | 0.00079702 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1631-155_0_4_load_49 | 50 | 0.0046283 | 0.00116 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1631-155_0_4_load_50 | 51 | 0.0030324 | 0.00075998 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1631-155_0_4_load_52 | 53 | 0.0080774 | 0.0020244 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1631-155_0_4_load_56 | 54 | 0.0030702 | 0.00076946 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1631-155_0_4_load_59 | 55 | 0.0037199 | 0.00093229 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1631-155_0_4_load_58 | 56 | 0.0085408 | 0.0021405 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 16 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1631-155_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.025364 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1631-155_0_4_line_1 | NAYY 4x150 SE | 1 | 2 | 0.012352 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1631-155_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.026429 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1631-155_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.019863 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1631-155_0_4_line_4 | NAYY 4x150 SE | 4 | 5 | 0.0076194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1631-155_0_4_line_5 | NAYY 4x150 SE | 5 | 11 | 0.0024326 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1631-155_0_4_line_6 | NAYY 4x150 SE | 6 | 7 | 0.0239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1631-155_0_4_line_7 | NAYY 4x150 SE | 7 | 8 | 0.021153 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1631-155_0_4_line_8 | NAYY 4x150 SE | 8 | 9 | 0.017592 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1631-155_0_4_line_9 | NAYY 4x150 SE | 9 | 10 | 0.0099842 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1631-155_0_4_line_10 | NAYY 4x150 SE | 10 | 13 | 0.0085098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1631-155_0_4_line_11 | NAYY 4x150 SE | 11 | 12 | 0.011146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1631-155_0_4_line_12 | NAYY 4x150 SE | 12 | 18 | 0.00828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1631-155_0_4_line_13 | NAYY 4x150 SE | 12 | 16 | 0.015613 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1631-155_0_4_line_14 | NAYY 4x150 SE | 13 | 14 | 0.033307 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1631-155_0_4_line_15 | NAYY 4x150 SE | 14 | 15 | 0.02249 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1631-155_0_4_line_16 | NAYY 4x150 SE | 15 | 16 | 0.013433 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1631-155_0_4_line_17 | NAYY 4x150 SE | 16 | 17 | 0.003677 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
18 | LV_1631-155_0_4_line_18 | NAYY 4x150 SE | 17 | 21 | 0.018786 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1631-155_0_4_line_19 | NAYY 4x150 SE | 17 | 22 | 0.0042187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1631-155_0_4_line_20 | NAYY 4x150 SE | 18 | 23 | 0.004336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1631-155_0_4_line_21 | NAYY 4x150 SE | 19 | 20 | 0.0034064 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1631-155_0_4_line_22 | NAYY 4x150 SE | 20 | 41 | 0.0077717 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1631-155_0_4_line_23 | NAYY 4x150 SE | 21 | 28 | 0.011527 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1631-155_0_4_line_24 | NAYY 4x150 SE | 22 | 25 | 0.014572 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1631-155_0_4_line_25 | NAYY 4x150 SE | 23 | 24 | 0.032227 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1631-155_0_4_line_26 | NAYY 4x150 SE | 25 | 26 | 0.038103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1631-155_0_4_line_27 | NAYY 4x150 SE | 26 | 27 | 0.022073 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1631-155_0_4_line_28 | NAYY 4x150 SE | 27 | 29 | 0.0036949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1631-155_0_4_line_29 | NAYY 4x150 SE | 28 | 30 | 0.016659 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1631-155_0_4_line_30 | NAYY 4x150 SE | 28 | 31 | 0.0032102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1631-155_0_4_line_31 | NAYY 4x150 SE | 29 | 54 | 0.0092042 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1631-155_0_4_line_32 | NAYY 4x150 SE | 30 | 51 | 0.015772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1631-155_0_4_line_33 | NAYY 4x150 SE | 31 | 47 | 0.016968 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1631-155_0_4_line_34 | NAYY 4x150 SE | 32 | 33 | 0.010566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1631-155_0_4_line_35 | NAYY 4x150 SE | 32 | 34 | 0.0075091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1631-155_0_4_line_36 | NAYY 4x150 SE | 34 | 35 | 0.005024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1631-155_0_4_line_37 | NAYY 4x150 SE | 34 | 36 | 0.021357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1631-155_0_4_line_38 | NAYY 4x150 SE | 35 | 37 | 0.0079794 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1631-155_0_4_line_39 | NAYY 4x150 SE | 35 | 38 | 0.01266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1631-155_0_4_line_40 | NAYY 4x150 SE | 36 | 39 | 0.011431 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1631-155_0_4_line_41 | NAYY 4x150 SE | 37 | 40 | 0.025522 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1631-155_0_4_line_42 | NAYY 4x150 SE | 38 | 41 | 0.0034653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1631-155_0_4_line_43 | NAYY 4x150 SE | 39 | 42 | 0.0059251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1631-155_0_4_line_44 | NAYY 4x150 SE | 42 | 43 | 0.011535 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1631-155_0_4_line_45 | NAYY 4x150 SE | 43 | 44 | 0.010901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1631-155_0_4_line_46 | NAYY 4x150 SE | 43 | 45 | 0.009486 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1631-155_0_4_line_47 | NAYY 4x150 SE | 45 | 46 | 0.0028586 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1631-155_0_4_line_48 | NAYY 4x150 SE | 46 | 50 | 0.0139 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1631-155_0_4_line_49 | NAYY 4x150 SE | 47 | 48 | 0.017089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1631-155_0_4_line_50 | NAYY 4x150 SE | 48 | 49 | 0.012885 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1631-155_0_4_line_51 | NAYY 4x150 SE | 48 | 50 | 0.012366 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1631-155_0_4_line_52 | NAYY 4x150 SE | 49 | 52 | 0.013666 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1631-155_0_4_line_53 | NAYY 4x150 SE | 52 | 53 | 0.002527 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1631-155_0_4_line_54 | NAYY 4x150 SE | 54 | 55 | 0.0052015 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1631-155_0_4_line_55 | NAYY 4x150 SE | 55 | 56 | 0.0026053 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1631-155_0_4_trafo_16 | 0.25 MVA 20/0.4 kV | 57 | 16 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2725214.0805 | 1206890.1755 | 2725214.0805 | 1206890.1755 | 2725221.764 | 1206882.553 | 2725228.7862 | 1206877.4408 | 2725233.7796 | 1206874.3829
1 | 2725243.1978 | 1206866.4862 | 2725237.055 | 1206872.3771 | 2725233.7796 | 1206874.3829
2 | 2725233.7796 | 1206874.3829 | 2725244.7826 | 1206898.4121
3 | 2725256.9162 | 1206852.1449 | 2725252.6926 | 1206856.2039 | 2725245.9054 | 1206863.8896 | 2725243.1978 | 1206866.4862
4 | 2725256.9162 | 1206852.1449 | 2725258.3067 | 1206844.6535
5 | 2725258.7506 | 1206842.2617 | 2725258.3067 | 1206844.6535
6 | 2725299.1293 | 1206921.2837 | 2725302.8822 | 1206926.9557 | 2725307.5423 | 1206935.7936 | 2725310.5435 | 1206942.2364
7 | 2725299.1293 | 1206921.2837 | 2725292.1145 | 1206912.641 | 2725289.8251 | 1206907.5557 | 2725288.9914 | 1206903.4239 | 2725288.9476 | 1206903.1978
8 | 2725288.9476 | 1206903.1978 | 2725287.2415 | 1206894.3803 | 2725285.3088 | 1206885.9892
9 | 2725283.0677 | 1206876.2598 | 2725285.3088 | 1206885.9892
10 | 2725283.0677 | 1206876.2598 | 2725282.3824 | 1206873.2843 | 2725280.8291 | 1206868.0537
11 | 2725260.6103 | 1206831.2731 | 2725259.558 | 1206837.9117 | 2725258.7506 | 1206842.2617
12 | 2725260.6103 | 1206831.2731 | 2725252.3372 | 1206831.6106
13 | 2725260.6103 | 1206831.2731 | 2725261.6454 | 1206824.3673 | 2725262.1144 | 1206821.2303 | 2725262.92 | 1206815.832
14 | 2725272.0281 | 1206836.0163 | 2725274.9762 | 1206843.4283 | 2725278.4748 | 1206860.1256 | 2725280.8291 | 1206868.0537
15 | 2725272.0281 | 1206836.0163 | 2725276.2388 | 1206828.2209 | 2725276.3349 | 1206814.5903
16 | 2725262.92 | 1206815.832 | 2725276.3349 | 1206814.5903
17 | 2725262.92 | 1206815.832 | 2725263.468 | 1206812.1962
18 | 2725267.3003 | 1206793.807 | 2725263.468 | 1206812.1962
19 | 2725263.468 | 1206812.1962 | 2725260.7506 | 1206810.4601 | 2725260.1698 | 1206809.6534
20 | 2725252.3372 | 1206831.6106 | 2725248.0048 | 1206831.7874
21 | 2725302.9318 | 1206812.7944 | 2725299.5332 | 1206813.0239
22 | 2725302.9318 | 1206812.7944 | 2725310.6859 | 1206812.2708
23 | 2725267.3003 | 1206793.807 | 2725269.3414 | 1206782.4634
24 | 2725260.1698 | 1206809.6534 | 2725258.2227 | 1206806.9488 | 2725255.7188 | 1206802.2927 | 2725251.4906 | 1206798.1024
25 | 2725215.8046 | 1206833.101 | 2725248.0048 | 1206831.7874
26 | 2725217.9314 | 1206782.1318 | 2725222.4688 | 1206782.291 | 2725232.3991 | 1206785.4239 | 2725234.6207 | 1206786.4936 | 2725238.9282 | 1206790.398 | 2725247.0083 | 1206794.3261 | 2725249.1161 | 1206795.7492 | 2725251.4906 | 1206798.1024
27 | 2725196.079 | 1206779.4042 | 2725209.85 | 1206781.8482 | 2725217.9314 | 1206782.1318
28 | 2725192.4409 | 1206778.7586 | 2725196.079 | 1206779.4042
29 | 2725255.1497 | 1206774.326 | 2725260.5373 | 1206779.3207 | 2725269.3414 | 1206782.4634
30 | 2725269.3414 | 1206782.4634 | 2725270.0254 | 1206779.3269
31 | 2725192.4409 | 1206778.7586 | 2725187.9775 | 1206775.3957 | 2725184.3757 | 1206775.0775
32 | 2725255.1497 | 1206774.326 | 2725254.4363 | 1206758.5702
33 | 2725270.0254 | 1206779.3269 | 2725271.2943 | 1206773.5086 | 2725272.6575 | 1206769.0894 | 2725275.4604 | 1206763.3492
34 | 2725338.9954 | 1206808.1676 | 2725349.5581 | 1206807.8892
35 | 2725331.489 | 1206808.3653 | 2725338.9954 | 1206808.1676
36 | 2725331.489 | 1206808.3653 | 2725326.5882 | 1206809.53
37 | 2725331.489 | 1206808.3653 | 2725326.6746 | 1206803.2492 | 2725324.0623 | 1206797.957 | 2725320.5584 | 1206790.2902
38 | 2725326.5882 | 1206809.53 | 2725326.1492 | 1206817.4973
39 | 2725326.5882 | 1206809.53 | 2725314.1433 | 1206812.0374
40 | 2725320.5584 | 1206790.2902 | 2725318.2076 | 1206785.1465 | 2725316.4077 | 1206779.6582
41 | 2725336.7676 | 1206839.9795 | 2725325.8997 | 1206822.0251 | 2725326.1492 | 1206817.4973
42 | 2725314.1433 | 1206812.0374 | 2725310.6859 | 1206812.2708
43 | 2725316.4077 | 1206779.6582 | 2725314.5614 | 1206774.0281
44 | 2725312.8603 | 1206762.6615 | 2725312.8359 | 1206765.2741 | 2725314.5614 | 1206774.0281 | 2725314.5614 | 1206774.0281
45 | 2725312.8603 | 1206762.6615 | 2725319.3789 | 1206768.1359 | 2725321.6631 | 1206768.8342
46 | 2725312.8603 | 1206762.6615 | 2725312.9378 | 1206753.1781
47 | 2725312.9378 | 1206753.1781 | 2725310.1665 | 1206752.4771
48 | 2725310.1665 | 1206752.4771 | 2725303.494 | 1206750.7892 | 2725296.6638 | 1206749.1812
49 | 2725284.4591 | 1206749.0439 | 2725281.8507 | 1206751.5355 | 2725280.257 | 1206753.5258 | 2725275.4604 | 1206763.3492
50 | 2725284.4591 | 1206749.0439 | 2725278.3346 | 1206742.9107 | 2725274.6425 | 1206740.8731
51 | 2725284.4591 | 1206749.0439 | 2725288.6832 | 1206748.2208 | 2725294.1073 | 1206748.5794 | 2725296.6638 | 1206749.1812
52 | 2725261.2882 | 1206738.4829 | 2725264.8089 | 1206738.5569 | 2725273.7473 | 1206740.3792 | 2725274.6425 | 1206740.8731
53 | 2725261.2882 | 1206738.4829 | 2725259.0142 | 1206737.3677
54 | 2725179.1944 | 1206774.6196 | 2725184.3757 | 1206775.0775
55 | 2725176.5992 | 1206774.3903 | 2725179.1944 | 1206774.6196

## bus_geodata
| x | y | coords
0 | 2725214.0805 | 1206890.1755
1 | 2725233.7796 | 1206874.3829
2 | 2725243.1978 | 1206866.4862
3 | 2725244.7826 | 1206898.4121
4 | 2725256.9162 | 1206852.1449
5 | 2725258.3067 | 1206844.6535
6 | 2725310.5435 | 1206942.2364
7 | 2725299.1293 | 1206921.2837
8 | 2725288.9476 | 1206903.1978
9 | 2725285.3088 | 1206885.9892
10 | 2725283.0677 | 1206876.2598
11 | 2725258.7506 | 1206842.2617
12 | 2725260.6103 | 1206831.2731
13 | 2725280.8291 | 1206868.0537
14 | 2725272.0281 | 1206836.0163
15 | 2725276.3349 | 1206814.5903
16 | 2725262.92 | 1206815.832
17 | 2725263.468 | 1206812.1962
18 | 2725252.3372 | 1206831.6106
19 | 2725299.5332 | 1206813.0239
20 | 2725302.9318 | 1206812.7944
21 | 2725267.3003 | 1206793.807
22 | 2725260.1698 | 1206809.6534
23 | 2725248.0048 | 1206831.7874
24 | 2725215.8046 | 1206833.101
25 | 2725251.4906 | 1206798.1024
26 | 2725217.9314 | 1206782.1318
27 | 2725196.079 | 1206779.4042
28 | 2725269.3414 | 1206782.4634
29 | 2725192.4409 | 1206778.7586
30 | 2725255.1497 | 1206774.326
31 | 2725270.0254 | 1206779.3269
32 | 2725338.9954 | 1206808.1676
33 | 2725349.5581 | 1206807.8892
34 | 2725331.489 | 1206808.3653
35 | 2725326.5882 | 1206809.53
36 | 2725320.5584 | 1206790.2902
37 | 2725326.1492 | 1206817.4973
38 | 2725314.1433 | 1206812.0374
39 | 2725316.4077 | 1206779.6582
40 | 2725336.7676 | 1206839.9795
41 | 2725310.6859 | 1206812.2708
42 | 2725314.5614 | 1206774.0281
43 | 2725312.8603 | 1206762.6615
44 | 2725321.6631 | 1206768.8342
45 | 2725312.9378 | 1206753.1781
46 | 2725310.1665 | 1206752.4771
47 | 2725275.4604 | 1206763.3492
48 | 2725284.4591 | 1206749.0439
49 | 2725274.6425 | 1206740.8731
50 | 2725296.6638 | 1206749.1812
51 | 2725254.4363 | 1206758.5702
52 | 2725261.2882 | 1206738.4829
53 | 2725259.0142 | 1206737.3677
54 | 2725184.3757 | 1206775.0775
55 | 2725179.1944 | 1206774.6196
56 | 2725176.5992 | 1206774.3903
57 | 2725263.468 | 1206812.1962

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99669 | -0.023216 | 0.0058089 | 0.0014558
1 | 0.9969 | -0.021735 | 0.005357 | 0.0013426
2 | 0.99724 | -0.019348 | 0.0051581 | 0.0012927
3 | 0.99659 | -0.023882 | 0.0080848 | 0.0020263
4 | 0.99793 | -0.014484 | 0 | 0
5 | 0.9982 | -0.01262 | 0.0046218 | 0.0011583
6 | 0.99639 | -0.025328 | 0.0041221 | 0.0010331
7 | 0.99653 | -0.024338 | 0 | 0
8 | 0.99665 | -0.023461 | 0.0038095 | 0.00095475
9 | 0.99685 | -0.022058 | 0.0048474 | 0.0012149
10 | 0.99703 | -0.020777 | 0.0068571 | 0.0017186
11 | 0.9983 | -0.011912 | 0.0052719 | 0.0013213
12 | 0.99884 | -0.0080847 | 0 | 0
13 | 0.99727 | -0.019099 | 0.0060865 | 0.0015254
14 | 0.9985 | -0.010509 | 0 | 0
15 | 0.99933 | -0.0047197 | 0.0094441 | 0.0023669
16 | 1 | 0 | -0.20023 | -0.050105
17 | 0.99971 | -0.0020468 | 0 | 0
18 | 0.99864 | -0.0095353 | 0.0037948 | 0.00095108
19 | 0.98748 | -0.087875 | 0.0038044 | 0.00095348
20 | 0.9875 | -0.087742 | 0.0041697 | 0.001045
21 | 0.9976 | -0.016667 | 0.0021828 | 0.00054707
22 | 0.9995 | -0.0034688 | 0.0080068 | 0.0020067
23 | 0.99855 | -0.01013 | 0.0050557 | 0.0012671
24 | 0.99815 | -0.012924 | 0.0086555 | 0.0021693
25 | 0.99897 | -0.007218 | 0.0025479 | 0.00063856
26 | 0.9977 | -0.016066 | 0.004319 | 0.0010825
27 | 0.99711 | -0.020244 | 0.0035334 | 0.00088556
28 | 0.99635 | -0.025415 | 0 | 0
29 | 0.99703 | -0.020813 | 0 | 0
30 | 0.99628 | -0.025923 | 0 | 0
31 | 0.99602 | -0.027757 | 0.0060181 | 0.0015083
32 | 0.98789 | -0.084971 | 0.004136 | 0.0010366
33 | 0.98782 | -0.085459 | 0.0045133 | 0.0011311
34 | 0.98798 | -0.084307 | 0 | 0
35 | 0.98785 | -0.08524 | 0 | 0
36 | 0.98881 | -0.078458 | 0.0028151 | 0.00070554
37 | 0.98777 | -0.085797 | 0.0036991 | 0.00092708
38 | 0.98764 | -0.086706 | 0 | 0
39 | 0.9893 | -0.075004 | 0.0043463 | 0.0010893
40 | 0.98766 | -0.086614 | 0.0031268 | 0.00078364
41 | 0.98759 | -0.087108 | 0.0033479 | 0.00083905
42 | 0.98959 | -0.072952 | 0.00315 | 0.00078946
43 | 0.9902 | -0.06859 | 0 | 0
44 | 0.99013 | -0.069112 | 0.0047026 | 0.0011786
45 | 0.99078 | -0.064554 | 0 | 0
46 | 0.99095 | -0.063339 | 0.0057167 | 0.0014327
47 | 0.99439 | -0.039132 | 0.0030914 | 0.00077477
48 | 0.99283 | -0.05009 | 0 | 0
49 | 0.99262 | -0.05156 | 0.0031802 | 0.00079702
50 | 0.9919 | -0.056629 | 0.0046283 | 0.00116
51 | 0.99621 | -0.026404 | 0.0030324 | 0.00075998
52 | 0.99246 | -0.052678 | 0 | 0
53 | 0.99243 | -0.052885 | 0.0080774 | 0.0020244
54 | 0.99683 | -0.02223 | 0.0030702 | 0.00076946
55 | 0.99673 | -0.02287 | 0.0037199 | 0.00093229
56 | 0.9967 | -0.023094 | 0.0085408 | 0.0021405
57 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0058089 | -0.0014558 | 0.00581 | 0.001456 | 1.1904e-06 | 1.272e-07 | 0.0086724 | 0.0086723 | 0.0086724 | 0.99669 | -0.023216 | 0.9969 | -0.021735 | 3.212
1 | -0.019254 | -0.0048254 | 0.019261 | 0.0048277 | 6.3662e-06 | 2.2874e-06 | 0.02874 | 0.02874 | 0.02874 | 0.9969 | -0.021735 | 0.99724 | -0.019348 | 10.6444
2 | 0.0080873 | 0.0020268 | -0.0080848 | -0.0020263 | 2.4031e-06 | 5.7981e-07 | 0.012071 | 0.012072 | 0.012072 | 0.9969 | -0.021735 | 0.99659 | -0.023882 | 4.4709
3 | -0.024419 | -0.0061204 | 0.024435 | 0.0061265 | 1.6455e-05 | 6.0695e-06 | 0.036436 | 0.036436 | 0.036436 | 0.99724 | -0.019348 | 0.99793 | -0.014484 | 13.495
4 | -0.024435 | -0.0061265 | 0.024442 | 0.0061288 | 6.3121e-06 | 2.3281e-06 | 0.036436 | 0.036436 | 0.036436 | 0.99793 | -0.014484 | 0.9982 | -0.01262 | 13.4949
5 | -0.029063 | -0.0072871 | 0.029066 | 0.0072882 | 2.8494e-06 | 1.0641e-06 | 0.043326 | 0.043326 | 0.043326 | 0.9982 | -0.01262 | 0.9983 | -0.011912 | 16.0466
6 | -0.0041221 | -0.0010331 | 0.0041227 | 0.001033 | 5.6516e-07 | -9.3961e-08 | 0.006156 | 0.0061559 | 0.006156 | 0.99639 | -0.025328 | 0.99653 | -0.024338 | 2.28
7 | -0.0041227 | -0.001033 | 0.0041232 | 0.0010329 | 5.002e-07 | -8.3244e-08 | 0.0061559 | 0.0061558 | 0.0061559 | 0.99653 | -0.024338 | 0.99665 | -0.023461 | 2.28
8 | -0.0079327 | -0.0019877 | 0.0079342 | 0.001988 | 1.5397e-06 | 3.6291e-07 | 0.011843 | 0.011843 | 0.011843 | 0.99665 | -0.023461 | 0.99685 | -0.022058 | 4.3865
9 | -0.012782 | -0.0032029 | 0.012784 | 0.0032036 | 2.2678e-06 | 7.4206e-07 | 0.019079 | 0.019079 | 0.019079 | 0.99685 | -0.022058 | 0.99703 | -0.020777 | 7.0663
10 | -0.019641 | -0.0049222 | 0.019646 | 0.0049238 | 4.5627e-06 | 1.6439e-06 | 0.029313 | 0.029313 | 0.029313 | 0.99703 | -0.020777 | 0.99727 | -0.019099 | 10.8566
11 | -0.034338 | -0.0086095 | 0.034356 | 0.0086163 | 1.8221e-05 | 6.8621e-06 | 0.051184 | 0.051184 | 0.051184 | 0.9983 | -0.011912 | 0.99884 | -0.0080847 | 18.957
12 | 0.017514 | 0.0043899 | -0.017511 | -0.0043887 | 3.5173e-06 | 1.2445e-06 | 0.026092 | 0.026092 | 0.026092 | 0.99884 | -0.0080847 | 0.99864 | -0.0095353 | 9.6636
13 | -0.05187 | -0.013006 | 0.051929 | 0.013028 | 5.8177e-05 | 2.2171e-05 | 0.077275 | 0.077275 | 0.077275 | 0.99884 | -0.0080847 | 1 | 0 | 28.6205
14 | -0.025732 | -0.0064493 | 0.025763 | 0.0064606 | 3.0638e-05 | 1.1349e-05 | 0.038394 | 0.038394 | 0.038394 | 0.99727 | -0.019099 | 0.9985 | -0.010509 | 14.2202
15 | -0.025763 | -0.0064606 | 0.025783 | 0.0064683 | 2.0687e-05 | 7.6623e-06 | 0.038394 | 0.038394 | 0.038394 | 0.9985 | -0.010509 | 0.99933 | -0.0047197 | 14.2201
16 | -0.035227 | -0.0088352 | 0.03525 | 0.0088439 | 2.3065e-05 | 8.6951e-06 | 0.052457 | 0.052457 | 0.052457 | 0.99933 | -0.0047197 | 1 | 0 | 19.4284
17 | 0.11226 | 0.028233 | -0.11222 | -0.028221 | 3.2023e-05 | 1.222e-05 | 0.16707 | 0.16707 | 0.16707 | 1 | 0 | 0.99971 | -0.0020468 | 30.9394
18 | 0.07842 | 0.019741 | -0.07826 | -0.01968 | 0.0001598 | 6.1216e-05 | 0.11676 | 0.11676 | 0.11676 | 0.99971 | -0.0020468 | 0.9976 | -0.016667 | 43.2429
19 | 0.033803 | 0.0084793 | -0.033796 | -0.0084767 | 6.6649e-06 | 2.5081e-06 | 0.050317 | 0.050317 | 0.050317 | 0.99971 | -0.0020468 | 0.9995 | -0.0034688 | 18.6359
20 | 0.013716 | 0.0034376 | -0.013715 | -0.0034372 | 1.1301e-06 | 3.7793e-07 | 0.020437 | 0.020437 | 0.020437 | 0.99864 | -0.0095353 | 0.99855 | -0.01013 | 7.5693
21 | -0.0038044 | -0.00095347 | 0.0038045 | 0.00095346 | 6.9858e-08 | -1.671e-08 | 0.0057328 | 0.0057328 | 0.0057328 | 0.98748 | -0.087875 | 0.9875 | -0.087742 | 2.1233
22 | -0.0079742 | -0.0019985 | 0.0079749 | 0.0019986 | 7.0019e-07 | 1.6987e-07 | 0.012016 | 0.012016 | 0.012016 | 0.9875 | -0.087742 | 0.98759 | -0.087108 | 4.4503
23 | 0.076078 | 0.019133 | -0.075985 | -0.019098 | 9.266e-05 | 3.5488e-05 | 0.1135 | 0.1135 | 0.1135 | 0.9976 | -0.016667 | 0.99635 | -0.025415 | 42.037
24 | 0.02579 | 0.00647 | -0.025776 | -0.0064651 | 1.3406e-05 | 4.9652e-06 | 0.038397 | 0.038397 | 0.038397 | 0.9995 | -0.0034688 | 0.99897 | -0.007218 | 14.221
25 | 0.0086589 | 0.0021701 | -0.0086555 | -0.0021693 | 3.3482e-06 | 8.6635e-07 | 0.012903 | 0.012903 | 0.012903 | 0.99855 | -0.01013 | 0.99815 | -0.012924 | 4.779
26 | 0.023228 | 0.0058265 | -0.0232 | -0.0058161 | 2.8467e-05 | 1.0451e-05 | 0.034602 | 0.034602 | 0.034602 | 0.99897 | -0.007218 | 0.9977 | -0.016066 | 12.8155
27 | 0.018881 | 0.0047336 | -0.01887 | -0.0047297 | 1.0922e-05 | 3.9128e-06 | 0.02816 | 0.02816 | 0.02816 | 0.9977 | -0.016066 | 0.99711 | -0.020244 | 10.4297
28 | 0.015336 | 0.0038441 | -0.015335 | -0.0038437 | 1.2078e-06 | 4.1633e-07 | 0.022887 | 0.022887 | 0.022887 | 0.99711 | -0.020244 | 0.99703 | -0.020813 | 8.4767
29 | 0.0030328 | 0.00075972 | -0.0030326 | -0.00075985 | 2.1325e-07 | -1.3493e-07 | 0.0045292 | 0.0045293 | 0.0045293 | 0.99635 | -0.025415 | 0.99628 | -0.025923 | 1.6775
30 | 0.072952 | 0.018338 | -0.072928 | -0.018329 | 2.3787e-05 | 9.1069e-06 | 0.10897 | 0.10897 | 0.10897 | 0.99635 | -0.025415 | 0.99602 | -0.027757 | 40.3595
31 | 0.015335 | 0.0038437 | -0.015332 | -0.0038427 | 3.0086e-06 | 1.0371e-06 | 0.022887 | 0.022887 | 0.022887 | 0.99703 | -0.020813 | 0.99683 | -0.02223 | 8.4768
32 | 0.0030326 | 0.00075985 | -0.0030324 | -0.00075998 | 2.019e-07 | -1.2771e-07 | 0.0045293 | 0.0045294 | 0.0045294 | 0.99628 | -0.025923 | 0.99621 | -0.026404 | 1.6775
33 | 0.06691 | 0.01682 | -0.066804 | -0.01678 | 0.00010584 | 4.0486e-05 | 0.09998 | 0.09998 | 0.09998 | 0.99602 | -0.027757 | 0.99439 | -0.039132 | 37.0296
34 | 0.0045136 | 0.0011311 | -0.0045132 | -0.0011311 | 3.0475e-07 | -1.8064e-08 | 0.0067985 | 0.0067986 | 0.0067986 | 0.98789 | -0.084971 | 0.98782 | -0.085459 | 2.518
35 | -0.0086495 | -0.0021677 | 0.0086503 | 0.0021679 | 7.9533e-07 | 2.0975e-07 | 0.013028 | 0.013028 | 0.013028 | 0.98789 | -0.084971 | 0.98798 | -0.084307 | 4.8253
36 | 0.018155 | 0.0045501 | -0.018152 | -0.0045492 | 2.3439e-06 | 8.3716e-07 | 0.027343 | 0.027343 | 0.027343 | 0.98798 | -0.084307 | 0.98785 | -0.08524 | 10.1271
37 | -0.026805 | -0.0067179 | 0.026827 | 0.006726 | 2.172e-05 | 8.0802e-06 | 0.040372 | 0.040371 | 0.040372 | 0.98798 | -0.084307 | 0.98881 | -0.078458 | 14.9524
38 | 0.0068267 | 0.0017106 | -0.0068262 | -0.0017105 | 5.2651e-07 | 1.0036e-07 | 0.010283 | 0.010283 | 0.010283 | 0.98785 | -0.08524 | 0.98777 | -0.085797 | 3.8086
39 | 0.011326 | 0.0028386 | -0.011323 | -0.0028379 | 2.2992e-06 | 7.2227e-07 | 0.01706 | 0.01706 | 0.01706 | 0.98785 | -0.08524 | 0.98764 | -0.086706 | 6.3186
40 | -0.029642 | -0.0074316 | 0.029656 | 0.0074369 | 1.4194e-05 | 5.3125e-06 | 0.044608 | 0.044608 | 0.044608 | 0.98881 | -0.078458 | 0.9893 | -0.075004 | 16.5214
41 | 0.0031271 | 0.00078345 | -0.0031268 | -0.00078364 | 3.5341e-07 | -1.9073e-07 | 0.0047107 | 0.0047108 | 0.0047108 | 0.98777 | -0.085797 | 0.98766 | -0.086614 | 1.7448
42 | 0.011323 | 0.0028379 | -0.011323 | -0.0028377 | 6.2934e-07 | 1.9771e-07 | 0.01706 | 0.01706 | 0.01706 | 0.98764 | -0.086706 | 0.98759 | -0.087108 | 6.3186
43 | -0.034002 | -0.0085262 | 0.034012 | 0.0085298 | 9.6713e-06 | 3.6436e-06 | 0.051145 | 0.051145 | 0.051145 | 0.9893 | -0.075004 | 0.98959 | -0.072952 | 18.9426
44 | -0.037162 | -0.0093193 | 0.037185 | 0.0093278 | 2.2477e-05 | 8.4969e-06 | 0.055882 | 0.055882 | 0.055882 | 0.98959 | -0.072952 | 0.9902 | -0.06859 | 20.6969
45 | 0.0047029 | 0.0011786 | -0.0047026 | -0.0011786 | 3.3974e-07 | -9.5444e-09 | 0.0070672 | 0.0070673 | 0.0070673 | 0.9902 | -0.06859 | 0.99013 | -0.069112 | 2.6175
46 | -0.041887 | -0.010506 | 0.041911 | 0.010515 | 2.3455e-05 | 8.8992e-06 | 0.062949 | 0.062949 | 0.062949 | 0.9902 | -0.06859 | 0.99078 | -0.064554 | 23.3144
47 | -0.041911 | -0.010515 | 0.041918 | 0.010518 | 7.0682e-06 | 2.6817e-06 | 0.062949 | 0.062949 | 0.062949 | 0.99078 | -0.064554 | 0.99095 | -0.063339 | 23.3143
48 | -0.047635 | -0.011951 | 0.047679 | 0.011968 | 4.4381e-05 | 1.689e-05 | 0.071533 | 0.071533 | 0.071533 | 0.99095 | -0.063339 | 0.9919 | -0.056629 | 26.4937
49 | 0.063713 | 0.016005 | -0.063616 | -0.015968 | 9.6956e-05 | 3.7069e-05 | 0.095354 | 0.095354 | 0.095354 | 0.99439 | -0.039132 | 0.99283 | -0.05009 | 35.3163
50 | 0.011261 | 0.0028225 | -0.011259 | -0.0028218 | 2.2903e-06 | 7.1432e-07 | 0.016878 | 0.016878 | 0.016878 | 0.99283 | -0.05009 | 0.99262 | -0.05156 | 6.2512
51 | 0.052355 | 0.013146 | -0.052307 | -0.013127 | 4.7521e-05 | 1.8118e-05 | 0.078476 | 0.078476 | 0.078476 | 0.99283 | -0.05009 | 0.9919 | -0.056629 | 29.0652
52 | 0.0080789 | 0.0020247 | -0.0080776 | -0.0020244 | 1.2508e-06 | 3.0444e-07 | 0.012111 | 0.012111 | 0.012111 | 0.99262 | -0.05156 | 0.99246 | -0.052678 | 4.4855
53 | 0.0080776 | 0.0020244 | -0.0080774 | -0.0020244 | 2.3128e-07 | 5.6301e-08 | 0.012111 | 0.012111 | 0.012111 | 0.99246 | -0.052678 | 0.99243 | -0.052885 | 4.4855
54 | 0.012262 | 0.0030732 | -0.012261 | -0.0030729 | 1.0875e-06 | 3.5046e-07 | 0.018304 | 0.018304 | 0.018304 | 0.99683 | -0.02223 | 0.99673 | -0.02287 | 6.7793
55 | 0.008541 | 0.0021406 | -0.0085408 | -0.0021405 | 2.6431e-07 | 6.7704e-08 | 0.012751 | 0.012751 | 0.012751 | 0.99673 | -0.02287 | 0.9967 | -0.023094 | 4.7225

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.20023 | 0.050105

## res_load
| p_mw | q_mvar
0 | 0.0058089 | 0.0014558
1 | 0.005357 | 0.0013426
2 | 0.0051581 | 0.0012927
3 | 0.0080848 | 0.0020263
4 | 0.0046218 | 0.0011583
5 | 0.0041221 | 0.0010331
6 | 0.0038095 | 0.00095475
7 | 0.0048474 | 0.0012149
8 | 0.0068571 | 0.0017186
9 | 0.0052719 | 0.0013213
10 | 0.0060865 | 0.0015254
11 | 0.0094441 | 0.0023669
12 | 0.0037948 | 0.00095108
13 | 0.0038044 | 0.00095348
14 | 0.0041697 | 0.001045
15 | 0.0021828 | 0.00054707
16 | 0.0080068 | 0.0020067
17 | 0.0050557 | 0.0012671
18 | 0.0086555 | 0.0021693
19 | 0.0025479 | 0.00063856
20 | 0.004319 | 0.0010825
21 | 0.0035334 | 0.00088556
22 | 0.0060181 | 0.0015083
23 | 0.004136 | 0.0010366
24 | 0.0045133 | 0.0011311
25 | 0.0028151 | 0.00070554
26 | 0.0036991 | 0.00092708
27 | 0.0043463 | 0.0010893
28 | 0.0031268 | 0.00078364
29 | 0.0033479 | 0.00083905
30 | 0.00315 | 0.00078946
31 | 0.0047026 | 0.0011786
32 | 0.0057167 | 0.0014327
33 | 0.0030914 | 0.00077477
34 | 0.0031802 | 0.00079702
35 | 0.0046283 | 0.00116
36 | 0.0030324 | 0.00075998
37 | 0.0080774 | 0.0020244
38 | 0.0030702 | 0.00076946
39 | 0.0037199 | 0.00093229
40 | 0.0085408 | 0.0021405

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1