## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1631-156_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1631-156_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1631-156_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1631-156_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1631-156_0_3_node_11 | 0.4 | n |  | TRUE
5 | bus_LV_1631-156_0_3_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_1631-156_0_3_node_10 | 0.4 | n |  | TRUE
7 | bus_LV_1631-156_0_3_node_14 | 0.4 | n |  | TRUE
8 | bus_LV_1631-156_0_3_node_12 | 0.4 | n |  | TRUE
9 | bus_LV_1631-156_0_3_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_1631-156_0_3_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_1631-156_0_3_node_37 | 0.4 | n |  | TRUE
12 | bus_LV_1631-156_0_3_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1631-156_0_3_node_36 | 0.4 | n |  | TRUE
14 | bus_LV_1631-156_0_3_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_1631-156_0_3_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_1631-156_0_3_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_1631-156_0_3_node_16 | 0.4 | n |  | TRUE
18 | bus_LV_1631-156_0_3_node_44 | 0.4 | n |  | TRUE
19 | bus_LV_1631-156_0_3_node_45 | 0.4 | n |  | TRUE
20 | bus_LV_1631-156_0_3_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_1631-156_0_3_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_1631-156_0_3_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_1631-156_0_3_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_1631-156_0_3_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_1631-156_0_3_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_1631-156_0_3_node_43 | 0.4 | n |  | TRUE
27 | bus_LV_1631-156_0_3_node_42 | 0.4 | n |  | TRUE
28 | bus_LV_1631-156_0_3_node_24 | 0.4 | n |  | TRUE
29 | bus_LV_1631-156_0_3_node_25 | 0.4 | n |  | TRUE
30 | bus_LV_1631-156_0_3_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_1631-156_0_3_node_27 | 0.4 | n |  | TRUE
32 | bus_LV_1631-156_0_3_node_28 | 0.4 | n |  | TRUE
33 | bus_LV_1631-156_0_3_node_29 | 0.4 | n |  | TRUE
34 | bus_LV_1631-156_0_3_node_32 | 0.4 | n |  | TRUE
35 | bus_LV_1631-156_0_3_node_30 | 0.4 | n |  | TRUE
36 | bus_LV_1631-156_0_3_node_31 | 0.4 | n |  | TRUE
37 | bus_LV_1631-156_0_3_node_33 | 0.4 | n |  | TRUE
38 | bus_LV_1631-156_0_3_node_34 | 0.4 | n |  | TRUE
39 | bus_LV_1631-156_0_3_node_35 | 0.4 | n |  | TRUE
40 | bus_LV_1631-156_0_3_node_38 | 0.4 | n |  | TRUE
41 | bus_LV_1631-156_0_3_node_39 | 0.4 | n |  | TRUE
42 | bus_LV_1631-156_0_3_node_40 | 0.4 | n |  | TRUE
43 | bus_LV_1631-156_0_3_node_41 | 0.4 | n |  | TRUE
44 | bus_MV_145_1_node_57 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1631-156_0_3_load_0 | 0 | 0.0023898 | 0.00059894 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1631-156_0_3_load_4 | 5 | 0.0015549 | 0.00038968 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1631-156_0_3_load_10 | 6 | 0.0028329 | 0.00071 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1631-156_0_3_load_14 | 7 | 0.0029773 | 0.00074618 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1631-156_0_3_load_5 | 9 | 0.0024293 | 0.00060884 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1631-156_0_3_load_37 | 11 | 0.0020792 | 0.00052109 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1631-156_0_3_load_8 | 12 | 0.0026782 | 0.00067121 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1631-156_0_3_load_36 | 13 | 0.0021539 | 0.00053981 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1631-156_0_3_load_7 | 14 | 0.0017189 | 0.00043079 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1631-156_0_3_load_13 | 15 | 0.002862 | 0.00071728 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1631-156_0_3_load_15 | 16 | 0.0026612 | 0.00066695 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1631-156_0_3_load_16 | 17 | 0.0030264 | 0.0007585 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1631-156_0_3_load_17 | 20 | 0.0024496 | 0.00061392 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1631-156_0_3_load_20 | 23 | 0.0029724 | 0.00074495 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1631-156_0_3_load_21 | 24 | 0.0031898 | 0.00079943 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1631-156_0_3_load_22 | 25 | 0.011348 | 0.0028442 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1631-156_0_3_load_43 | 26 | 0.0024367 | 0.0006107 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1631-156_0_3_load_42 | 27 | 0.0029104 | 0.00072942 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1631-156_0_3_load_24 | 28 | 0.0051697 | 0.0012957 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1631-156_0_3_load_25 | 29 | 0.0027537 | 0.00069013 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1631-156_0_3_load_26 | 30 | 0.0026544 | 0.00066526 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1631-156_0_3_load_27 | 31 | 0.0029999 | 0.00075186 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1631-156_0_3_load_28 | 32 | 0.0037411 | 0.00093761 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1631-156_0_3_load_29 | 33 | 0.002924 | 0.00073282 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1631-156_0_3_load_32 | 34 | 0.0024407 | 0.00061169 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1631-156_0_3_load_30 | 35 | 0.0039101 | 0.00097997 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1631-156_0_3_load_31 | 36 | 0.0021036 | 0.00052721 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1631-156_0_3_load_33 | 37 | 0.0040071 | 0.0010043 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1631-156_0_3_load_34 | 38 | 0.002958 | 0.00074135 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1631-156_0_3_load_35 | 39 | 0.0020713 | 0.00051913 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1631-156_0_3_load_38 | 40 | 0.0025957 | 0.00065054 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1631-156_0_3_load_39 | 41 | 0.0021434 | 0.00053719 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1631-156_0_3_load_40 | 42 | 0.0020674 | 0.00051815 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1631-156_0_3_load_41 | 43 | 0.00259 | 0.00064911 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 36 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1631-156_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.13316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1631-156_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.062504 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
2 | LV_1631-156_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.048676 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
3 | LV_1631-156_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.061431 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
4 | LV_1631-156_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.022623 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
5 | LV_1631-156_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.050262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
6 | LV_1631-156_0_3_line_6 | NAYY 4x150 SE | 5 | 9 | 0.13956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
7 | LV_1631-156_0_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.020072 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_1631-156_0_3_line_8 | NAYY 4x150 SE | 7 | 8 | 0.020773 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1631-156_0_3_line_9 | NAYY 4x150 SE | 8 | 15 | 0.082777 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
10 | LV_1631-156_0_3_line_10 | NAYY 4x150 SE | 9 | 10 | 0.0055283 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
11 | LV_1631-156_0_3_line_11 | NAYY 4x150 SE | 10 | 11 | 0.014827 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
12 | LV_1631-156_0_3_line_12 | NAYY 4x150 SE | 10 | 12 | 0.020206 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1631-156_0_3_line_13 | NAYY 4x150 SE | 11 | 13 | 0.0059189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
14 | LV_1631-156_0_3_line_14 | NAYY 4x150 SE | 12 | 14 | 0.036457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1631-156_0_3_line_15 | NAYY 4x150 SE | 13 | 39 | 0.011509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
16 | LV_1631-156_0_3_line_16 | NAYY 4x150 SE | 15 | 16 | 0.10934 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
17 | LV_1631-156_0_3_line_17 | NAYY 4x150 SE | 16 | 17 | 0.0039944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
18 | LV_1631-156_0_3_line_18 | NAYY 4x150 SE | 17 | 18 | 0.030806 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
19 | LV_1631-156_0_3_line_19 | NAYY 4x150 SE | 18 | 19 | 0.060108 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
20 | LV_1631-156_0_3_line_20 | NAYY 4x150 SE | 19 | 24 | 0.017353 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1631-156_0_3_line_21 | NAYY 4x150 SE | 20 | 21 | 0.043271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1631-156_0_3_line_22 | NAYY 4x150 SE | 20 | 22 | 0.02998 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1631-156_0_3_line_23 | NAYY 4x150 SE | 21 | 23 | 0.011682 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1631-156_0_3_line_24 | NAYY 4x150 SE | 21 | 24 | 0.037107 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1631-156_0_3_line_25 | NAYY 4x150 SE | 22 | 25 | 0.01981 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1631-156_0_3_line_26 | NAYY 4x150 SE | 23 | 26 | 0.00012026 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1631-156_0_3_line_27 | NAYY 4x150 SE | 26 | 27 | 0.0089029 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1631-156_0_3_line_28 | NAYY 4x150 SE | 27 | 43 | 0.0062868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1631-156_0_3_line_29 | NAYY 4x150 SE | 28 | 29 | 0.0010174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1631-156_0_3_line_30 | NAYY 4x150 SE | 28 | 30 | 0.0036224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1631-156_0_3_line_31 | NAYY 4x150 SE | 29 | 31 | 0.009931 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1631-156_0_3_line_32 | NAYY 4x150 SE | 30 | 32 | 0.017322 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1631-156_0_3_line_33 | NAYY 4x150 SE | 31 | 33 | 0.0066767 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1631-156_0_3_line_34 | NAYY 4x150 SE | 33 | 34 | 0.000277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1631-156_0_3_line_35 | NAYY 4x150 SE | 34 | 35 | 0.0019914 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1631-156_0_3_line_36 | NAYY 4x150 SE | 35 | 36 | 0.010001 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1631-156_0_3_line_37 | NAYY 4x150 SE | 36 | 37 | 0.0044832 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
38 | LV_1631-156_0_3_line_38 | NAYY 4x150 SE | 37 | 38 | 0.00092758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
39 | LV_1631-156_0_3_line_39 | NAYY 4x150 SE | 38 | 39 | 0.00044673 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
40 | LV_1631-156_0_3_line_40 | NAYY 4x150 SE | 40 | 41 | 0.010671 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1631-156_0_3_line_41 | NAYY 4x150 SE | 40 | 42 | 0.007582 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1631-156_0_3_line_42 | NAYY 4x150 SE | 42 | 43 | 0.011334 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1631-156_0_3_trafo_31 | 0.25 MVA 20/0.4 kV | 44 | 36 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24
0 | 2732967.7551 | 1198019.7539 | 2732962.3301 | 1198026.2717 | 2732957.9979 | 1198030.5898 | 2732954.7122 | 1198035.1314 | 2732952.628 | 1198040.8006 | 2732949.6344 | 1198055.8346 | 2732947.8952 | 1198064.1468 | 2732946.0328 | 1198068.064 | 2732939.3571 | 1198077.7231 | 2732935.3999 | 1198082.9948 | 2732929.8544 | 1198088.4313 | 2732926.3048 | 1198092.8447 | 2732920.975 | 1198097.83 | 2732912.8908 | 1198104.3665 | 2732906.0145 | 1198109.0062 | 2732895.0045 | 1198118.6356 | 2732891.0541 | 1198120.1823 | 2732888.9188 | 1198120.2255
1 | 2732967.7551 | 1198019.7539 | 2732979.8917 | 1198016.6881 | 2732990.5861 | 1198014.7467 | 2733002.5648 | 1198014.324 | 2733009.4144 | 1198013.2866 | 2733014.7557 | 1198011.215 | 2733023.3039 | 1198006.0901 | 2733027.2453 | 1198003.5869
2 | 2732967.7551 | 1198019.7539 | 2732958.8831 | 1198023.3372 | 2732951.4887 | 1198027.2869 | 2732942.7149 | 1198033.6523 | 2732934.1162 | 1198041.3894 | 2732930.1619 | 1198043.7922 | 2732926.3752 | 1198043.7969
3 | 2733082.3966 | 1197977.0047 | 2733065.128 | 1197982.6581 | 2733055.5933 | 1197986.5711 | 2733047.5515 | 1197990.8511 | 2733035.8556 | 1197997.7295 | 2733027.2453 | 1198003.5869
4 | 2732926.3752 | 1198043.7969 | 2732922.0784 | 1198042.0779 | 2732920.6997 | 1198039.3228 | 2732920.7001 | 1198035.1974 | 2732923.4546 | 1198031.5892 | 2732928.413 | 1198027.785
5 | 2733082.3966 | 1197977.0047 | 2733093.3902 | 1197958.902 | 2733092.8024 | 1197954.163 | 2733086.6006 | 1197942.1934 | 2733087.3505 | 1197941.0203 | 2733092.4523 | 1197942.1792 | 2733093.8888 | 1197938.2303
6 | 2732928.413 | 1198027.785 | 2732930.8492 | 1198025.9158 | 2732937.0441 | 1198019.0371 | 2732941.86 | 1198012.4947 | 2732954.0644 | 1197985.1559 | 2732965.2444 | 1197957.2939 | 2732973.6699 | 1197930.9831 | 2732977.9682 | 1197920.6595 | 2732982.9596 | 1197912.0638 | 2732984.5065 | 1197908.2842 | 2732985.0251 | 1197905.1822 | 2732984.3321 | 1197902.0866
7 | 2733097.6047 | 1197922.2561 | 2733100.9924 | 1197929.5595 | 2733100.7672 | 1197932.1454 | 2733099.6665 | 1197934.3559 | 2733093.8888 | 1197938.2303
8 | 2733097.6047 | 1197922.2561 | 2733093.5258 | 1197922.7213 | 2733086.2767 | 1197924.2389 | 2733079.4032 | 1197930.4462
9 | 2733097.6047 | 1197922.2561 | 2733090.9636 | 1197918.3719 | 2733090.2962 | 1197916.867 | 2733091.1544 | 1197915.9632 | 2733098.0066 | 1197915.1596 | 2733101.7553 | 1197911.0509 | 2733101.7644 | 1197907.9042 | 2733104.1655 | 1197906.1452 | 2733106.4452 | 1197901.9705 | 2733108.8775 | 1197899.8341 | 2733119.4791 | 1197899.6811 | 2733122.0588 | 1197898.7934 | 2733121.1113 | 1197895.1584 | 2733118.627 | 1197892.4454 | 2733116.1179 | 1197890.8438 | 2733113.0136 | 1197890.3076 | 2733110.9658 | 1197887.4932 | 2733111.0762 | 1197881.8579 | 2733108.7981 | 1197873.99 | 2733108.8143 | 1197872.5781
10 | 2732980.1612 | 1197898.8135 | 2732982.961 | 1197900.0212 | 2732984.3321 | 1197902.0866
11 | 2732980.1612 | 1197898.8135 | 2732982.1927 | 1197894.1439 | 2732987.2247 | 1197889.5412 | 2732989.7316 | 1197888.053
12 | 2732980.1612 | 1197898.8135 | 2732977.0642 | 1197898.9781 | 2732969.4939 | 1197904.6586 | 2732964.6284 | 1197910.5487
13 | 2732989.7316 | 1197888.053 | 2732990.7996 | 1197887.419 | 2732994.9855 | 1197885.3328
14 | 2732938.9589 | 1197936.2596 | 2732940.846 | 1197935.1453 | 2732947.6591 | 1197929.2477 | 2732962.9637 | 1197912.564 | 2732964.6284 | 1197910.5487
15 | 2733005.2863 | 1197880.1987 | 2732994.9855 | 1197885.3328
16 | 2733079.4179 | 1197801.1793 | 2733079.4179 | 1197801.1793 | 2733081.3451 | 1197804.2801 | 2733091.4851 | 1197814.5916 | 2733093.266 | 1197819.4684 | 2733099.0637 | 1197825.302 | 2733099.1219 | 1197829.5288 | 2733099.7833 | 1197831.9899 | 2733101.0028 | 1197834.3634 | 2733102.4368 | 1197836.686 | 2733108.4288 | 1197838.2428 | 2733109.4281 | 1197844.0029 | 2733117.0491 | 1197845.9741 | 2733120.2628 | 1197848.4364 | 2733121.7355 | 1197851.0713 | 2733121.6913 | 1197855.4515 | 2733116.7771 | 1197858.5222 | 2733114.7551 | 1197861.0458 | 2733112.7086 | 1197862.279 | 2733116.1524 | 1197865.3581 | 2733118.0602 | 1197869.3259 | 2733118.2424 | 1197872.4324 | 2733115.9066 | 1197872.9697 | 2733110.0333 | 1197870.8706 | 2733108.8143 | 1197872.5781
17 | 2733078.9266 | 1197797.2152 | 2733079.4179 | 1197801.1793
18 | 2733085.9351 | 1197772.3241 | 2733089.5444 | 1197776.1852 | 2733083.4866 | 1197783.3893 | 2733078.8246 | 1197787.1107 | 2733078.4685 | 1197793.5189 | 2733078.9266 | 1197797.2152
19 | 2733085.9351 | 1197772.3241 | 2733081.9602 | 1197774.2705 | 2733077.9122 | 1197774.7141 | 2733074.1547 | 1197773.7408 | 2733069.5818 | 1197770.3808 | 2733053.3076 | 1197755.6516 | 2733050.6961 | 1197753.5141 | 2733047.651 | 1197752.3677 | 2733044.1305 | 1197751.0216 | 2733041.3027 | 1197750.7251 | 2733034.6992 | 1197753.0133
20 | 2733034.6992 | 1197753.0133 | 2733031.6509 | 1197754.0685 | 2733018.6349 | 1197759.5616
21 | 2732984.4482 | 1197773.9895 | 2732979.5645 | 1197772.2684 | 2732975.4271 | 1197772.2764 | 2732970.4807 | 1197774.0567 | 2732949.09 | 1197784.8338 | 2732944.6175 | 1197786.4228
22 | 2732916.0598 | 1197795.152 | 2732922.1105 | 1197794.4192 | 2732944.6175 | 1197786.4228
23 | 2732984.4482 | 1197773.9895 | 2732984.2417 | 1197778.1326 | 2732983.6044 | 1197781.4321 | 2732981.9271 | 1197785.2533
24 | 2732984.4482 | 1197773.9895 | 2733018.6349 | 1197759.5616
25 | 2732916.0598 | 1197795.152 | 2732917.5633 | 1197814.9007
26 | 2732981.8788 | 1197785.3634 | 2732981.9271 | 1197785.2533
27 | 2732976.2785 | 1197792.2843 | 2732981.8788 | 1197785.3634 | 2732981.8788 | 1197785.3634
28 | 2732972.3238 | 1197797.1714 | 2732976.2785 | 1197792.2843
29 | 2733036.2463 | 1197864.4563 | 2733037.1462 | 1197863.9814
30 | 2733040.3497 | 1197862.2907 | 2733037.1462 | 1197863.9814
31 | 2733036.2463 | 1197864.4563 | 2733027.4634 | 1197869.0916
32 | 2733056.777 | 1197856.7965 | 2733040.3497 | 1197862.2907
33 | 2733021.5098 | 1197872.1127 | 2733025.6319 | 1197870.0582 | 2733027.4634 | 1197869.0916
34 | 2733021.5098 | 1197872.1127 | 2733021.2619 | 1197872.2363
35 | 2733019.4796 | 1197873.1246 | 2733021.2619 | 1197872.2363
36 | 2733019.4796 | 1197873.1246 | 2733010.5288 | 1197877.5858
37 | 2733010.5288 | 1197877.5858 | 2733006.5163 | 1197879.5856
38 | 2733006.5163 | 1197879.5856 | 2733005.6861 | 1197879.9994
39 | 2733005.6861 | 1197879.9994 | 2733005.2863 | 1197880.1987
40 | 2732960.4247 | 1197811.8764 | 2732953.7123 | 1197820.1715
41 | 2732960.4247 | 1197811.8764 | 2732965.1941 | 1197805.9824
42 | 2732972.3238 | 1197797.1714 | 2732965.1941 | 1197805.9824

## bus_geodata
| x | y | coords
0 | 2732888.9188 | 1198120.2255
1 | 2732967.7551 | 1198019.7539
2 | 2733027.2453 | 1198003.5869
3 | 2732926.3752 | 1198043.7969
4 | 2733082.3966 | 1197977.0047
5 | 2732928.413 | 1198027.785
6 | 2733093.8888 | 1197938.2303
7 | 2733079.4032 | 1197930.4462
8 | 2733097.6047 | 1197922.2561
9 | 2732984.3321 | 1197902.0866
10 | 2732980.1612 | 1197898.8135
11 | 2732989.7316 | 1197888.053
12 | 2732964.6284 | 1197910.5487
13 | 2732994.9855 | 1197885.3327
14 | 2732938.9589 | 1197936.2596
15 | 2733108.8143 | 1197872.5781
16 | 2733079.4179 | 1197801.1793
17 | 2733078.9266 | 1197797.2152
18 | 2733085.9351 | 1197772.3241
19 | 2733034.6992 | 1197753.0133
20 | 2732944.6175 | 1197786.4228
21 | 2732984.4482 | 1197773.9895
22 | 2732916.0598 | 1197795.152
23 | 2732981.9271 | 1197785.2533
24 | 2733018.6349 | 1197759.5616
25 | 2732917.5633 | 1197814.9007
26 | 2732981.8788 | 1197785.3634
27 | 2732976.2785 | 1197792.2843
28 | 2733037.1462 | 1197863.9814
29 | 2733036.2463 | 1197864.4563
30 | 2733040.3497 | 1197862.2907
31 | 2733027.4634 | 1197869.0916
32 | 2733056.777 | 1197856.7964
33 | 2733021.5098 | 1197872.1127
34 | 2733021.2619 | 1197872.2363
35 | 2733019.4796 | 1197873.1246
36 | 2733010.5288 | 1197877.5858
37 | 2733006.5163 | 1197879.5856
38 | 2733005.6861 | 1197879.9994
39 | 2733005.2863 | 1197880.1987
40 | 2732960.4247 | 1197811.8764
41 | 2732953.7123 | 1197820.1715
42 | 2732965.1941 | 1197805.9824
43 | 2732972.3238 | 1197797.1714
44 | 2732980.1612 | 1197898.8135

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98947 | -0.072934 | 0.0023898 | 0.00059894
1 | 0.98993 | -0.069683 | 0 | 0
2 | 0.98769 | -0.085368 | 0 | 0
3 | 0.99176 | -0.056921 | 0 | 0
4 | 0.98548 | -0.10085 | 0 | 0
5 | 0.99261 | -0.051005 | 0.0015549 | 0.00038968
6 | 0.98368 | -0.11357 | 0.0028329 | 0.00071
7 | 0.98291 | -0.119 | 0.0029773 | 0.00074618
8 | 0.983 | -0.11836 | 0 | 0
9 | 0.99802 | -0.013633 | 0.0024293 | 0.00060884
10 | 0.99824 | -0.012093 | 0 | 0
11 | 0.99889 | -0.0076402 | 0.0020792 | 0.00052109
12 | 0.99812 | -0.012984 | 0.0026782 | 0.00067121
13 | 0.99916 | -0.0058027 | 0.0021539 | 0.00053981
14 | 0.99803 | -0.013612 | 0.0017189 | 0.00043079
15 | 0.98037 | -0.13693 | 0.002862 | 0.00071728
16 | 0.97713 | -0.15996 | 0.0026612 | 0.00066695
17 | 0.97702 | -0.16075 | 0.0030264 | 0.0007585
18 | 0.97624 | -0.16635 | 0 | 0
19 | 0.97471 | -0.1773 | 0 | 0
20 | 0.97123 | -0.20228 | 0.0024496 | 0.00061392
21 | 0.97211 | -0.19597 | 0 | 0
22 | 0.97073 | -0.20588 | 0 | 0
23 | 0.97181 | -0.19815 | 0.0029724 | 0.00074495
24 | 0.97383 | -0.18363 | 0.0031898 | 0.00079943
25 | 0.9704 | -0.20827 | 0.011348 | 0.0028442
26 | 0.9718 | -0.19817 | 0.0024367 | 0.0006107
27 | 0.97164 | -0.19933 | 0.0029104 | 0.00072942
28 | 0.99916 | -0.0058578 | 0.0051697 | 0.0012957
29 | 0.99918 | -0.0057402 | 0.0027537 | 0.00069013
30 | 0.99913 | -0.0060895 | 0.0026544 | 0.00066526
31 | 0.99938 | -0.0043187 | 0.0029999 | 0.00075186
32 | 0.99904 | -0.0067376 | 0.0037411 | 0.00093761
33 | 0.99955 | -0.0031631 | 0.002924 | 0.00073282
34 | 0.99956 | -0.0031071 | 0.0024407 | 0.00061169
35 | 0.99962 | -0.0026558 | 0.0039101 | 0.00097997
36 | 1 | 0 | -0.10184 | -0.025479
37 | 0.99976 | -0.0016399 | 0.0040071 | 0.0010043
38 | 0.99972 | -0.0019607 | 0.002958 | 0.00074135
39 | 0.99969 | -0.0021086 | 0.0020713 | 0.00051913
40 | 0.97139 | -0.20115 | 0.0025957 | 0.00065054
41 | 0.97136 | -0.20139 | 0.0021434 | 0.00053719
42 | 0.97144 | -0.20077 | 0.0020674 | 0.00051815
43 | 0.97156 | -0.19996 | 0.00259 | 0.00064911
44 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0023898 | -0.00059894 | 0.0023909 | 0.00059764 | 1.073e-06 | -1.2984e-06 | 0.0035939 | 0.0035933 | 0.0035939 | 0.98947 | -0.072934 | 0.98993 | -0.069683 | 1.3311
1 | 0.049844 | 0.012582 | -0.049734 | -0.012541 | 0.00010956 | 4.0536e-05 | 0.074955 | 0.074955 | 0.074955 | 0.98993 | -0.069683 | 0.98769 | -0.085368 | 13.8806
2 | -0.052235 | -0.013179 | 0.052328 | 0.013214 | 9.3699e-05 | 3.4784e-05 | 0.078548 | 0.078547 | 0.078548 | 0.98993 | -0.069683 | 0.99176 | -0.056921 | 14.5459
3 | 0.049734 | 0.012541 | -0.049626 | -0.012501 | 0.00010768 | 3.9848e-05 | 0.074955 | 0.074956 | 0.074956 | 0.98769 | -0.085368 | 0.98548 | -0.10085 | 13.8807
4 | -0.052328 | -0.013214 | 0.052372 | 0.01323 | 4.3548e-05 | 1.6165e-05 | 0.078547 | 0.078547 | 0.078547 | 0.99176 | -0.056921 | 0.99261 | -0.051005 | 14.5458
5 | 0.049626 | 0.012501 | -0.049538 | -0.012469 | 8.8106e-05 | 3.2608e-05 | 0.074956 | 0.074956 | 0.074956 | 0.98548 | -0.10085 | 0.98368 | -0.11357 | 13.8808
6 | -0.053927 | -0.01362 | 0.054211 | 0.013726 | 0.00028483 | 0.00010592 | 0.080878 | 0.080877 | 0.080878 | 0.99261 | -0.051005 | 0.99802 | -0.013633 | 14.9774
7 | 0.046705 | 0.011759 | -0.046674 | -0.011747 | 3.1278e-05 | 1.1521e-05 | 0.070671 | 0.070671 | 0.070671 | 0.98368 | -0.11357 | 0.983 | -0.11836 | 13.0872
8 | -0.0029773 | -0.00074618 | 0.0029776 | 0.00074602 | 2.6334e-07 | -1.6203e-07 | 0.0045073 | 0.0045072 | 0.0045073 | 0.98291 | -0.119 | 0.983 | -0.11836 | 1.6694
9 | 0.043697 | 0.011001 | -0.043583 | -0.01096 | 0.00011306 | 4.1392e-05 | 0.066164 | 0.066164 | 0.066164 | 0.983 | -0.11836 | 0.98037 | -0.13693 | 12.2527
10 | -0.056641 | -0.014335 | 0.056653 | 0.014339 | 1.2315e-05 | 4.5921e-06 | 0.084499 | 0.084499 | 0.084499 | 0.99802 | -0.013633 | 0.99824 | -0.012093 | 15.6479
11 | -0.061051 | -0.015441 | 0.061089 | 0.015455 | 3.8354e-05 | 1.4364e-05 | 0.091054 | 0.091054 | 0.091054 | 0.99824 | -0.012093 | 0.99889 | -0.0076402 | 16.8618
12 | 0.0043977 | 0.0011015 | -0.0043972 | -0.0011016 | 5.4179e-07 | -5.5738e-08 | 0.0065552 | 0.0065553 | 0.0065553 | 0.99824 | -0.012093 | 0.99812 | -0.012984 | 2.4279
13 | -0.063168 | -0.015976 | 0.063185 | 0.015982 | 1.637e-05 | 6.1411e-06 | 0.094151 | 0.094151 | 0.094151 | 0.99889 | -0.0076402 | 0.99916 | -0.0058027 | 17.4354
14 | 0.001719 | 0.00043037 | -0.0017189 | -0.00043079 | 1.494e-07 | -4.1898e-07 | 0.0025626 | 0.0025628 | 0.0025628 | 0.99812 | -0.012984 | 0.99803 | -0.013612 | 0.94917
15 | -0.065339 | -0.016522 | 0.065373 | 0.016535 | 3.4037e-05 | 1.279e-05 | 0.097359 | 0.097359 | 0.097359 | 0.99916 | -0.0058027 | 0.99969 | -0.0021086 | 18.0294
16 | 0.040721 | 0.010242 | -0.040591 | -0.010195 | 0.00013038 | 4.7398e-05 | 0.06182 | 0.061821 | 0.061821 | 0.98037 | -0.13693 | 0.97713 | -0.15996 | 11.4484
17 | 0.03793 | 0.009528 | -0.037926 | -0.0095265 | 4.1591e-06 | 1.4996e-06 | 0.057769 | 0.057769 | 0.057769 | 0.97713 | -0.15996 | 0.97702 | -0.16075 | 10.698
18 | 0.034899 | 0.008768 | -0.034872 | -0.0087583 | 2.7161e-05 | 9.6757e-06 | 0.05316 | 0.05316 | 0.05316 | 0.97702 | -0.16075 | 0.97624 | -0.16635 | 9.8444
19 | 0.034872 | 0.0087583 | -0.034819 | -0.0087394 | 5.2998e-05 | 1.8883e-05 | 0.05316 | 0.053161 | 0.053161 | 0.97624 | -0.16635 | 0.97471 | -0.1773 | 9.8445
20 | 0.034819 | 0.0087394 | -0.034789 | -0.0087279 | 3.0602e-05 | 1.1554e-05 | 0.053161 | 0.053161 | 0.053161 | 0.97471 | -0.1773 | 0.97383 | -0.18363 | 19.6891
21 | -0.013807 | -0.0034611 | 0.01382 | 0.0034652 | 1.2083e-05 | 4.1114e-06 | 0.021155 | 0.021154 | 0.021155 | 0.97123 | -0.20228 | 0.97211 | -0.19597 | 7.835
22 | 0.011358 | 0.0028472 | -0.011352 | -0.0028454 | 5.665e-06 | 1.808e-06 | 0.017402 | 0.017402 | 0.017402 | 0.97123 | -0.20228 | 0.97073 | -0.20588 | 6.4451
23 | 0.017725 | 0.0044429 | -0.01772 | -0.004441 | 5.3663e-06 | 1.9192e-06 | 0.027132 | 0.027132 | 0.027132 | 0.97211 | -0.19597 | 0.97181 | -0.19815 | 10.0491
24 | -0.031545 | -0.0079082 | 0.031599 | 0.0079285 | 5.3987e-05 | 2.0303e-05 | 0.048287 | 0.048287 | 0.048287 | 0.97211 | -0.19597 | 0.97383 | -0.18363 | 17.884
25 | 0.011352 | 0.0028454 | -0.011348 | -0.0028442 | 3.7433e-06 | 1.1949e-06 | 0.017402 | 0.017402 | 0.017402 | 0.97073 | -0.20588 | 0.9704 | -0.20827 | 6.4451
26 | 0.014748 | 0.003696 | -0.014747 | -0.003696 | 3.8265e-08 | 1.3227e-08 | 0.022581 | 0.022581 | 0.022581 | 0.97181 | -0.19815 | 0.9718 | -0.19817 | 8.3634
27 | 0.012311 | 0.0030853 | -0.012309 | -0.0030847 | 1.974e-06 | 6.4894e-07 | 0.01885 | 0.01885 | 0.01885 | 0.9718 | -0.19817 | 0.97164 | -0.19933 | 6.9815
28 | 0.0093984 | 0.0023553 | -0.0093976 | -0.002355 | 8.1268e-07 | 2.3471e-07 | 0.014393 | 0.014393 | 0.014393 | 0.97164 | -0.19933 | 0.97156 | -0.19996 | 5.3308
29 | -0.011566 | -0.0028985 | 0.011566 | 0.0028985 | 1.8836e-07 | 5.9119e-08 | 0.017224 | 0.017224 | 0.017224 | 0.99916 | -0.0058578 | 0.99918 | -0.0057402 | 6.3794
30 | 0.006396 | 0.0016028 | -0.0063958 | -0.0016028 | 2.0509e-07 | 3.1437e-08 | 0.0095253 | 0.0095253 | 0.0095253 | 0.99916 | -0.0058578 | 0.99913 | -0.0060895 | 3.5279
31 | -0.01432 | -0.0035886 | 0.014322 | 0.0035896 | 2.8182e-06 | 9.538e-07 | 0.021325 | 0.021325 | 0.021325 | 0.99918 | -0.0057402 | 0.99938 | -0.0043187 | 7.8982
32 | 0.0037414 | 0.00093751 | -0.0037411 | -0.00093761 | 3.356e-07 | -9.7756e-08 | 0.0055721 | 0.0055722 | 0.0055722 | 0.99913 | -0.0060895 | 0.99904 | -0.0067376 | 2.0638
33 | -0.017322 | -0.0043415 | 0.017325 | 0.0043424 | 2.7715e-06 | 9.7846e-07 | 0.025792 | 0.025792 | 0.025792 | 0.99938 | -0.0043187 | 0.99955 | -0.0031631 | 9.5526
34 | -0.020249 | -0.0050753 | 0.020249 | 0.0050753 | 1.5707e-07 | 5.6781e-08 | 0.030145 | 0.030145 | 0.030145 | 0.99955 | -0.0031631 | 0.99956 | -0.0031071 | 11.1647
35 | -0.02269 | -0.005687 | 0.022691 | 0.0056875 | 1.4178e-06 | 5.192e-07 | 0.033778 | 0.033778 | 0.033778 | 0.99956 | -0.0031071 | 0.99962 | -0.0026558 | 12.5104
36 | -0.026602 | -0.0066675 | 0.026611 | 0.0066711 | 9.7856e-06 | 3.6325e-06 | 0.039599 | 0.039599 | 0.039599 | 0.99962 | -0.0026558 | 1 | 0 | 14.6662
37 | 0.074431 | 0.018808 | -0.074414 | -0.018801 | 1.7175e-05 | 6.4881e-06 | 0.11081 | 0.11081 | 0.11081 | 1 | 0 | 0.99976 | -0.0016399 | 20.5201
38 | 0.070407 | 0.017797 | -0.070403 | -0.017796 | 3.1812e-06 | 1.1992e-06 | 0.10484 | 0.10484 | 0.10484 | 0.99976 | -0.0016399 | 0.99972 | -0.0019607 | 19.4156
39 | 0.067445 | 0.017055 | -0.067444 | -0.017054 | 1.4061e-06 | 5.2911e-07 | 0.10044 | 0.10044 | 0.10044 | 0.99972 | -0.0019607 | 0.99969 | -0.0021086 | 18.6003
40 | 0.0021435 | 0.00053708 | -0.0021434 | -0.00053719 | 7.1785e-08 | -1.0448e-07 | 0.0032834 | 0.0032835 | 0.0032835 | 0.97139 | -0.20115 | 0.97136 | -0.20139 | 1.2161
41 | -0.0047391 | -0.0011876 | 0.0047394 | 0.0011876 | 2.4934e-07 | 2.034e-09 | 0.0072596 | 0.0072595 | 0.0072596 | 0.97139 | -0.20115 | 0.97144 | -0.20077 | 2.6887
42 | -0.0068068 | -0.0017058 | 0.0068076 | 0.0017059 | 7.6885e-07 | 1.5537e-07 | 0.010426 | 0.010426 | 0.010426 | 0.97144 | -0.20077 | 0.97156 | -0.19996 | 3.8616

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.10395 | 0.026006

## res_load
| p_mw | q_mvar
0 | 0.0023898 | 0.00059894
1 | 0.0015549 | 0.00038968
2 | 0.0028329 | 0.00071
3 | 0.0029773 | 0.00074618
4 | 0.0024293 | 0.00060884
5 | 0.0020792 | 0.00052109
6 | 0.0026782 | 0.00067121
7 | 0.0021539 | 0.00053981
8 | 0.0017189 | 0.00043079
9 | 0.002862 | 0.00071728
10 | 0.0026612 | 0.00066695
11 | 0.0030264 | 0.0007585
12 | 0.0024496 | 0.00061392
13 | 0.0029724 | 0.00074495
14 | 0.0031898 | 0.00079943
15 | 0.011348 | 0.0028442
16 | 0.0024367 | 0.0006107
17 | 0.0029104 | 0.00072942
18 | 0.0051697 | 0.0012957
19 | 0.0027537 | 0.00069013
20 | 0.0026544 | 0.00066526
21 | 0.0029999 | 0.00075186
22 | 0.0037411 | 0.00093761
23 | 0.002924 | 0.00073282
24 | 0.0024407 | 0.00061169
25 | 0.0039101 | 0.00097997
26 | 0.0021036 | 0.00052721
27 | 0.0040071 | 0.0010043
28 | 0.002958 | 0.00074135
29 | 0.0020713 | 0.00051913
30 | 0.0025957 | 0.00065054
31 | 0.0021434 | 0.00053719
32 | 0.0020674 | 0.00051815
33 | 0.00259 | 0.00064911

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1