## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1631-158_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1631-158_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1631-158_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1631-158_0_2_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_1631-158_0_2_node_50 | 0.4 | n |  | TRUE
5 | bus_LV_1631-158_0_2_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_1631-158_0_2_node_16 | 0.4 | n |  | TRUE
7 | bus_LV_1631-158_0_2_node_14 | 0.4 | n |  | TRUE
8 | bus_LV_1631-158_0_2_node_4 | 0.4 | n |  | TRUE
9 | bus_LV_1631-158_0_2_node_51 | 0.4 | n |  | TRUE
10 | bus_LV_1631-158_0_2_node_13 | 0.4 | n |  | TRUE
11 | bus_LV_1631-158_0_2_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1631-158_0_2_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1631-158_0_2_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1631-158_0_2_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_1631-158_0_2_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_1631-158_0_2_node_21 | 0.4 | n |  | TRUE
17 | bus_LV_1631-158_0_2_node_18 | 0.4 | n |  | TRUE
18 | bus_LV_1631-158_0_2_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_1631-158_0_2_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_1631-158_0_2_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_1631-158_0_2_node_49 | 0.4 | n |  | TRUE
22 | bus_LV_1631-158_0_2_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_1631-158_0_2_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_1631-158_0_2_node_27 | 0.4 | n |  | TRUE
25 | bus_LV_1631-158_0_2_node_25 | 0.4 | n |  | TRUE
26 | bus_LV_1631-158_0_2_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_1631-158_0_2_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_1631-158_0_2_node_30 | 0.4 | n |  | TRUE
29 | bus_LV_1631-158_0_2_node_31 | 0.4 | n |  | TRUE
30 | bus_LV_1631-158_0_2_node_32 | 0.4 | n |  | TRUE
31 | bus_LV_1631-158_0_2_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_1631-158_0_2_node_26 | 0.4 | n |  | TRUE
33 | bus_LV_1631-158_0_2_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_1631-158_0_2_node_44 | 0.4 | n |  | TRUE
35 | bus_LV_1631-158_0_2_node_41 | 0.4 | n |  | TRUE
36 | bus_LV_1631-158_0_2_node_42 | 0.4 | n |  | TRUE
37 | bus_LV_1631-158_0_2_node_33 | 0.4 | n |  | TRUE
38 | bus_LV_1631-158_0_2_node_36 | 0.4 | n |  | TRUE
39 | bus_LV_1631-158_0_2_node_34 | 0.4 | n |  | TRUE
40 | bus_LV_1631-158_0_2_node_45 | 0.4 | n |  | TRUE
41 | bus_LV_1631-158_0_2_node_35 | 0.4 | n |  | TRUE
42 | bus_LV_1631-158_0_2_node_38 | 0.4 | n |  | TRUE
43 | bus_LV_1631-158_0_2_node_43 | 0.4 | n |  | TRUE
44 | bus_LV_1631-158_0_2_node_47 | 0.4 | n |  | TRUE
45 | bus_LV_1631-158_0_2_node_46 | 0.4 | n |  | TRUE
46 | bus_LV_1631-158_0_2_node_48 | 0.4 | n |  | TRUE
47 | bus_MV_145_0_node_60 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1631-158_0_2_load_0 | 0 | 0.0039882 | 0.00099954 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1631-158_0_2_load_2 | 2 | 0.0056352 | 0.0014123 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1631-158_0_2_load_5 | 3 | 0.002163 | 0.0005421 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1631-158_0_2_load_14 | 7 | 0.0041011 | 0.0010278 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1631-158_0_2_load_4 | 8 | 0.0027025 | 0.00067731 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1631-158_0_2_load_51 | 9 | 0.0031716 | 0.00079489 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1631-158_0_2_load_7 | 11 | 0.018452 | 0.0046245 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1631-158_0_2_load_8 | 12 | 0.00734 | 0.0018396 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1631-158_0_2_load_9 | 13 | 0.0030209 | 0.00075712 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1631-158_0_2_load_11 | 15 | 0.0052077 | 0.0013052 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1631-158_0_2_load_21 | 16 | 0.0049414 | 0.0012384 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1631-158_0_2_load_18 | 17 | 0.0054752 | 0.0013722 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1631-158_0_2_load_17 | 19 | 0.01234 | 0.0030927 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1631-158_0_2_load_15 | 20 | 0.0056608 | 0.0014187 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1631-158_0_2_load_49 | 21 | 0.0021963 | 0.00055044 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1631-158_0_2_load_19 | 22 | 0.0039804 | 0.00099757 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1631-158_0_2_load_20 | 23 | 0.0026491 | 0.00066393 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1631-158_0_2_load_27 | 24 | 0.0040381 | 0.001012 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1631-158_0_2_load_25 | 25 | 0.0042103 | 0.0010552 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1631-158_0_2_load_22 | 26 | 0.019144 | 0.004798 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1631-158_0_2_load_30 | 28 | 0.0045437 | 0.0011388 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1631-158_0_2_load_31 | 29 | 0.0034397 | 0.00086206 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1631-158_0_2_load_32 | 30 | 0.0062107 | 0.0015566 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1631-158_0_2_load_24 | 31 | 0.0025411 | 0.00063686 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1631-158_0_2_load_44 | 34 | 0.0029891 | 0.00074913 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1631-158_0_2_load_41 | 35 | 0.0068716 | 0.0017222 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1631-158_0_2_load_42 | 36 | 0.0021377 | 0.00053577 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1631-158_0_2_load_36 | 38 | 0.0035714 | 0.00089508 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1631-158_0_2_load_34 | 39 | 0.0031745 | 0.00079561 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1631-158_0_2_load_45 | 40 | 0.003195 | 0.00080075 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1631-158_0_2_load_35 | 41 | 0.0036182 | 0.00090682 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1631-158_0_2_load_38 | 42 | 0.0047242 | 0.001184 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1631-158_0_2_load_47 | 44 | 0.0016923 | 0.00042413 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1631-158_0_2_load_46 | 45 | 0.0045871 | 0.0011496 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1631-158_0_2_load_48 | 46 | 0.0016807 | 0.00042121 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 26 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1631-158_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.026551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1631-158_0_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.045028 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1631-158_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.14146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1631-158_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.13077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
4 | LV_1631-158_0_2_line_4 | NAYY 4x150 SE | 3 | 8 | 0.011826 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1631-158_0_2_line_5 | NAYY 4x150 SE | 4 | 9 | 0.12101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
6 | LV_1631-158_0_2_line_6 | NAYY 4x150 SE | 5 | 6 | 0.080198 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
7 | LV_1631-158_0_2_line_7 | NAYY 4x150 SE | 5 | 7 | 0.040655 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_1631-158_0_2_line_8 | NAYY 4x150 SE | 6 | 9 | 0.037427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
9 | LV_1631-158_0_2_line_9 | NAYY 4x150 SE | 7 | 10 | 0.030596 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
10 | LV_1631-158_0_2_line_10 | NAYY 4x150 SE | 10 | 20 | 0.0054527 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1631-158_0_2_line_11 | NAYY 4x150 SE | 10 | 18 | 0.16191 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
12 | LV_1631-158_0_2_line_12 | NAYY 4x150 SE | 11 | 12 | 0.00035437 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
13 | LV_1631-158_0_2_line_13 | NAYY 4x150 SE | 11 | 13 | 0.012798 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
14 | LV_1631-158_0_2_line_14 | NAYY 4x150 SE | 12 | 14 | 0.013577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
15 | LV_1631-158_0_2_line_15 | NAYY 4x150 SE | 13 | 15 | 0.004221 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
16 | LV_1631-158_0_2_line_16 | NAYY 4x150 SE | 14 | 16 | 0.011513 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1631-158_0_2_line_17 | NAYY 4x150 SE | 14 | 17 | 0.0091762 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
18 | LV_1631-158_0_2_line_18 | NAYY 4x150 SE | 15 | 18 | 0.19115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
19 | LV_1631-158_0_2_line_19 | NAYY 4x150 SE | 17 | 19 | 0.017228 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
20 | LV_1631-158_0_2_line_20 | NAYY 4x150 SE | 19 | 22 | 0.0048739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
21 | LV_1631-158_0_2_line_21 | NAYY 4x150 SE | 20 | 21 | 0.0021125 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1631-158_0_2_line_22 | NAYY 4x150 SE | 22 | 23 | 0.013626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
23 | LV_1631-158_0_2_line_23 | NAYY 4x150 SE | 23 | 24 | 0.0066984 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
24 | LV_1631-158_0_2_line_24 | NAYY 4x150 SE | 24 | 25 | 0.0011536 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
25 | LV_1631-158_0_2_line_25 | NAYY 4x150 SE | 25 | 31 | 0.01194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
26 | LV_1631-158_0_2_line_26 | NAYY 4x150 SE | 26 | 27 | 0.013881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
27 | LV_1631-158_0_2_line_27 | NAYY 4x150 SE | 27 | 28 | 0.041296 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1631-158_0_2_line_28 | NAYY 4x150 SE | 27 | 29 | 0.0035705 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
29 | LV_1631-158_0_2_line_29 | NAYY 4x150 SE | 29 | 30 | 0.0063323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
30 | LV_1631-158_0_2_line_30 | NAYY 4x150 SE | 30 | 37 | 0.0028719 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
31 | LV_1631-158_0_2_line_31 | NAYY 4x150 SE | 31 | 32 | 0.0098431 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
32 | LV_1631-158_0_2_line_32 | NAYY 4x150 SE | 32 | 33 | 0.004924 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
33 | LV_1631-158_0_2_line_33 | NAYY 4x150 SE | 33 | 34 | 0.013136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1631-158_0_2_line_34 | NAYY 4x150 SE | 33 | 35 | 0.015814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
35 | LV_1631-158_0_2_line_35 | NAYY 4x150 SE | 35 | 36 | 0.00017278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
36 | LV_1631-158_0_2_line_36 | NAYY 4x150 SE | 36 | 43 | 0.0098851 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
37 | LV_1631-158_0_2_line_37 | NAYY 4x150 SE | 37 | 38 | 0.020285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
38 | LV_1631-158_0_2_line_38 | NAYY 4x150 SE | 37 | 39 | 0.0071218 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1631-158_0_2_line_39 | NAYY 4x150 SE | 38 | 40 | 0.012691 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
40 | LV_1631-158_0_2_line_40 | NAYY 4x150 SE | 39 | 41 | 0.0066552 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1631-158_0_2_line_41 | NAYY 4x150 SE | 40 | 43 | 0.004899 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
42 | LV_1631-158_0_2_line_42 | NAYY 4x150 SE | 41 | 42 | 0.0093403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1631-158_0_2_line_43 | NAYY 4x150 SE | 43 | 46 | 0.0054555 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1631-158_0_2_line_44 | NAYY 4x150 SE | 44 | 45 | 0.010641 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1631-158_0_2_line_45 | NAYY 4x150 SE | 45 | 46 | 0.0088557 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1631-158_0_2_trafo_22 | 0.25 MVA 20/0.4 kV | 47 | 26 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2724857.9995 | 1205882.0479 | 2724878.0273 | 1205882.3003 | 2724884.0664 | 1205884.7624
1 | 2724857.9995 | 1205882.0479 | 2724874.8262 | 1205892.7413 | 2724885.3894 | 1205897.6993 | 2724891.3806 | 1205898.9923 | 2724898.6651 | 1205898.6435
2 | 2724857.9995 | 1205882.0479 | 2724797.7856 | 1205754.0463
3 | 2725013.5545 | 1205907.8002 | 2725010.9117 | 1205906.4771 | 2724994.3253 | 1205909.3877 | 2724988.9234 | 1205909.0188 | 2724982.0035 | 1205905.5713 | 2724973.9019 | 1205900.42 | 2724948.1653 | 1205881.7672 | 2724943.1825 | 1205878.4604 | 2724938.4574 | 1205877.7498 | 2724933.3329 | 1205878.6655 | 2724929.3694 | 1205880.4618 | 2724905.6576 | 1205897.0005 | 2724900.2685 | 1205898.5668 | 2724898.6651 | 1205898.6435
4 | 2724786.1567 | 1205753.5781 | 2724792.9446 | 1205754.8688 | 2724795.3472 | 1205754.5854 | 2724797.7856 | 1205754.0463
5 | 2725013.5545 | 1205907.8002 | 2725004.447 | 1205913.2581 | 2724997.0046 | 1205917.6834 | 2724989.5869 | 1205920.9306 | 2724984.1222 | 1205921.3833 | 2724959.2034 | 1205919.994 | 2724953.6804 | 1205920.69 | 2724950.1357 | 1205921.7389 | 2724946.8306 | 1205923.7046 | 2724941.8807 | 1205928.6381 | 2724935.9724 | 1205942.6474 | 2724932.6567 | 1205947.6596 | 2724917.4523 | 1205963.3989
6 | 2724885.2593 | 1205981.7051 | 2724880.2393 | 1205982.7231 | 2724873.6961 | 1205983.4535 | 2724862.9937 | 1205982.9738 | 2724823.3749 | 1205981.6333 | 2724805.1925 | 1205979.0179
7 | 2724805.1925 | 1205979.0179 | 2724796.4723 | 1205977.6123 | 2724781.903 | 1205976.4959 | 2724764.7029 | 1205977.0827
8 | 2724885.2593 | 1205981.7051 | 2724901.6272 | 1205975.0424 | 2724907.0461 | 1205972.0535 | 2724911.3938 | 1205968.9866 | 2724916.2319 | 1205964.6623 | 2724917.4523 | 1205963.3989
9 | 2724734.1581 | 1205978.8111 | 2724757.8588 | 1205977.3163 | 2724764.7029 | 1205977.0827
10 | 2724734.1581 | 1205978.8111 | 2724729.4214 | 1205976.1101
11 | 2724734.1581 | 1205978.8111 | 2724710.1448 | 1205980.344 | 2724706.3569 | 1205981.021 | 2724692.1069 | 1205984.2814 | 2724680.1929 | 1205985.7115 | 2724668.4947 | 1205986.2788 | 2724641.858 | 1205984.0988 | 2724626.178 | 1205984.7943 | 2724613.6598 | 1205985.6448 | 2724594.1729 | 1205988.2957 | 2724578.2848 | 1205992.7676 | 2724576.1999 | 1205993.8694 | 2724574.4981 | 1205995.2126
12 | 2724768.5266 | 1206057.0333 | 2724768.2377 | 1206056.8282
13 | 2724768.2377 | 1206056.8282 | 2724764.1691 | 1206053.9399 | 2724758.0515 | 1206049.0873
14 | 2724779.5977 | 1206064.8929 | 2724768.5266 | 1206057.0333
15 | 2724758.0515 | 1206049.0873 | 2724755.2855 | 1206046.8933 | 2724754.7023 | 1206046.5236
16 | 2724779.5977 | 1206064.8929 | 2724781.9476 | 1206062.3956 | 2724785.4313 | 1206061.7124 | 2724789.3554 | 1206061.7944 | 2724789.9623 | 1206061.8416
17 | 2724779.5977 | 1206064.8929 | 2724778.6573 | 1206068.387 | 2724778.5297 | 1206071.9426 | 2724779.111 | 1206073.8561
18 | 2724574.4981 | 1205995.2126 | 2724640.9585 | 1206000.2034 | 2724659.4297 | 1206002.4685 | 2724672.0884 | 1206004.7234 | 2724679.6988 | 1206006.8062 | 2724687.9013 | 1206009.6796 | 2724704.393 | 1206016.3736 | 2724748.4827 | 1206042.5812 | 2724754.7023 | 1206046.5236
19 | 2724786.9615 | 1206089.14 | 2724779.8181 | 1206076.1839 | 2724779.111 | 1206073.8561
20 | 2724789.3148 | 1206093.4082 | 2724786.9615 | 1206089.14
21 | 2724727.3413 | 1205975.7414 | 2724729.4214 | 1205976.1101 | 2724729.4214 | 1205976.1101
22 | 2724796.4496 | 1206105.0102 | 2724791.0258 | 1206096.5114 | 2724789.3148 | 1206093.4082
23 | 2724800.0531 | 1206110.6567 | 2724796.4496 | 1206105.0102
24 | 2724800.0531 | 1206110.6567 | 2724800.6737 | 1206111.6291
25 | 2724800.6737 | 1206111.6291 | 2724807.0971 | 1206121.6943
26 | 2724827.3574 | 1206064.7466 | 2724813.5179 | 1206063.6715
27 | 2724827.3574 | 1206064.7466 | 2724823.5868 | 1206076.599 | 2724820.1351 | 1206080.4854 | 2724812.172 | 1206085.8119 | 2724809.4529 | 1206086.3221 | 2724803.2225 | 1206076.8291
28 | 2724827.3574 | 1206064.7466 | 2724830.8119 | 1206065.6492
29 | 2724830.8119 | 1206065.6492 | 2724834.2508 | 1206066.5476 | 2724836.8686 | 1206067.4772
30 | 2724839.575 | 1206068.4382 | 2724836.8686 | 1206067.4772
31 | 2724812.1578 | 1206130.1343 | 2724808.9563 | 1206124.6076 | 2724807.0971 | 1206121.6943
32 | 2724812.1578 | 1206130.1343 | 2724816.5418 | 1206127.8687
33 | 2724816.5418 | 1206127.8687 | 2724829.5713 | 1206129.5355
34 | 2724816.5418 | 1206127.8687 | 2724822.5446 | 1206113.2385
35 | 2724822.5446 | 1206113.2385 | 2724822.6102 | 1206113.0787
36 | 2724826.3625 | 1206103.9335 | 2724822.6102 | 1206113.0787
37 | 2724839.575 | 1206068.4382 | 2724832.4988 | 1206087.4485
38 | 2724839.575 | 1206068.4382 | 2724845.5309 | 1206071.4094 | 2724845.9296 | 1206071.6506
39 | 2724832.4988 | 1206087.4485 | 2724828.0715 | 1206099.3422
40 | 2724851.624 | 1206075.0952 | 2724845.9296 | 1206071.6506
41 | 2724826.3625 | 1206103.9335 | 2724828.0715 | 1206099.3422
42 | 2724851.624 | 1206075.0952 | 2724859.6805 | 1206079.821
43 | 2724826.3625 | 1206103.9335 | 2724831.4428 | 1206105.9218
44 | 2724839.6894 | 1206109.1494 | 2724843.7194 | 1206099.3006
45 | 2724839.6894 | 1206109.1494 | 2724839.6894 | 1206109.1494 | 2724831.4428 | 1206105.9218

## bus_geodata
| x | y | coords
0 | 2724884.0664 | 1205884.7624
1 | 2724857.9995 | 1205882.0479
2 | 2724898.6651 | 1205898.6435
3 | 2724797.7856 | 1205754.0463
4 | 2725013.5545 | 1205907.8002
5 | 2724805.1925 | 1205979.0179
6 | 2724885.2593 | 1205981.7051
7 | 2724764.7029 | 1205977.0827
8 | 2724786.1567 | 1205753.5781
9 | 2724917.4523 | 1205963.3989
10 | 2724734.1581 | 1205978.8111
11 | 2724768.2377 | 1206056.8282
12 | 2724768.5266 | 1206057.0333
13 | 2724758.0515 | 1206049.0873
14 | 2724779.5977 | 1206064.8929
15 | 2724754.7023 | 1206046.5236
16 | 2724789.9623 | 1206061.8416
17 | 2724779.111 | 1206073.8561
18 | 2724574.4981 | 1205995.2126
19 | 2724786.9615 | 1206089.14
20 | 2724729.4214 | 1205976.1101
21 | 2724727.3413 | 1205975.7414
22 | 2724789.3148 | 1206093.4082
23 | 2724796.4496 | 1206105.0102
24 | 2724800.0531 | 1206110.6567
25 | 2724800.6737 | 1206111.6291
26 | 2724813.5179 | 1206063.6715
27 | 2724827.3574 | 1206064.7466
28 | 2724803.2225 | 1206076.8291
29 | 2724830.8119 | 1206065.6492
30 | 2724836.8686 | 1206067.4772
31 | 2724807.0971 | 1206121.6943
32 | 2724812.1578 | 1206130.1343
33 | 2724816.5418 | 1206127.8687
34 | 2724829.5713 | 1206129.5355
35 | 2724822.5446 | 1206113.2385
36 | 2724822.6102 | 1206113.0787
37 | 2724839.575 | 1206068.4382
38 | 2724832.4988 | 1206087.4485
39 | 2724845.9296 | 1206071.6506
40 | 2724828.0715 | 1206099.3422
41 | 2724851.624 | 1206075.0952
42 | 2724859.6805 | 1206079.821
43 | 2724826.3625 | 1206103.9335
44 | 2724843.7194 | 1206099.3006
45 | 2724839.6894 | 1206109.1494
46 | 2724831.4428 | 1206105.9218
47 | 2724827.3574 | 1206064.7466

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97168 | -0.20037 | 0.0039882 | 0.00099954
1 | 0.97183 | -0.19925 | 0 | 0
2 | 0.97242 | -0.19503 | 0.0056352 | 0.0014123
3 | 0.97082 | -0.20654 | 0.002163 | 0.0005421
4 | 0.97381 | -0.18502 | 0 | 0
5 | 0.97662 | -0.16484 | 0 | 0
6 | 0.97558 | -0.17229 | 0 | 0
7 | 0.97714 | -0.16106 | 0.0041011 | 0.0010278
8 | 0.97078 | -0.20688 | 0.0027025 | 0.00067731
9 | 0.97509 | -0.17577 | 0.0031716 | 0.00079489
10 | 0.97763 | -0.15757 | 0 | 0
11 | 0.98574 | -0.099885 | 0.018452 | 0.0046245
12 | 0.98575 | -0.099782 | 0.00734 | 0.0018396
13 | 0.98538 | -0.10238 | 0.0030209 | 0.00075712
14 | 0.98638 | -0.095336 | 0 | 0
15 | 0.98528 | -0.10314 | 0.0052077 | 0.0013052
16 | 0.9863 | -0.095919 | 0.0049414 | 0.0012384
17 | 0.98684 | -0.092101 | 0.0054752 | 0.0013722
18 | 0.98114 | -0.13252 | 0 | 0
19 | 0.98776 | -0.085554 | 0.01234 | 0.0030927
20 | 0.97757 | -0.15802 | 0.0056608 | 0.0014187
21 | 0.97756 | -0.15806 | 0.0021963 | 0.00055044
22 | 0.98807 | -0.083396 | 0.0039804 | 0.00099757
23 | 0.98896 | -0.077095 | 0.0026491 | 0.00066393
24 | 0.98941 | -0.073911 | 0.0040381 | 0.001012
25 | 0.9895 | -0.073339 | 0.0042103 | 0.0010552
26 | 1 | 0 | -0.159 | -0.03988
27 | 0.99843 | -0.010855 | 0 | 0
28 | 0.99817 | -0.012735 | 0.0045437 | 0.0011388
29 | 0.99804 | -0.013572 | 0.0034397 | 0.00086206
30 | 0.99736 | -0.018285 | 0.0062107 | 0.0015566
31 | 0.99037 | -0.06717 | 0.0025411 | 0.00063686
32 | 0.99111 | -0.061965 | 0 | 0
33 | 0.99148 | -0.059365 | 0 | 0
34 | 0.99143 | -0.059763 | 0.0029891 | 0.00074913
35 | 0.99271 | -0.050786 | 0.0068716 | 0.0017222
36 | 0.99272 | -0.050686 | 0.0021377 | 0.00053577
37 | 0.99707 | -0.020336 | 0 | 0
38 | 0.99515 | -0.033674 | 0.0035714 | 0.00089508
39 | 0.99695 | -0.021159 | 0.0031745 | 0.00079561
40 | 0.99399 | -0.041816 | 0.003195 | 0.00080075
41 | 0.99687 | -0.021717 | 0.0036182 | 0.00090682
42 | 0.99681 | -0.02216 | 0.0047242 | 0.001184
43 | 0.99355 | -0.044884 | 0 | 0
44 | 0.99338 | -0.046068 | 0.0016923 | 0.00042413
45 | 0.99341 | -0.045886 | 0.0045871 | 0.0011496
46 | 0.99349 | -0.045324 | 0.0016807 | 0.00042121
47 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0039882 | -0.00099954 | 0.0039888 | 0.00099945 | 6.1799e-07 | -9.1242e-08 | 0.0061075 | 0.0061074 | 0.0061075 | 0.97168 | -0.20037 | 0.97183 | -0.19925 | 2.262
1 | -0.0088594 | -0.0022189 | 0.0088645 | 0.0022203 | 5.1697e-06 | 1.4301e-06 | 0.013564 | 0.013564 | 0.013564 | 0.97183 | -0.19925 | 0.97242 | -0.19503 | 5.0239
2 | 0.0048705 | 0.0012195 | -0.0048656 | -0.0012193 | 4.9089e-06 | 1.3711e-07 | 0.0074571 | 0.0074577 | 0.0074577 | 0.97183 | -0.19925 | 0.97082 | -0.20654 | 2.7621
3 | -0.0145 | -0.0036326 | 0.01452 | 0.0036371 | 2.0084e-05 | 4.4754e-06 | 0.022187 | 0.022186 | 0.022187 | 0.97242 | -0.19503 | 0.97381 | -0.18502 | 4.1088
4 | 0.0027026 | 0.00067722 | -0.0027025 | -0.00067731 | 1.2663e-07 | -9.7517e-08 | 0.0041424 | 0.0041424 | 0.0041424 | 0.97082 | -0.20654 | 0.97078 | -0.20688 | 1.5342
5 | -0.01452 | -0.0036371 | 0.014538 | 0.0036412 | 1.8583e-05 | 4.1324e-06 | 0.022186 | 0.022185 | 0.022186 | 0.97381 | -0.18502 | 0.97509 | -0.17577 | 4.1085
6 | 0.017737 | 0.0044435 | -0.017719 | -0.0044385 | 1.8274e-05 | 5.0235e-06 | 0.027024 | 0.027025 | 0.027025 | 0.97662 | -0.16484 | 0.97558 | -0.17229 | 5.0046
7 | -0.017737 | -0.0044435 | 0.017746 | 0.004446 | 9.2632e-06 | 2.5448e-06 | 0.027024 | 0.027024 | 0.027024 | 0.97662 | -0.16484 | 0.97714 | -0.16106 | 5.0044
8 | 0.017719 | 0.0044385 | -0.01771 | -0.0044361 | 8.5283e-06 | 2.346e-06 | 0.027025 | 0.027025 | 0.027025 | 0.97558 | -0.17229 | 0.97509 | -0.17577 | 5.0046
9 | -0.021847 | -0.0054739 | 0.021858 | 0.0054772 | 1.0566e-05 | 3.2968e-06 | 0.033269 | 0.033269 | 0.033269 | 0.97714 | -0.16106 | 0.97763 | -0.15757 | 6.1609
10 | 0.0078576 | 0.0019693 | -0.0078571 | -0.0019692 | 4.8669e-07 | 1.1882e-07 | 0.01196 | 0.01196 | 0.01196 | 0.97763 | -0.15757 | 0.97757 | -0.15802 | 4.4296
11 | -0.029715 | -0.0074465 | 0.029819 | 0.0074821 | 0.00010333 | 3.5668e-05 | 0.045229 | 0.045227 | 0.045229 | 0.97763 | -0.15757 | 0.98114 | -0.13252 | 8.3757
12 | -0.056638 | -0.014217 | 0.056639 | 0.014217 | 8.0835e-07 | 3.0187e-07 | 0.085506 | 0.085506 | 0.085506 | 0.98574 | -0.099885 | 0.98575 | -0.099782 | 15.8344
13 | 0.038186 | 0.0095926 | -0.038173 | -0.0095878 | 1.3272e-05 | 4.7783e-06 | 0.057652 | 0.057652 | 0.057652 | 0.98574 | -0.099885 | 0.98538 | -0.10238 | 10.6763
14 | -0.063979 | -0.016057 | 0.064019 | 0.016072 | 3.9518e-05 | 1.4853e-05 | 0.096586 | 0.096586 | 0.096586 | 0.98575 | -0.099782 | 0.98638 | -0.095336 | 17.8863
15 | 0.035152 | 0.0088307 | -0.035148 | -0.0088294 | 3.7119e-06 | 1.3201e-06 | 0.05309 | 0.05309 | 0.05309 | 0.98538 | -0.10238 | 0.98528 | -0.10314 | 9.8315
16 | 0.0049418 | 0.0012384 | -0.0049414 | -0.0012384 | 3.9927e-07 | 6.6251e-09 | 0.007455 | 0.0074551 | 0.0074551 | 0.98638 | -0.095336 | 0.9863 | -0.095919 | 2.7611
17 | -0.06896 | -0.01731 | 0.068991 | 0.017322 | 3.099e-05 | 1.1685e-05 | 0.10404 | 0.10404 | 0.10404 | 0.98638 | -0.095336 | 0.98684 | -0.092101 | 19.2668
18 | 0.029941 | 0.0075242 | -0.029819 | -0.0074821 | 0.00012199 | 4.2069e-05 | 0.045225 | 0.045227 | 0.045227 | 0.98528 | -0.10314 | 0.98114 | -0.13252 | 8.3754
19 | -0.074467 | -0.018694 | 0.074534 | 0.01872 | 6.7782e-05 | 2.5629e-05 | 0.1123 | 0.1123 | 0.1123 | 0.98684 | -0.092101 | 0.98776 | -0.085554 | 20.7957
20 | -0.086874 | -0.021812 | 0.0869 | 0.021822 | 2.605e-05 | 9.8946e-06 | 0.13089 | 0.13089 | 0.13089 | 0.98776 | -0.085554 | 0.98807 | -0.083396 | 24.2381
21 | 0.0021963 | 0.00055042 | -0.0021963 | -0.00055044 | 1.4733e-08 | -2.0818e-08 | 0.0033431 | 0.0033432 | 0.0033432 | 0.97757 | -0.15802 | 0.97756 | -0.15806 | 1.2382
22 | -0.090881 | -0.02282 | 0.09096 | 0.02285 | 7.9651e-05 | 3.0286e-05 | 0.13688 | 0.13688 | 0.13688 | 0.98807 | -0.083396 | 0.98896 | -0.077095 | 25.3482
23 | -0.093609 | -0.023514 | 0.093651 | 0.02353 | 4.147e-05 | 1.5778e-05 | 0.14087 | 0.14087 | 0.14087 | 0.98896 | -0.077095 | 0.98941 | -0.073911 | 26.0863
24 | -0.097689 | -0.024542 | 0.097697 | 0.024545 | 7.7708e-06 | 2.9591e-06 | 0.14694 | 0.14694 | 0.14694 | 0.98941 | -0.073911 | 0.9895 | -0.073339 | 27.2109
25 | -0.10191 | -0.0256 | 0.10199 | 0.025633 | 8.7515e-05 | 3.3352e-05 | 0.15327 | 0.15327 | 0.15327 | 0.9895 | -0.073339 | 0.99037 | -0.06717 | 28.3834
26 | 0.1582 | 0.03988 | -0.15796 | -0.039788 | 0.00024016 | 9.2005e-05 | 0.23548 | 0.23548 | 0.23548 | 1 | 0 | 0.99843 | -0.010855 | 43.608
27 | 0.0045449 | 0.0011387 | -0.0045437 | -0.0011388 | 1.1822e-06 | -8.5227e-08 | 0.0067733 | 0.0067735 | 0.0067735 | 0.99843 | -0.010855 | 0.99817 | -0.012735 | 2.5087
28 | 0.15341 | 0.038649 | -0.15335 | -0.038627 | 5.8271e-05 | 2.2319e-05 | 0.22871 | 0.22871 | 0.22871 | 0.99843 | -0.010855 | 0.99804 | -0.013572 | 42.3537
29 | 0.14992 | 0.037765 | -0.14982 | -0.037727 | 9.8761e-05 | 3.782e-05 | 0.22358 | 0.22358 | 0.22358 | 0.99804 | -0.013572 | 0.99736 | -0.018285 | 41.404
30 | 0.14361 | 0.03617 | -0.14356 | -0.036155 | 4.1156e-05 | 1.5754e-05 | 0.21432 | 0.21432 | 0.21432 | 0.99736 | -0.018285 | 0.99707 | -0.020336 | 39.6881
31 | -0.10454 | -0.02627 | 0.10461 | 0.026299 | 7.5783e-05 | 2.8894e-05 | 0.15709 | 0.15709 | 0.15709 | 0.99037 | -0.06717 | 0.99111 | -0.061965 | 29.0904
32 | -0.10461 | -0.026299 | 0.10465 | 0.026314 | 3.791e-05 | 1.4454e-05 | 0.15709 | 0.15709 | 0.15709 | 0.99111 | -0.061965 | 0.99148 | -0.059365 | 29.0904
33 | 0.0029892 | 0.00074903 | -0.0029891 | -0.00074913 | 1.6497e-07 | -1.0595e-07 | 0.0044862 | 0.0044863 | 0.0044863 | 0.99148 | -0.059365 | 0.99143 | -0.059763 | 1.6616
34 | -0.10764 | -0.027063 | 0.10777 | 0.027112 | 0.0001288 | 4.9132e-05 | 0.16157 | 0.16157 | 0.16157 | 0.99148 | -0.059365 | 0.99271 | -0.050786 | 29.9212
35 | -0.11464 | -0.028834 | 0.11464 | 0.028835 | 1.5925e-06 | 6.0803e-07 | 0.17187 | 0.17187 | 0.17187 | 0.99271 | -0.050786 | 0.99272 | -0.050686 | 31.8286
36 | -0.11678 | -0.02937 | 0.11687 | 0.029406 | 9.4537e-05 | 3.6104e-05 | 0.17508 | 0.17508 | 0.17508 | 0.99272 | -0.050686 | 0.99355 | -0.044884 | 32.422
37 | 0.13205 | 0.033268 | -0.1318 | -0.033173 | 0.00024592 | 9.4058e-05 | 0.19712 | 0.19712 | 0.19712 | 0.99707 | -0.020336 | 0.99515 | -0.033674 | 36.5046
38 | 0.011519 | 0.002887 | -0.011518 | -0.0028866 | 1.3134e-06 | 4.1226e-07 | 0.017191 | 0.017191 | 0.017191 | 0.99707 | -0.020336 | 0.99695 | -0.021159 | 6.3671
39 | 0.12823 | 0.032278 | -0.12808 | -0.032223 | 0.00014564 | 5.5686e-05 | 0.19178 | 0.19178 | 0.19178 | 0.99515 | -0.033674 | 0.99399 | -0.041816 | 35.5157
40 | 0.0083433 | 0.002091 | -0.0083427 | -0.0020908 | 6.4401e-07 | 1.6092e-07 | 0.012453 | 0.012453 | 0.012453 | 0.99695 | -0.021159 | 0.99687 | -0.021717 | 4.6122
41 | 0.12489 | 0.031422 | -0.12483 | -0.031402 | 5.3451e-05 | 2.0431e-05 | 0.187 | 0.187 | 0.187 | 0.99399 | -0.041816 | 0.99355 | -0.044884 | 34.6299
42 | 0.0047244 | 0.001184 | -0.0047242 | -0.001184 | 2.8985e-07 | -1.0283e-08 | 0.0070521 | 0.0070521 | 0.0070521 | 0.99687 | -0.021717 | 0.99681 | -0.02216 | 2.6119
43 | 0.0079611 | 0.0019951 | -0.0079606 | -0.0019949 | 4.8395e-07 | 1.1549e-07 | 0.011923 | 0.011923 | 0.011923 | 0.99355 | -0.044884 | 0.99349 | -0.045324 | 4.416
44 | -0.0016923 | -0.00042413 | 0.0016923 | 0.00042401 | 4.2669e-08 | -1.2136e-07 | 0.0025349 | 0.0025349 | 0.0025349 | 0.99338 | -0.046068 | 0.99341 | -0.045886 | 0.93887
45 | -0.0062795 | -0.0015737 | 0.00628 | 0.0015737 | 4.8889e-07 | 7.3371e-08 | 0.0094059 | 0.0094059 | 0.0094059 | 0.99341 | -0.045886 | 0.99349 | -0.045324 | 3.4837

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.17814 | 0.044678

## res_load
| p_mw | q_mvar
0 | 0.0039882 | 0.00099954
1 | 0.0056352 | 0.0014123
2 | 0.002163 | 0.0005421
3 | 0.0041011 | 0.0010278
4 | 0.0027025 | 0.00067731
5 | 0.0031716 | 0.00079489
6 | 0.018452 | 0.0046245
7 | 0.00734 | 0.0018396
8 | 0.0030209 | 0.00075712
9 | 0.0052077 | 0.0013052
10 | 0.0049414 | 0.0012384
11 | 0.0054752 | 0.0013722
12 | 0.01234 | 0.0030927
13 | 0.0056608 | 0.0014187
14 | 0.0021963 | 0.00055044
15 | 0.0039804 | 0.00099757
16 | 0.0026491 | 0.00066393
17 | 0.0040381 | 0.001012
18 | 0.0042103 | 0.0010552
19 | 0.019144 | 0.004798
20 | 0.0045437 | 0.0011388
21 | 0.0034397 | 0.00086206
22 | 0.0062107 | 0.0015566
23 | 0.0025411 | 0.00063686
24 | 0.0029891 | 0.00074913
25 | 0.0068716 | 0.0017222
26 | 0.0021377 | 0.00053577
27 | 0.0035714 | 0.00089508
28 | 0.0031745 | 0.00079561
29 | 0.003195 | 0.00080075
30 | 0.0036182 | 0.00090682
31 | 0.0047242 | 0.001184
32 | 0.0016923 | 0.00042413
33 | 0.0045871 | 0.0011496
34 | 0.0016807 | 0.00042121

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1