## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1631-176_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1631-176_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1631-176_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1631-176_0_4_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_1631-176_0_4_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_1631-176_0_4_node_10 | 0.4 | n |  | TRUE
6 | bus_LV_1631-176_0_4_node_20 | 0.4 | n |  | TRUE
7 | bus_LV_1631-176_0_4_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_1631-176_0_4_node_13 | 0.4 | n |  | TRUE
9 | bus_LV_1631-176_0_4_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_1631-176_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_1631-176_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1631-176_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1631-176_0_4_node_17 | 0.4 | n |  | TRUE
14 | bus_LV_1631-176_0_4_node_18 | 0.4 | n |  | TRUE
15 | bus_LV_1631-176_0_4_node_19 | 0.4 | n |  | TRUE
16 | bus_LV_1631-176_0_4_node_16 | 0.4 | n |  | TRUE
17 | bus_LV_1631-176_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_1631-176_0_4_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_1631-176_0_4_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_1631-176_0_4_node_23 | 0.4 | n |  | TRUE
21 | bus_LV_1631-176_0_4_node_33 | 0.4 | n |  | TRUE
22 | bus_LV_1631-176_0_4_node_24 | 0.4 | n |  | TRUE
23 | bus_LV_1631-176_0_4_node_22 | 0.4 | n |  | TRUE
24 | bus_LV_1631-176_0_4_node_35 | 0.4 | n |  | TRUE
25 | bus_LV_1631-176_0_4_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_1631-176_0_4_node_28 | 0.4 | n |  | TRUE
27 | bus_LV_1631-176_0_4_node_25 | 0.4 | n |  | TRUE
28 | bus_LV_1631-176_0_4_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_1631-176_0_4_node_27 | 0.4 | n |  | TRUE
30 | bus_LV_1631-176_0_4_node_29 | 0.4 | n |  | TRUE
31 | bus_LV_1631-176_0_4_node_30 | 0.4 | n |  | TRUE
32 | bus_LV_1631-176_0_4_node_31 | 0.4 | n |  | TRUE
33 | bus_LV_1631-176_0_4_node_32 | 0.4 | n |  | TRUE
34 | bus_LV_1631-176_0_4_node_34 | 0.4 | n |  | TRUE
35 | bus_MV_145_0_node_122 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1631-176_0_4_load_0 | 0 | 0.037317 | 0.0093525 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1631-176_0_4_load_1 | 1 | 0.019236 | 0.0048211 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1631-176_0_4_load_3 | 4 | 0.0017745 | 0.00044473 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1631-176_0_4_load_20 | 6 | 0.0047546 | 0.0011916 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1631-176_0_4_load_4 | 7 | 0.0028019 | 0.00070223 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1631-176_0_4_load_9 | 9 | 0.0055258 | 0.0013849 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1631-176_0_4_load_6 | 10 | 0.0072243 | 0.0018106 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1631-176_0_4_load_7 | 11 | 0.0043964 | 0.0011018 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1631-176_0_4_load_8 | 12 | 0.0064022 | 0.0016045 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1631-176_0_4_load_18 | 14 | 0.0042172 | 0.0010569 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1631-176_0_4_load_19 | 15 | 0.003533 | 0.00088546 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1631-176_0_4_load_16 | 16 | 0.0037719 | 0.00094532 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1631-176_0_4_load_14 | 18 | 0.0098097 | 0.0024586 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1631-176_0_4_load_15 | 19 | 0.0047061 | 0.0011795 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1631-176_0_4_load_22 | 23 | 0.0094541 | 0.0023694 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1631-176_0_4_load_35 | 24 | 0.022687 | 0.0056859 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1631-176_0_4_load_21 | 25 | 0.0028434 | 0.00071262 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1631-176_0_4_load_28 | 26 | 0.048306 | 0.012107 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1631-176_0_4_load_25 | 27 | 0.0025133 | 0.0006299 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1631-176_0_4_load_26 | 28 | 0.0030223 | 0.00075746 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1631-176_0_4_load_27 | 29 | 0.0030748 | 0.00077061 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1631-176_0_4_load_29 | 30 | 0.0022318 | 0.00055934 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1631-176_0_4_load_31 | 32 | 0.022488 | 0.005636 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1631-176_0_4_load_34 | 34 | 0.0062817 | 0.0015744 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 23 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1631-176_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.019593 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1631-176_0_4_line_1 | NAYY 4x150 SE | 1 | 2 | 0.019907 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1631-176_0_4_line_2 | NAYY 4x150 SE | 2 | 3 | 0.019064 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1631-176_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.017608 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1631-176_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.006581 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1631-176_0_4_line_5 | NAYY 4x150 SE | 3 | 6 | 0.009757 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1631-176_0_4_line_6 | NAYY 4x150 SE | 4 | 7 | 0.015745 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1631-176_0_4_line_7 | NAYY 4x150 SE | 5 | 8 | 0.014579 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1631-176_0_4_line_8 | NAYY 4x150 SE | 5 | 9 | 0.010483 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1631-176_0_4_line_9 | NAYY 4x150 SE | 8 | 19 | 0.026827 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1631-176_0_4_line_10 | NAYY 4x150 SE | 8 | 18 | 0.029502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1631-176_0_4_line_11 | NAYY 4x150 SE | 10 | 11 | 0.028494 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1631-176_0_4_line_12 | NAYY 4x150 SE | 11 | 12 | 0.0079647 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1631-176_0_4_line_13 | NAYY 4x150 SE | 12 | 13 | 0.015127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1631-176_0_4_line_14 | NAYY 4x150 SE | 13 | 14 | 0.013393 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
15 | LV_1631-176_0_4_line_15 | NAYY 4x150 SE | 13 | 15 | 0.014594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1631-176_0_4_line_16 | NAYY 4x150 SE | 13 | 16 | 0.014411 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1631-176_0_4_line_17 | NAYY 4x150 SE | 14 | 20 | 0.029234 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
18 | LV_1631-176_0_4_line_18 | NAYY 4x150 SE | 15 | 21 | 0.052289 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1631-176_0_4_line_19 | NAYY 4x150 SE | 16 | 17 | 0.018568 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1631-176_0_4_line_20 | NAYY 4x150 SE | 17 | 18 | 0.014576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1631-176_0_4_line_21 | NAYY 4x150 SE | 20 | 22 | 0.007535 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1631-176_0_4_line_22 | NAYY 4x150 SE | 20 | 23 | 0.013089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
23 | LV_1631-176_0_4_line_23 | NAYY 4x150 SE | 21 | 24 | 0.014853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1631-176_0_4_line_24 | NAYY 4x150 SE | 22 | 26 | 0.039021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1631-176_0_4_line_25 | NAYY 4x150 SE | 22 | 27 | 0.012874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1631-176_0_4_line_26 | NAYY 4x150 SE | 23 | 25 | 0.00076137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1631-176_0_4_line_27 | NAYY 4x150 SE | 27 | 28 | 0.00020034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1631-176_0_4_line_28 | NAYY 4x150 SE | 28 | 29 | 0.02208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1631-176_0_4_line_29 | NAYY 4x150 SE | 29 | 30 | 0.00058508 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1631-176_0_4_line_30 | NAYY 4x150 SE | 30 | 31 | 0.0088748 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1631-176_0_4_line_31 | NAYY 4x150 SE | 31 | 32 | 0.019875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1631-176_0_4_line_32 | NAYY 4x150 SE | 31 | 33 | 0.041968 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1631-176_0_4_line_33 | NAYY 4x150 SE | 33 | 34 | 0.018484 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1631-176_0_4_trafo_22 | 0.25 MVA 20/0.4 kV | 35 | 23 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2723049.0771 | 1204629.9121 | 2723056.8529 | 1204618.324 | 2723057.5131 | 1204616.2027 | 2723057.7356 | 1204612.7936 | 2723057.7356 | 1204612.7936
1 | 2723052.4793 | 1204595.3388 | 2723051.074 | 1204599.2795 | 2723050.8799 | 1204601.3104 | 2723051.0612 | 1204602.4817 | 2723055.4951 | 1204607.4101 | 2723057.0707 | 1204610.3447 | 2723057.7356 | 1204612.7936
2 | 2723064.2272 | 1204580.3029 | 2723052.4793 | 1204595.3388
3 | 2723052.4793 | 1204595.3388 | 2723037.6594 | 1204585.8299
4 | 2723058.6139 | 1204576.8402 | 2723064.2272 | 1204580.3029
5 | 2723064.2272 | 1204580.3029 | 2723072.0288 | 1204586.1624
6 | 2723037.6594 | 1204585.8299 | 2723033.6427 | 1204583.2527 | 2723027.7017 | 1204592.4781
7 | 2723058.6139 | 1204576.8402 | 2723063.3728 | 1204569.6995 | 2723066.7999 | 1204564.7775
8 | 2723058.6139 | 1204576.8402 | 2723049.8493 | 1204571.09
9 | 2723064.9452 | 1204539.2089 | 2723062.4693 | 1204556.6822 | 2723066.7999 | 1204564.7775
10 | 2723066.7999 | 1204564.7775 | 2723073.9185 | 1204555.3949 | 2723077.373 | 1204553.9428 | 2723081.0025 | 1204553.5951 | 2723089.1989 | 1204559.8835
11 | 2723126.7962 | 1204561.7104 | 2723125.255 | 1204555.4308 | 2723124.8699 | 1204551.9647 | 2723125.7186 | 1204547.7124 | 2723126.8804 | 1204543.4108 | 2723131.6734 | 1204534.9212
12 | 2723126.7962 | 1204561.7104 | 2723128.6947 | 1204569.4455
13 | 2723126.3039 | 1204583.8962 | 2723128.2095 | 1204580.4217 | 2723129.0503 | 1204576.9253 | 2723129.3476 | 1204572.1056 | 2723128.6947 | 1204569.4455
14 | 2723126.3039 | 1204583.8962 | 2723119.7347 | 1204595.568
15 | 2723126.3039 | 1204583.8962 | 2723135.7592 | 1204585.559 | 2723139.4422 | 1204588.9316
16 | 2723126.3039 | 1204583.8962 | 2723116.3482 | 1204581.4002 | 2723112.6529 | 1204579.5179
17 | 2723108.1176 | 1204621.8165 | 2723112.7062 | 1204617.0297 | 2723119.2575 | 1204596.4159 | 2723119.7347 | 1204595.568
18 | 2723163.1569 | 1204625.2984 | 2723153.9361 | 1204624.4409 | 2723150.2325 | 1204621.0064 | 2723148.9405 | 1204616.8655 | 2723148.9088 | 1204613.6069 | 2723151.7351 | 1204600.1884 | 2723139.4422 | 1204588.9316
19 | 2723097.0751 | 1204569.4494 | 2723109.8867 | 1204578.1089 | 2723112.6529 | 1204579.5179
20 | 2723097.0751 | 1204569.4494 | 2723098.5326 | 1204567.0443 | 2723089.1989 | 1204559.8835
21 | 2723108.1176 | 1204621.8165 | 2723112.2104 | 1204628.1501
22 | 2723108.1176 | 1204621.8165 | 2723103.6566 | 1204615.6199 | 2723099.8005 | 1204611.7632
23 | 2723165.5815 | 1204610.6929 | 2723163.2819 | 1204621.4536 | 2723163.1569 | 1204625.2984
24 | 2723112.2104 | 1204628.1501 | 2723086.6444 | 1204657.6296
25 | 2723112.2104 | 1204628.1501 | 2723118.745 | 1204639.2425
26 | 2723099.2622 | 1204611.2247 | 2723099.8005 | 1204611.7632
27 | 2723118.745 | 1204639.2425 | 2723118.8467 | 1204639.4152
28 | 2723118.8467 | 1204639.4152 | 2723130.0542 | 1204658.4397
29 | 2723130.0542 | 1204658.4397 | 2723130.3512 | 1204658.9438
30 | 2723134.8558 | 1204666.5904 | 2723130.3512 | 1204658.9438
31 | 2723134.8558 | 1204666.5904 | 2723117.4061 | 1204676.1935
32 | 2723134.8558 | 1204666.5904 | 2723139.3261 | 1204674.1772 | 2723156.4174 | 1204702.5955
33 | 2723156.4174 | 1204702.5955 | 2723151.4786 | 1204706.6523 | 2723143.6856 | 1204715.8986

## bus_geodata
| x | y | coords
0 | 2723049.0771 | 1204629.9121
1 | 2723057.7356 | 1204612.7936
2 | 2723052.4793 | 1204595.3388
3 | 2723064.2272 | 1204580.3029
4 | 2723037.6594 | 1204585.8299
5 | 2723058.6139 | 1204576.8402
6 | 2723072.0288 | 1204586.1624
7 | 2723027.7017 | 1204592.4781
8 | 2723066.7999 | 1204564.7775
9 | 2723049.8493 | 1204571.09
10 | 2723131.6734 | 1204534.9212
11 | 2723126.7962 | 1204561.7104
12 | 2723128.6947 | 1204569.4455
13 | 2723126.3039 | 1204583.8962
14 | 2723119.7347 | 1204595.568
15 | 2723139.4422 | 1204588.9316
16 | 2723112.6529 | 1204579.5179
17 | 2723097.0751 | 1204569.4494
18 | 2723089.1989 | 1204559.8835
19 | 2723064.9452 | 1204539.2089
20 | 2723108.1176 | 1204621.8165
21 | 2723163.1569 | 1204625.2984
22 | 2723112.2104 | 1204628.1501
23 | 2723099.8005 | 1204611.7632
24 | 2723165.5815 | 1204610.6929
25 | 2723099.2622 | 1204611.2247
26 | 2723086.6444 | 1204657.6296
27 | 2723118.745 | 1204639.2425
28 | 2723118.8467 | 1204639.4152
29 | 2723130.0542 | 1204658.4397
30 | 2723130.3512 | 1204658.9438
31 | 2723134.8558 | 1204666.5904
32 | 2723117.4061 | 1204676.1935
33 | 2723156.4174 | 1204702.5955
34 | 2723143.6856 | 1204715.8986
35 | 2723108.1176 | 1204621.8165

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97952 | -0.14382 | 0.037317 | 0.0093525
1 | 0.98059 | -0.13622 | 0.019236 | 0.0048211
2 | 0.98223 | -0.12456 | 0 | 0
3 | 0.98392 | -0.11252 | 0 | 0
4 | 0.98211 | -0.12539 | 0.0017745 | 0.00044473
5 | 0.98455 | -0.10805 | 0 | 0
6 | 0.98385 | -0.113 | 0.0047546 | 0.0011916
7 | 0.98204 | -0.12585 | 0.0028019 | 0.00070223
8 | 0.98606 | -0.097347 | 0 | 0
9 | 0.98447 | -0.10865 | 0.0055258 | 0.0013849
10 | 0.99452 | -0.038152 | 0.0072243 | 0.0018106
11 | 0.99481 | -0.036075 | 0.0043964 | 0.0011018
12 | 0.99495 | -0.035141 | 0.0064022 | 0.0016045
13 | 0.99534 | -0.032393 | 0 | 0
14 | 0.99663 | -0.023366 | 0.0042172 | 0.0010569
15 | 0.99479 | -0.036251 | 0.003533 | 0.00088546
16 | 0.99346 | -0.045443 | 0.0037719 | 0.00094532
17 | 0.99115 | -0.061618 | 0 | 0
18 | 0.98933 | -0.074369 | 0.0098097 | 0.0024586
19 | 0.98588 | -0.098643 | 0.0047061 | 0.0011795
20 | 0.99858 | -0.0098612 | 0 | 0
21 | 0.99308 | -0.048238 | 0 | 0
22 | 0.99763 | -0.016499 | 0 | 0
23 | 1 | 0 | -0.23199 | -0.058236
24 | 0.9926 | -0.05165 | 0.022687 | 0.0056859
25 | 1 | -2.1606e-05 | 0.0028434 | 0.00071262
26 | 0.99493 | -0.035453 | 0.048306 | 0.012107
27 | 0.9969 | -0.021618 | 0.0025133 | 0.0006299
28 | 0.99689 | -0.021693 | 0.0030223 | 0.00075746
29 | 0.99581 | -0.029259 | 0.0030748 | 0.00077061
30 | 0.99579 | -0.029442 | 0.0022318 | 0.00055934
31 | 0.99542 | -0.032014 | 0 | 0
32 | 0.99478 | -0.036518 | 0.022488 | 0.005636
33 | 0.99504 | -0.034672 | 0 | 0
34 | 0.99488 | -0.035842 | 0.0062817 | 0.0015744
35 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.037317 | -0.0093525 | 0.037356 | 0.0093674 | 3.929e-05 | 1.4865e-05 | 0.056689 | 0.056689 | 0.056689 | 0.97952 | -0.14382 | 0.98059 | -0.13622 | 20.9959
1 | -0.056593 | -0.014188 | 0.056684 | 0.014223 | 9.1616e-05 | 3.4985e-05 | 0.08588 | 0.08588 | 0.08588 | 0.98059 | -0.13622 | 0.98223 | -0.12456 | 31.8073
2 | -0.061261 | -0.01537 | 0.061364 | 0.015409 | 0.00010248 | 3.9172e-05 | 0.092814 | 0.092813 | 0.092814 | 0.98223 | -0.12456 | 0.98392 | -0.11252 | 34.3754
3 | 0.0045771 | 0.0011468 | -0.0045766 | -0.0011468 | 5.2829e-07 | -1.9654e-08 | 0.006934 | 0.0069341 | 0.0069341 | 0.98223 | -0.12456 | 0.98211 | -0.12539 | 2.5682
4 | -0.066119 | -0.016601 | 0.06616 | 0.016617 | 4.1069e-05 | 1.5712e-05 | 0.1 | 0.1 | 0.1 | 0.98392 | -0.11252 | 0.98455 | -0.10805 | 37.0387
5 | 0.004755 | 0.0011916 | -0.0047546 | -0.0011916 | 3.1484e-07 | -2.8206e-09 | 0.0071911 | 0.0071911 | 0.0071911 | 0.98392 | -0.11252 | 0.98385 | -0.113 | 2.6634
6 | 0.0028021 | 0.0007021 | -0.0028019 | -0.00070223 | 1.7709e-07 | -1.3112e-07 | 0.0042455 | 0.0042456 | 0.0042456 | 0.98211 | -0.12539 | 0.98204 | -0.12585 | 1.5724
7 | -0.071686 | -0.018002 | 0.071793 | 0.018043 | 0.00010681 | 4.0895e-05 | 0.10836 | 0.10836 | 0.10836 | 0.98455 | -0.10805 | 0.98606 | -0.097347 | 40.1321
8 | 0.0055262 | 0.0013849 | -0.0055258 | -0.0013849 | 4.563e-07 | 4.2204e-08 | 0.0083521 | 0.0083522 | 0.0083522 | 0.98455 | -0.10805 | 0.98447 | -0.10865 | 3.0934
9 | 0.0047069 | 0.0011794 | -0.0047061 | -0.0011795 | 8.4458e-07 | -1.731e-08 | 0.0071029 | 0.007103 | 0.007103 | 0.98606 | -0.097347 | 0.98588 | -0.098643 | 2.6308
10 | -0.0765 | -0.019222 | 0.076745 | 0.019316 | 0.00024541 | 9.401e-05 | 0.11546 | 0.11546 | 0.11546 | 0.98606 | -0.097347 | 0.98933 | -0.074369 | 42.7628
11 | -0.0072243 | -0.0018106 | 0.0072264 | 0.001811 | 2.0774e-06 | 4.2915e-07 | 0.010809 | 0.010809 | 0.010809 | 0.99452 | -0.038152 | 0.99481 | -0.036075 | 4.0034
12 | -0.011623 | -0.0029129 | 0.011624 | 0.0029133 | 1.5021e-06 | 4.7431e-07 | 0.017385 | 0.017385 | 0.017385 | 0.99481 | -0.036075 | 0.99495 | -0.035141 | 6.4389
13 | -0.018026 | -0.0045179 | 0.018033 | 0.0045203 | 6.8606e-06 | 2.4422e-06 | 0.02696 | 0.02696 | 0.02696 | 0.99495 | -0.035141 | 0.99534 | -0.032393 | 9.9851
14 | -0.13516 | -0.034033 | 0.13533 | 0.034098 | 0.00017071 | 6.5309e-05 | 0.20212 | 0.20212 | 0.20212 | 0.99534 | -0.032393 | 0.99663 | -0.023366 | 37.4292
15 | 0.026283 | 0.0065944 | -0.026269 | -0.0065891 | 1.4062e-05 | 5.2188e-06 | 0.039295 | 0.039295 | 0.039295 | 0.99534 | -0.032393 | 0.99479 | -0.036251 | 14.5536
16 | 0.090844 | 0.022918 | -0.090678 | -0.022854 | 0.00016599 | 6.3655e-05 | 0.13586 | 0.13586 | 0.13586 | 0.99534 | -0.032393 | 0.99346 | -0.045443 | 50.3197
17 | -0.13955 | -0.035155 | 0.13981 | 0.035255 | 0.00026412 | 0.00010044 | 0.20841 | 0.20841 | 0.20841 | 0.99663 | -0.023366 | 0.99858 | -0.0098612 | 25.7301
18 | 0.022736 | 0.0057037 | -0.022698 | -0.0056899 | 3.7741e-05 | 1.3838e-05 | 0.03401 | 0.03401 | 0.03401 | 0.99479 | -0.036251 | 0.99308 | -0.048238 | 12.5964
19 | 0.086906 | 0.021909 | -0.086709 | -0.021834 | 0.00019646 | 7.532e-05 | 0.13021 | 0.13021 | 0.13021 | 0.99346 | -0.045443 | 0.99115 | -0.061618 | 48.2273
20 | 0.086709 | 0.021834 | -0.086555 | -0.021775 | 0.00015422 | 5.9129e-05 | 0.13021 | 0.13021 | 0.13021 | 0.99115 | -0.061618 | 0.98933 | -0.074369 | 48.2273
21 | 0.088219 | 0.022148 | -0.088138 | -0.022117 | 8.127e-05 | 3.1159e-05 | 0.13147 | 0.13147 | 0.13147 | 0.99858 | -0.0098612 | 0.99763 | -0.016499 | 48.6931
22 | -0.22803 | -0.057403 | 0.22835 | 0.057524 | 0.00031451 | 0.00012045 | 0.33989 | 0.33988 | 0.33989 | 0.99858 | -0.0098612 | 1 | 0 | 41.9611
23 | 0.022698 | 0.0056899 | -0.022687 | -0.0056859 | 1.0721e-05 | 3.9313e-06 | 0.03401 | 0.03401 | 0.03401 | 0.99308 | -0.048238 | 0.9926 | -0.05165 | 12.5964
24 | 0.048433 | 0.012155 | -0.048306 | -0.012107 | 0.00012709 | 4.8374e-05 | 0.072246 | 0.072247 | 0.072247 | 0.99763 | -0.016499 | 0.99493 | -0.035453 | 26.758
25 | 0.039704 | 0.0099617 | -0.039676 | -0.009951 | 2.8178e-05 | 1.067e-05 | 0.059225 | 0.059225 | 0.059225 | 0.99763 | -0.016499 | 0.9969 | -0.021618 | 21.9352
26 | 0.0028434 | 0.00071261 | -0.0028434 | -0.00071262 | 8.5049e-09 | -6.7175e-09 | 0.004231 | 0.004231 | 0.004231 | 1 | 0 | 1 | -2.1606e-05 | 1.567
27 | 0.037163 | 0.0093211 | -0.037163 | -0.009321 | 3.8471e-07 | 1.4535e-07 | 0.055474 | 0.055474 | 0.055474 | 0.9969 | -0.021618 | 0.99689 | -0.021693 | 20.5457
28 | 0.03414 | 0.0085635 | -0.034104 | -0.00855 | 3.5784e-05 | 1.3475e-05 | 0.050962 | 0.050962 | 0.050962 | 0.99689 | -0.021693 | 0.99581 | -0.029259 | 18.8749
29 | 0.03103 | 0.0077794 | -0.031029 | -0.0077791 | 7.8494e-07 | 2.9429e-07 | 0.046368 | 0.046368 | 0.046368 | 0.99581 | -0.029259 | 0.99579 | -0.029442 | 17.1732
30 | 0.028797 | 0.0072198 | -0.028787 | -0.0072159 | 1.0255e-05 | 3.8289e-06 | 0.043033 | 0.043033 | 0.043033 | 0.99579 | -0.029442 | 0.99542 | -0.032014 | 15.9381
31 | 0.022502 | 0.0056411 | -0.022488 | -0.005636 | 1.4033e-05 | 5.139e-06 | 0.033638 | 0.033638 | 0.033638 | 0.99542 | -0.032014 | 0.99478 | -0.036518 | 12.4584
32 | 0.0062851 | 0.0015748 | -0.0062828 | -0.0015745 | 2.3116e-06 | 3.4375e-07 | 0.0093952 | 0.0093954 | 0.0093954 | 0.99542 | -0.032014 | 0.99504 | -0.034672 | 3.4798
33 | 0.0062828 | 0.0015745 | -0.0062817 | -0.0015744 | 1.0181e-06 | 1.5154e-07 | 0.0093954 | 0.0093955 | 0.0093955 | 0.99504 | -0.034672 | 0.99488 | -0.035842 | 3.4798

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.24144 | 0.060606

## res_load
| p_mw | q_mvar
0 | 0.037317 | 0.0093525
1 | 0.019236 | 0.0048211
2 | 0.0017745 | 0.00044473
3 | 0.0047546 | 0.0011916
4 | 0.0028019 | 0.00070223
5 | 0.0055258 | 0.0013849
6 | 0.0072243 | 0.0018106
7 | 0.0043964 | 0.0011018
8 | 0.0064022 | 0.0016045
9 | 0.0042172 | 0.0010569
10 | 0.003533 | 0.00088546
11 | 0.0037719 | 0.00094532
12 | 0.0098097 | 0.0024586
13 | 0.0047061 | 0.0011795
14 | 0.0094541 | 0.0023694
15 | 0.022687 | 0.0056859
16 | 0.0028434 | 0.00071262
17 | 0.048306 | 0.012107
18 | 0.0025133 | 0.0006299
19 | 0.0030223 | 0.00075746
20 | 0.0030748 | 0.00077061
21 | 0.0022318 | 0.00055934
22 | 0.022488 | 0.005636
23 | 0.0062817 | 0.0015744

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1