## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1631-184_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1631-184_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1631-184_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1631-184_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1631-184_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1631-184_0_3_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_1631-184_0_3_node_8 | 0.4 | n |  | TRUE
7 | bus_LV_1631-184_0_3_node_35 | 0.4 | n |  | TRUE
8 | bus_LV_1631-184_0_3_node_10 | 0.4 | n |  | TRUE
9 | bus_LV_1631-184_0_3_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_1631-184_0_3_node_30 | 0.4 | n |  | TRUE
11 | bus_LV_1631-184_0_3_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_1631-184_0_3_node_14 | 0.4 | n |  | TRUE
13 | bus_LV_1631-184_0_3_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_1631-184_0_3_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_1631-184_0_3_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_1631-184_0_3_node_16 | 0.4 | n |  | TRUE
17 | bus_LV_1631-184_0_3_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_1631-184_0_3_node_18 | 0.4 | n |  | TRUE
19 | bus_LV_1631-184_0_3_node_19 | 0.4 | n |  | TRUE
20 | bus_LV_1631-184_0_3_node_20 | 0.4 | n |  | TRUE
21 | bus_LV_1631-184_0_3_node_21 | 0.4 | n |  | TRUE
22 | bus_LV_1631-184_0_3_node_22 | 0.4 | n |  | TRUE
23 | bus_LV_1631-184_0_3_node_23 | 0.4 | n |  | TRUE
24 | bus_LV_1631-184_0_3_node_24 | 0.4 | n |  | TRUE
25 | bus_LV_1631-184_0_3_node_25 | 0.4 | n |  | TRUE
26 | bus_LV_1631-184_0_3_node_26 | 0.4 | n |  | TRUE
27 | bus_LV_1631-184_0_3_node_27 | 0.4 | n |  | TRUE
28 | bus_LV_1631-184_0_3_node_28 | 0.4 | n |  | TRUE
29 | bus_LV_1631-184_0_3_node_29 | 0.4 | n |  | TRUE
30 | bus_LV_1631-184_0_3_node_34 | 0.4 | n |  | TRUE
31 | bus_LV_1631-184_0_3_node_32 | 0.4 | n |  | TRUE
32 | bus_LV_1631-184_0_3_node_31 | 0.4 | n |  | TRUE
33 | bus_LV_1631-184_0_3_node_33 | 0.4 | n |  | TRUE
34 | bus_MV_145_0_node_138 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1631-184_0_3_load_0 | 0 | 0.0064658 | 0.0016205 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1631-184_0_3_load_1 | 1 | 0.0055844 | 0.0013996 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1631-184_0_3_load_2 | 2 | 0.0096465 | 0.0024176 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1631-184_0_3_load_3 | 3 | 0.0072271 | 0.0018113 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1631-184_0_3_load_35 | 7 | 0.0094537 | 0.0023693 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1631-184_0_3_load_10 | 8 | 0.0042983 | 0.0010773 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1631-184_0_3_load_7 | 9 | 0.018654 | 0.0046752 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1631-184_0_3_load_9 | 11 | 0.021005 | 0.0052644 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1631-184_0_3_load_11 | 14 | 0.0018794 | 0.00047101 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1631-184_0_3_load_15 | 15 | 0.0029808 | 0.00074706 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1631-184_0_3_load_16 | 16 | 0.0027686 | 0.00069388 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1631-184_0_3_load_17 | 17 | 0.0018732 | 0.00046947 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1631-184_0_3_load_18 | 18 | 0.0085908 | 0.0021531 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1631-184_0_3_load_19 | 19 | 0.0078824 | 0.0019755 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1631-184_0_3_load_20 | 20 | 0.0081877 | 0.002052 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1631-184_0_3_load_21 | 21 | 0.0065271 | 0.0016358 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1631-184_0_3_load_22 | 22 | 0.0066453 | 0.0016655 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1631-184_0_3_load_23 | 23 | 0.0065729 | 0.0016473 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1631-184_0_3_load_24 | 24 | 0.0063126 | 0.0015821 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1631-184_0_3_load_25 | 25 | 0.0072484 | 0.0018166 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1631-184_0_3_load_26 | 26 | 0.0062997 | 0.0015788 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1631-184_0_3_load_27 | 27 | 0.0088613 | 0.0022209 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1631-184_0_3_load_28 | 28 | 0.0079899 | 0.0020025 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1631-184_0_3_load_29 | 29 | 0.0079125 | 0.0019831 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1631-184_0_3_load_34 | 30 | 0.015355 | 0.0038483 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1631-184_0_3_load_31 | 32 | 0.035917 | 0.0090015 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1631-184_0_3_load_33 | 33 | 0.0049944 | 0.0012517 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 27 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1631-184_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.012853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1631-184_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.006844 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1631-184_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.020895 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1631-184_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.055619 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1631-184_0_3_line_4 | NAYY 4x150 SE | 4 | 5 | 0.097711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1631-184_0_3_line_5 | NAYY 4x150 SE | 5 | 6 | 0.024248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1631-184_0_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.029695 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1631-184_0_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.047241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1631-184_0_3_line_8 | NAYY 4x150 SE | 6 | 9 | 0.016039 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1631-184_0_3_line_9 | NAYY 4x150 SE | 7 | 10 | 0.014668 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1631-184_0_3_line_10 | NAYY 4x150 SE | 8 | 12 | 0.019216 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1631-184_0_3_line_11 | NAYY 4x150 SE | 9 | 11 | 0.010368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1631-184_0_3_line_12 | NAYY 4x150 SE | 10 | 30 | 0.023043 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1631-184_0_3_line_13 | NAYY 4x150 SE | 10 | 29 | 0.019911 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
14 | LV_1631-184_0_3_line_14 | NAYY 4x150 SE | 12 | 13 | 0.13535 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1631-184_0_3_line_15 | NAYY 4x150 SE | 13 | 14 | 0.0022022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1631-184_0_3_line_16 | NAYY 4x150 SE | 15 | 16 | 0.017323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1631-184_0_3_line_17 | NAYY 4x150 SE | 16 | 17 | 0.0090361 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1631-184_0_3_line_18 | NAYY 4x150 SE | 17 | 18 | 0.014638 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1631-184_0_3_line_19 | NAYY 4x150 SE | 18 | 19 | 0.010546 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1631-184_0_3_line_20 | NAYY 4x150 SE | 19 | 20 | 0.0099192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1631-184_0_3_line_21 | NAYY 4x150 SE | 20 | 21 | 0.019249 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1631-184_0_3_line_22 | NAYY 4x150 SE | 21 | 22 | 0.0043381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1631-184_0_3_line_23 | NAYY 4x150 SE | 22 | 23 | 0.0053915 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1631-184_0_3_line_24 | NAYY 4x150 SE | 23 | 24 | 0.01781 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1631-184_0_3_line_25 | NAYY 4x150 SE | 24 | 25 | 0.0017511 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1631-184_0_3_line_26 | NAYY 4x150 SE | 25 | 26 | 0.01022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1631-184_0_3_line_27 | NAYY 4x150 SE | 26 | 27 | 0.017915 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1631-184_0_3_line_28 | NAYY 4x150 SE | 27 | 28 | 0.012251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
29 | LV_1631-184_0_3_line_29 | NAYY 4x150 SE | 28 | 29 | 0.018244 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
30 | LV_1631-184_0_3_line_30 | NAYY 4x150 SE | 30 | 31 | 0.019431 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1631-184_0_3_line_31 | NAYY 4x150 SE | 31 | 32 | 0.038104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1631-184_0_3_line_32 | NAYY 4x150 SE | 32 | 33 | 0.0044888 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1631-184_0_3_trafo_27 | 0.25 MVA 20/0.4 kV | 34 | 27 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2723991.5803 | 1206087.7359 | 2723980.4699 | 1206081.274
1 | 2723991.5803 | 1206087.7359 | 2723997.4965 | 1206091.1768
2 | 2723962.4078 | 1206070.769 | 2723980.4699 | 1206081.274
3 | 2724045.575 | 1206119.1395 | 2723997.4965 | 1206091.1768
4 | 2723973.8649 | 1206164.7292 | 2723980.8877 | 1206162.8736 | 2723987.7983 | 1206161.6495 | 2723999.3513 | 1206161.8229 | 2724014.2082 | 1206162.999 | 2724016.6085 | 1206163.1823 | 2724019.9961 | 1206163.4529 | 2724045.575 | 1206119.1395
5 | 2723973.8649 | 1206164.7292 | 2723965.1235 | 1206157.7646 | 2723952.9137 | 1206152.9519
6 | 2723973.8649 | 1206164.7292 | 2723964.6555 | 1206167.4734 | 2723959.5194 | 1206170.4357 | 2723955.1629 | 1206173.5921 | 2723952.2174 | 1206176.2107 | 2723949.1092 | 1206179.9148
7 | 2723952.9137 | 1206152.9519 | 2723908.9698 | 1206135.6139
8 | 2723952.9137 | 1206152.9519 | 2723944.775 | 1206140.4068 | 2723943.9386 | 1206139.7149
9 | 2723939.681 | 1206191.1507 | 2723949.1092 | 1206179.9148
10 | 2723891.0952 | 1206128.5615 | 2723908.9698 | 1206135.6139
11 | 2723935.9492 | 1206133.1069 | 2723943.9386 | 1206139.7149
12 | 2723939.681 | 1206191.1507 | 2723928.8406 | 1206204.2912 | 2723924.5801 | 1206208.5275
13 | 2723939.681 | 1206191.1507 | 2723921.2638 | 1206183.5847
14 | 2723758.311 | 1206109.5266 | 2723798.471 | 1206110.4042 | 2723815.5512 | 1206110.7698 | 2723838.5739 | 1206112.5709 | 2723847.2724 | 1206113.919 | 2723870.1746 | 1206121.5221 | 2723880.1031 | 1206124.8194 | 2723891.0952 | 1206128.5615
15 | 2723758.311 | 1206109.5266 | 2723756.1095 | 1206109.4702
16 | 2723759.619 | 1206143.8246 | 2723776.9269 | 1206144.5573
17 | 2723785.9549 | 1206144.9394 | 2723776.9269 | 1206144.5573
18 | 2723785.9549 | 1206144.9394 | 2723800.5798 | 1206145.5585
19 | 2723811.1166 | 1206146.0046 | 2723800.5798 | 1206145.5585
20 | 2723821.0064 | 1206146.7381 | 2723814.2086 | 1206146.1355 | 2723811.1166 | 1206146.0046
21 | 2723821.0064 | 1206146.7381 | 2723827.802 | 1206147.3405 | 2723839.8375 | 1206150.4356
22 | 2723843.8991 | 1206151.9563 | 2723840.0313 | 1206150.4854 | 2723839.8375 | 1206150.4356
23 | 2723843.8991 | 1206151.9563 | 2723848.9385 | 1206153.8728 | 2723848.9385 | 1206153.8728
24 | 2723848.9385 | 1206153.8728 | 2723865.4121 | 1206160.6403
25 | 2723867.0318 | 1206161.3057 | 2723865.4121 | 1206160.6403
26 | 2723876.4854 | 1206165.1893 | 2723867.0318 | 1206161.3057
27 | 2723876.4854 | 1206165.1893 | 2723893.0562 | 1206171.9967
28 | 2723904.3883 | 1206176.6521 | 2723893.0562 | 1206171.9967
29 | 2723904.3883 | 1206176.6521 | 2723921.2638 | 1206183.5847
30 | 2723909.7167 | 1206221.0181 | 2723921.8956 | 1206211.1968 | 2723924.5801 | 1206208.5275
31 | 2723909.7167 | 1206221.0181 | 2723888.0854 | 1206211.9513 | 2723882.3878 | 1206208.9863 | 2723876.8688 | 1206202.8864
32 | 2723873.8572 | 1206199.5577 | 2723876.8688 | 1206202.8864

## bus_geodata
| x | y | coords
0 | 2723991.5803 | 1206087.7359
1 | 2723980.4699 | 1206081.274
2 | 2723997.4965 | 1206091.1768
3 | 2723962.4078 | 1206070.769
4 | 2724045.575 | 1206119.1395
5 | 2723973.8649 | 1206164.7292
6 | 2723952.9137 | 1206152.9519
7 | 2723949.1092 | 1206179.9148
8 | 2723908.9698 | 1206135.6139
9 | 2723943.9386 | 1206139.7149
10 | 2723939.681 | 1206191.1507
11 | 2723935.9492 | 1206133.1069
12 | 2723891.0952 | 1206128.5615
13 | 2723758.311 | 1206109.5266
14 | 2723756.1095 | 1206109.4702
15 | 2723759.619 | 1206143.8246
16 | 2723776.9269 | 1206144.5573
17 | 2723785.9549 | 1206144.9394
18 | 2723800.5798 | 1206145.5585
19 | 2723811.1166 | 1206146.0046
20 | 2723821.0064 | 1206146.7381
21 | 2723839.8375 | 1206150.4356
22 | 2723843.8991 | 1206151.9563
23 | 2723848.9385 | 1206153.8728
24 | 2723865.4121 | 1206160.6403
25 | 2723867.0318 | 1206161.3057
26 | 2723876.4854 | 1206165.1893
27 | 2723893.0561 | 1206171.9967
28 | 2723904.3883 | 1206176.6521
29 | 2723921.2638 | 1206183.5847
30 | 2723924.5801 | 1206208.5275
31 | 2723909.7167 | 1206221.0181
32 | 2723876.8688 | 1206202.8864
33 | 2723873.8572 | 1206199.5577
34 | 2723893.0561 | 1206171.9967

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98303 | -0.11916 | 0.0064658 | 0.0016205
1 | 0.98279 | -0.12086 | 0.0055844 | 0.0013996
2 | 0.98322 | -0.1178 | 0.0096465 | 0.0024176
3 | 0.98257 | -0.12243 | 0.0072271 | 0.0018113
4 | 0.98555 | -0.10123 | 0 | 0
5 | 0.98965 | -0.072295 | 0 | 0
6 | 0.98805 | -0.083645 | 0 | 0
7 | 0.99286 | -0.049733 | 0.0094537 | 0.0023693
8 | 0.98763 | -0.086638 | 0.0042983 | 0.0010773
9 | 0.98713 | -0.090155 | 0.018654 | 0.0046752
10 | 0.99465 | -0.037242 | 0 | 0
11 | 0.98681 | -0.092386 | 0.021005 | 0.0052644
12 | 0.98757 | -0.087011 | 0 | 0
13 | 0.98721 | -0.089624 | 0 | 0
14 | 0.9872 | -0.089666 | 0.0018794 | 0.00047101
15 | 0.99334 | -0.046699 | 0.0029808 | 0.00074706
16 | 0.99341 | -0.046176 | 0.0027686 | 0.00069388
17 | 0.99349 | -0.045651 | 0.0018732 | 0.00046947
18 | 0.99365 | -0.044522 | 0.0085908 | 0.0021531
19 | 0.99389 | -0.042794 | 0.0078824 | 0.0019755
20 | 0.99424 | -0.040379 | 0.0081877 | 0.002052
21 | 0.99513 | -0.034109 | 0.0065271 | 0.0016358
22 | 0.99537 | -0.032413 | 0.0066453 | 0.0016655
23 | 0.99572 | -0.029944 | 0.0065729 | 0.0016473
24 | 0.99705 | -0.020628 | 0.0063126 | 0.0015821
25 | 0.9972 | -0.019602 | 0.0072484 | 0.0018166
26 | 0.99816 | -0.012879 | 0.0062997 | 0.0015788
27 | 1 | 0 | -0.23111 | -0.057984
28 | 0.99862 | -0.0095776 | 0.0079899 | 0.0020025
29 | 0.99667 | -0.023157 | 0.0079125 | 0.0019831
30 | 0.99278 | -0.050348 | 0.015355 | 0.0038483
31 | 0.99164 | -0.058408 | 0 | 0
32 | 0.98939 | -0.074266 | 0.035917 | 0.0090015
33 | 0.98936 | -0.074495 | 0.0049944 | 0.0012517
34 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.012816 | 0.0032122 | -0.012813 | -0.0032112 | 3.0184e-06 | 9.9802e-07 | 0.0194 | 0.0194 | 0.0194 | 0.98303 | -0.11916 | 0.98279 | -0.12086 | 7.1851
1 | -0.019282 | -0.0048327 | 0.019285 | 0.004834 | 3.6381e-06 | 1.3125e-06 | 0.029187 | 0.029187 | 0.029187 | 0.98303 | -0.11916 | 0.98322 | -0.1178 | 10.81
2 | 0.0072287 | 0.0018116 | -0.0072271 | -0.0018113 | 1.5618e-06 | 3.3599e-07 | 0.010945 | 0.010945 | 0.010945 | 0.98279 | -0.12086 | 0.98257 | -0.12243 | 4.0536
3 | -0.028932 | -0.0072516 | 0.028999 | 0.0072765 | 6.6539e-05 | 2.4885e-05 | 0.043786 | 0.043786 | 0.043786 | 0.98322 | -0.1178 | 0.98555 | -0.10123 | 16.2171
4 | -0.028999 | -0.0072765 | 0.029115 | 0.0073202 | 0.00011689 | 4.3709e-05 | 0.043786 | 0.043785 | 0.043786 | 0.98555 | -0.10123 | 0.98965 | -0.072295 | 16.217
5 | 0.045955 | 0.01153 | -0.045883 | -0.011502 | 7.2249e-05 | 2.7477e-05 | 0.069101 | 0.069101 | 0.069101 | 0.98965 | -0.072295 | 0.98805 | -0.083645 | 25.5931
6 | -0.07507 | -0.01885 | 0.075307 | 0.018941 | 0.00023613 | 9.0437e-05 | 0.11289 | 0.11289 | 0.11289 | 0.98965 | -0.072295 | 0.99286 | -0.049733 | 41.8099
7 | 0.006181 | 0.0015469 | -0.0061785 | -0.0015466 | 2.554e-06 | 3.7752e-07 | 0.0093079 | 0.0093081 | 0.0093081 | 0.98805 | -0.083645 | 0.98763 | -0.086638 | 3.4475
8 | 0.039702 | 0.0099555 | -0.039666 | -0.009942 | 3.5783e-05 | 1.3558e-05 | 0.059793 | 0.059793 | 0.059793 | 0.98805 | -0.083645 | 0.98713 | -0.090155 | 22.1457
9 | -0.08476 | -0.02131 | 0.084908 | 0.021367 | 0.00014775 | 5.6636e-05 | 0.12705 | 0.12705 | 0.12705 | 0.99286 | -0.049733 | 0.99465 | -0.037242 | 47.0574
10 | 0.0018801 | 0.00046931 | -0.0018801 | -0.00046952 | 9.6175e-08 | -2.0889e-07 | 0.0028321 | 0.0028322 | 0.0028322 | 0.98763 | -0.086638 | 0.98757 | -0.087011 | 1.0489
11 | 0.021012 | 0.0052668 | -0.021005 | -0.0052644 | 6.4906e-06 | 2.3639e-06 | 0.031674 | 0.031674 | 0.031674 | 0.98713 | -0.090155 | 0.98681 | -0.092386 | 11.7311
12 | 0.056505 | 0.014192 | -0.056402 | -0.014153 | 0.00010277 | 3.923e-05 | 0.084543 | 0.084543 | 0.084543 | 0.99465 | -0.037242 | 0.99278 | -0.050348 | 31.3124
13 | -0.14141 | -0.035559 | 0.14169 | 0.035665 | 0.00027814 | 0.00010646 | 0.2116 | 0.2116 | 0.2116 | 0.99465 | -0.037242 | 0.99667 | -0.023157 | 39.1848
14 | 0.0018801 | 0.00046952 | -0.0018794 | -0.00047099 | 6.7762e-07 | -1.4706e-06 | 0.0028322 | 0.0028328 | 0.0028328 | 0.98757 | -0.087011 | 0.98721 | -0.089624 | 1.0492
15 | 0.0018794 | 0.00047099 | -0.0018794 | -0.00047101 | 1.1027e-08 | -2.3915e-08 | 0.0028328 | 0.0028328 | 0.0028328 | 0.98721 | -0.089624 | 0.9872 | -0.089666 | 1.0492
16 | -0.0029808 | -0.00074706 | 0.002981 | 0.00074692 | 2.1553e-07 | -1.4138e-07 | 0.0044652 | 0.0044652 | 0.0044652 | 0.99334 | -0.046699 | 0.99341 | -0.046176 | 1.6538
17 | -0.0057496 | -0.0014408 | 0.00575 | 0.0014408 | 4.1821e-07 | 4.3849e-08 | 0.0086122 | 0.0086122 | 0.0086122 | 0.99341 | -0.046176 | 0.99349 | -0.045651 | 3.1897
18 | -0.0076233 | -0.0019103 | 0.0076244 | 0.0019106 | 1.1908e-06 | 2.6841e-07 | 0.011418 | 0.011418 | 0.011418 | 0.99349 | -0.045651 | 0.99365 | -0.044522 | 4.2288
19 | -0.016215 | -0.0040636 | 0.016219 | 0.004065 | 3.8804e-06 | 1.3558e-06 | 0.024283 | 0.024283 | 0.024283 | 0.99365 | -0.044522 | 0.99389 | -0.042794 | 8.9936
20 | -0.024102 | -0.0060405 | 0.02411 | 0.0060435 | 8.0591e-06 | 2.9711e-06 | 0.036084 | 0.036084 | 0.036084 | 0.99389 | -0.042794 | 0.99424 | -0.040379 | 13.3644
21 | -0.032297 | -0.0080955 | 0.032325 | 0.0081061 | 2.8066e-05 | 1.0545e-05 | 0.048338 | 0.048338 | 0.048338 | 0.99424 | -0.040379 | 0.99513 | -0.034109 | 17.9029
22 | -0.038852 | -0.0097419 | 0.038862 | 0.0097454 | 9.137e-06 | 3.4578e-06 | 0.058098 | 0.058098 | 0.058098 | 0.99513 | -0.034109 | 0.99537 | -0.032413 | 21.5177
23 | -0.045507 | -0.011411 | 0.045522 | 0.011417 | 1.5571e-05 | 5.9187e-06 | 0.068032 | 0.068032 | 0.068032 | 0.99537 | -0.032413 | 0.99572 | -0.029944 | 25.197
24 | -0.052095 | -0.013064 | 0.052163 | 0.01309 | 6.7361e-05 | 2.5676e-05 | 0.077855 | 0.077854 | 0.077855 | 0.99572 | -0.029944 | 0.99705 | -0.020628 | 28.835
25 | -0.058475 | -0.014672 | 0.058484 | 0.014675 | 8.3229e-06 | 3.1783e-06 | 0.087276 | 0.087275 | 0.087276 | 0.99705 | -0.020628 | 0.9972 | -0.019602 | 32.3243
26 | -0.065732 | -0.016492 | 0.065793 | 0.016515 | 6.1363e-05 | 2.3468e-05 | 0.098092 | 0.098091 | 0.098092 | 0.9972 | -0.019602 | 0.99816 | -0.012879 | 36.3302
27 | -0.072093 | -0.018094 | 0.072222 | 0.018143 | 0.00012914 | 4.9436e-05 | 0.10748 | 0.10748 | 0.10748 | 0.99816 | -0.012879 | 1 | 0 | 39.8085
28 | 0.15809 | 0.039841 | -0.15788 | -0.03976 | 0.00021166 | 8.1086e-05 | 0.23532 | 0.23532 | 0.23532 | 1 | 0 | 0.99862 | -0.0095776 | 43.5772
29 | 0.14989 | 0.037757 | -0.1496 | -0.037648 | 0.00028411 | 0.0001088 | 0.22341 | 0.22341 | 0.22341 | 0.99862 | -0.0095776 | 0.99667 | -0.023157 | 41.3725
30 | 0.041047 | 0.010305 | -0.041001 | -0.010287 | 4.5903e-05 | 1.7404e-05 | 0.061529 | 0.061529 | 0.061529 | 0.99278 | -0.050348 | 0.99164 | -0.058408 | 22.7885
31 | 0.041001 | 0.010287 | -0.040911 | -0.010253 | 9.0014e-05 | 3.413e-05 | 0.061529 | 0.061529 | 0.061529 | 0.99164 | -0.058408 | 0.98939 | -0.074266 | 22.7886
32 | 0.0049946 | 0.0012517 | -0.0049944 | -0.0012517 | 1.5805e-07 | 3.1427e-09 | 0.0075117 | 0.0075117 | 0.0075117 | 0.98939 | -0.074266 | 0.98936 | -0.074495 | 2.7821

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.23997 | 0.060205

## res_load
| p_mw | q_mvar
0 | 0.0064658 | 0.0016205
1 | 0.0055844 | 0.0013996
2 | 0.0096465 | 0.0024176
3 | 0.0072271 | 0.0018113
4 | 0.0094537 | 0.0023693
5 | 0.0042983 | 0.0010773
6 | 0.018654 | 0.0046752
7 | 0.021005 | 0.0052644
8 | 0.0018794 | 0.00047101
9 | 0.0029808 | 0.00074706
10 | 0.0027686 | 0.00069388
11 | 0.0018732 | 0.00046947
12 | 0.0085908 | 0.0021531
13 | 0.0078824 | 0.0019755
14 | 0.0081877 | 0.002052
15 | 0.0065271 | 0.0016358
16 | 0.0066453 | 0.0016655
17 | 0.0065729 | 0.0016473
18 | 0.0063126 | 0.0015821
19 | 0.0072484 | 0.0018166
20 | 0.0062997 | 0.0015788
21 | 0.0088613 | 0.0022209
22 | 0.0079899 | 0.0020025
23 | 0.0079125 | 0.0019831
24 | 0.015355 | 0.0038483
25 | 0.035917 | 0.0090015
26 | 0.0049944 | 0.0012517

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1